## SSR Database
Description | Description | Resource Characteristics | Resource Characteristics |  |  |  |  | Costs | [6 empty] | Operating Characteristics |  |  |  | Environmental |  |  |  |  | Plexos Model Inputs
Fuel | Resource | Elevation (AFSL) | Net Capacity (MW) | Resource Availability Year | Total Implementation Time (yrs) | Commercial Operation Year | Design Life (yrs) | Base Capital ($/kW) | Var O&M ($/MWh) | Fraction Var O&M Capitalized | Fraction Var O&M Adjusted by Capacity Changes | Fixed O&M ($/kW-yr) | Fraction Fixed O&M Capitalized | Demolition Cost ($/kW) | Average Full Load Heat Rate (HHV Btu/KWh) /Efficiency | EFOR (%) | POR (%) | Water Consumed (Gal/MWh) | SO2 (lbs/MMBtu) | NOx (lbs/MMBtu) | Hg (lbs/TBTu) | CO2 (lbs/MMBtu) | CH4 (lbs/MMBtu) | Minimum Capacity (per SC machine, per CCCT config,% capacity) | Minimum Capacity (per SC machine or per CCCT config, MW) | Spinning Reserves (per SC machine or per CCCT config, MW) | Run-up Rate (first fire to min capacity, warm start, MW/hr) | Ramp Rate (min capacity to full load, warm start, MW/hr) | Warm Start-Up Time to Minimum Capacity (min) | Heat Input for Warm Start (HHV, MMBtu) | Minimum Operational Up Time (hr) | Minimum Operational Down Time (hr)
Natural Gas | SCCT Aero x4 | 0 | 229.048 | 2023 | 4.0845 | 2027.0845 | 30 | 1529.5279 | 0.28333 | 1 | 0 | 18.6785 | 0.0011959 | 34.6652 | 9240.8 | 0.7 | 2 | 23 | 0.001431 | 0.091 | 0.255 | 118.9 |  | 50 | 28092 | 29.175 | 111.2606 | 450 | 3.9333 | 14.7 | 1 | 1
Natural Gas | SCCT Frame "J" x1 | 0 | 354.139 | 2023 | 4.0845 | 2027.0845 | 40 | 813.9556 | 2.3236 | 1 | 0 | 14.0889 | 0.0015987 | 20.8026 | 9073.3746 | 5.6 | 7.15 | 0 | 0.001961 | 0.057 | 0.255 | 118.9 |  | 29.7925 | 105506.7 | 354.139 | 1150.9822 | 1920 | 5.5 | 46.8 | 1 | 1
Natural Gas | SCCT Frame "J" x1, 30H2 | 0 | 337.448 | 2023 | 4.5036 | 2027.5036 | 40 | 3931.8591 | 2.4385 | 1 | 0 | 44.8001 | 0.00050088 | 28.2206 | 9190.5571 | 5.6 | 7.15 | 121.875 | 0.001829 | 0.055 | 0.1785 | 112 |  | 29.7822 | 100499.4 | 337.448 | 1096.3571 | 1920 | 5.5 | 46.8 | 1 | 1
Natural Gas | SCCT Frame "J" X1, 100H2 | 0 | 361.9301 | 2030 | 4.5036 | 2034.5036 | 40 | 6587.5917 | 2.2284 | 1 | 0 | 68.9995 | 0.00031727 | 31.3237 | 9489.0401 | 5.6 | 7.15 | 406.25 | 0 | 0.0655 | 0 | 0 |  | 29.7925 | 107827.8474 | 361.9301 | 1176.3038 | 1920 | 5.5 | 46.8 | 1 | 1
Natural Gas | SCCT Frame "J" X1, 100H2 - pipeline Willamette Valley | 0 | 361.9301 | 2030 | 4.5036 | 2034.5036 | 40 | 929.6355 | 2.2284 | 1 | 0 | 14.0889 | 0.00031727 | 31.3237 | 9489.0401 | 5.6 | 7.15 | 406.25 | 0 | 0.0655 | 0 | 0 |  | 29.7925 | 107827.8474 | 361.9301 | 1176.3038 | 1920 | 5.5 | 46.8 | 1 | 1
Natural Gas | SCCT Frame "J" X1, 100H2 - pipeline McNary | 0 | 361.9301 | 2030 | 4.5036 | 2034.5036 | 40 | 929.6355 | 2.2284 | 1 | 0 | 14.0889 | 0.00031727 | 31.3237 | 9489.0401 | 5.6 | 7.15 | 406.25 | 0 | 0.0655 | 0 | 0 |  | 29.7925 | 107827.8474 | 361.9301 | 1176.3038 | 1920 | 5.5 | 46.8 | 1 | 1
Natural Gas | SCCT Frame "J" X1, 100H2, BF | 0 | 361.93 | 2030 | 2.5038 | 2032.5038 | 40 | 5894.4561 | 2.2736 | 1 | 0 | 66.3667 | 0.00033654 | 31.3237 | 9489.0401 | 5.6 | 7.15 | 406.25 | 0 | 0.0655 | 0 | 0 |  | 29.7925 | 107827.8474 | 361.9301 | 1176.3038 | 1920 | 5.5 | 46.8 | 1 | 1
Natural Gas | CCCT Dry "J", 1X1 | 0 | 547.8114 | 2023 | 4.5036 | 2027.5036 | 40 | 1360.9903 | 1.6061 | 0.99 | 0.93518 | 22.7176 | 0.17694 | 20.9689 | 6227.0809 | 5.6 | 7.15 | 7.8 | 0.00197 | 0.00761 | 0.255 | 118.9 |  | 37.4558 | 205187.1022 | 248 | 351.7493 | 1920 | 14 | 645.582 | 1 | 1
Natural Gas | CCCT Dry "J", DF, 1x1 | 0 | 62.9996 | 2023 | 4.5036 | 2027.5036 | 40 | 0 | 1.1452 | 0 | 1 | 0 | 0 | 0 | 8726.1564 | 5.6 | 7.15 | 8.3 | 0.001962 | 0.00762 | 0.255 | 118.9 |  | 33.5926 | 205187.1022 | 248 | 351.7493 | 1920 | 14 | 645.582 | 0 | 0
Natural Gas | SCCT Aero x4 | 1500 | 216.3844 | 2023 | 4.0845 | 2027.0845 | 30 | 1619.0414 | 0.29991 | 1 | 0 | 19.7716 | 0.0011959 | 45.7981 | 9258.2 | 0.7 | 2 | 24.4 | 0.001431 | 0.091 | 0.255 | 118.9 |  | 50 | 26926.3 | 27.1698 | 111.2606 | 450 | 3.9333 | 14.7 | 1 | 1
Natural Gas | SCCT Frame "J" x1 | 1500 | 337.974 | 2023 | 4.0845 | 2027.0845 | 40 | 852.8864 | 2.4347 | 1 | 0 | 14.7628 | 0.0015987 | 28.2892 | 9065.7531 | 5.6 | 7.15 | 0 | 0.001954 | 0.057 | 0.255 | 118.9 |  | 29.7825 | 100657.2 | 337.974 | 1098.0785 | 1920 | 5.5 | 44.6 | 1 | 1
Natural Gas | SCCT Frame "J" x1, 30H2 | 1500 | 322.188 | 2023 | 4.5036 | 2027.5036 | 40 | 4118.0863 | 2.554 | 1 | 0 | 46.922 | 0.00050088 | 37.953 | 9184.0568 | 5.6 | 7.15 | 121.875 | 0.00181 | 0.055 | 0.1785 | 113 |  | 29.7719 | 95921.4 | 322.188 | 1046.4153 | 1920 | 5.5 | 44.6 | 1 | 1
Natural Gas | SCCT Frame "J" X1, 100H2 | 1500 | 345.4094 | 2030 | 4.5036 | 2034.5036 | 40 | 6902.6704 | 2.3823 | 1 | 0 | 73.7655 | 0.00031727 | 41.2149 | 9480.7354 | 5.6 | 7.15 | 406.25 | 0 | 0.0654 | 0 | 0 |  | 29.7825 | 102871.6584 | 345.4094 | 1122.2363 | 1920 | 5.5 | 44.6 | 1 | 1
Natural Gas | SCCT Frame "J" X1, 100H2 - pipeline Southern OR | 1500 | 345.4094 | 2030 | 4.5036 | 2034.5036 | 40 | 974.6377 | 2.3823 | 1 | 0 | 14.7628 | 0.00031727 | 41.2149 | 9480.7354 | 5.6 | 7.15 | 406.25 | 0 | 0.0654 | 0 | 0 |  | 29.7825 | 102871.6584 | 345.4094 | 1122.2363 | 1920 | 5.5 | 44.6 | 1 | 1
Natural Gas | SCCT Frame "J" X1, 100H2, BF | 1500 | 345.4094 | 2030 | 2.5038 | 2032.5038 | 40 | 6176.3817 | 2.3823 | 1 | 0 | 69.541 | 0.00033654 | 41.2149 | 9480.7354 | 5.6 | 7.15 | 406.25 | 0 | 0.0654 | 0 | 0 |  | 29.7825 | 102871.6584 | 345.4094 | 1122.2363 | 1920 | 5.5 | 44.6 | 1 | 1
Natural Gas | CCCT Dry "J", 1X1 | 1500 | 522.5997 | 2023 | 4.5036 | 2027.5036 | 40 | 1426.6482 | 1.6836 | 0.99 | 0.93518 | 23.8135 | 0.17694 | 27.7421 | 6226.8282 | 5.6 | 7.15 | 7.9 | 0.001969 | 0.00761 | 0.255 | 118.9 |  | 37.3049 | 194955.5153 | 237 | 334.2095 | 1920 | 14 | 615.8457 | 1 | 1
Natural Gas | CCCT Dry "J", DF, 1x1 | 1500 | 63.0003 | 2023 | 4.5036 | 2027.5036 | 40 | 0 | 1.1452 | 0 | 1 | 0 | 0 | 0 | 8688.3818 | 5.6 | 7.15 | 8.5 | 0.001962 | 0.00762 | 0.255 | 118.9 |  | 33.2916 | 194955.5153 | 237 | 334.2095 | 1920 | 14 | 615.8457 | 0 | 0
Natural Gas | SCCT Aero x4 | 3000 | 204.5184 | 2023 | 4.0845 | 2027.0845 | 30 | 1712.4418 | 0.31731 | 1 | 0 | 20.9188 | 0.0011959 | 46.1279 | 9286.6 | 0.7 | 2 | 25.8 | 0.001431 | 0.091 | 0.255 | 118.9 |  | 50 | 25443.1 | 25.675 | 111.2606 | 450 | 3.9333 | 14.7 | 1 | 1
Natural Gas | SCCT Frame "J" x1 | 3000 | 319.695 | 2023 | 4.0845 | 2027.0845 | 40 | 901.309 | 2.5739 | 1 | 0 | 15.6069 | 0.0015987 | 28.962 | 9071.8115 | 5.6 | 7.15 | 0 | 0.001956 | 0.0571 | 0.255 | 118.9 |  | 29.7701 | 95173.5 | 319.695 | 1038.2564 | 1920 | 5.5 | 42.3 | 1 | 1
Natural Gas | SCCT Frame "J" x1, 30H2 | 3000 | 304.625 | 2023 | 4.0845 | 2027.0845 | 40 | 4355.1001 | 2.7013 | 1 | 0 | 49.6273 | 0.00050088 | 37.8728 | 9189.142 | 5.6 | 7.15 | 121.875 | 0.001801 | 0.055 | 0.1785 | 113 |  | 29.7587 | 90652.5 | 304.625 | 988.9364 | 1920 | 5.5 | 42.3 | 1 | 1
Natural Gas | SCCT Frame "J" X1, 100H2 | 3000 | 326.7283 | 2030 | 4.0845 | 2034.0845 | 40 | 7296.9556 | 2.5185 | 1 | 0 | 77.9831 | 0.00031727 | 42.5583 | 9485.891 | 5.6 | 7.15 | 406.25 | 0 | 0.0655 | 0 | 0 |  | 29.7701 | 97267.317 | 326.7283 | 1061.098 | 1920 | 5.5 | 42.3 | 1 | 1
Natural Gas | SCCT Frame "J" X1, 100H2, BF | 3000 | 326.7283 | 2030 | 4.0845 | 2034.0845 | 40 | 6529.1803 | 2.5185 | 1 | 0 | 73.5171 | 0.00033654 | 42.5583 | 9485.891 | 5.6 | 7.15 | 406.25 | 0 | 0.0655 | 0 | 0 |  | 29.7701 | 97267.317 | 326.7283 | 1061.098 | 1920 | 5.5 | 42.3 | 1 | 1
Natural Gas | CCCT Dry "J", 1X1 | 3000 | 494.7646 | 2023 | 4.0845 | 2027.0845 | 40 | 1506.6564 | 1.7783 | 0.99 | 0.93518 | 25.1533 | 0.17694 | 27.3746 | 6226.245 | 5.6 | 7.15 | 8 | 0.001977 | 0.00761 | 0.255 | 118.9 |  | 37.2522 | 184310.6791 | 224 | 315.9612 | 1920 | 14 | 582.9895 | 1 | 1
Natural Gas | CCCT Dry "J", DF, 1x1 | 3000 | 63.0004 | 2023 | 4.5036 | 2027.5036 | 40 | 0 | 1.1452 | 0 | 1 | 0 | 0 | 0 | 8705.3523 | 5.6 | 7.15 | 8.7 | 0.001968 | 0.00762 | 0.255 | 118.9 |  | 33.0445 | 184310.6791 | 224 | 315.9612 | 1920 | 14 | 582.9895 | 0 | 0
Natural Gas | SCCT Aero x4 | 5050 | 189.7988 | 2023 | 4.5036 | 2027.5036 | 30 | 1843.9165 | 0.34191 | 1 | 0 | 22.5411 | 0.0011959 | 41.8338 | 9326.2 | 0.7 | 2 | 27.8 | 0.001431 | 0.091371 | 0.255 | 118.9 |  | 50 | 23603.2 | 23.85 | 111.2606 | 450 | 3.9333 | 14.7 | 1 | 1
Natural Gas | SCCT Frame "J" x1 | 5050 | 296.43 | 2023 | 5.5035 | 2028.5035 | 40 | 971.1948 | 2.7759 | 1 | 0 | 16.8318 | 0.0015987 | 24.8524 | 9079.7099 | 5.6 | 7.15 | 0 | 0.001951 | 0.0571 | 0.255 | 118.9 |  | 29.752 | 88194 | 296.43 | 962.1164 | 1920 | 5.5 | 39.2 | 1 | 1
Natural Gas | SCCT Frame "J" x1, 30H2 | 5050 | 282.433 | 2023 | 5.5035 | 2028.5035 | 40 | 4696.0812 | 2.9135 | 1 | 0 | 53.5267 | 0.00050088 | 33.7177 | 9197.2323 | 5.6 | 7.15 | 121.875 | 0.001819 | 0.055 | 0.1785 | 112 |  | 29.7398 | 83994.9 | 282.433 | 916.308 | 1920 | 5.5 | 39.2 | 1 | 1
Natural Gas | SCCT Frame "J" X1, 100H2 | 5050 | 302.9515 | 2030 | 4.5036 | 2034.5036 | 40 | 7868.5138 | 2.7162 | 1 | 0 | 84.1035 | 0.00031727 | 37.4218 | 9492.9578 | 5.6 | 7.15 | 406.25 | 0 | 0.0655 | 0 | 0 |  | 29.752 | 90134.268 | 302.9515 | 983.2829 | 1920 | 5.5 | 39.2 | 1 | 1
Natural Gas | SCCT Frame "J" X1, 100H2 - pipeline Utah North | 5050 | 302.9515 | 2030 | 4.5036 | 2034.5036 | 40 | 1109.2241 | 2.7162 | 1 | 0 | 16.8318 | 0.00031727 | 37.4218 | 9492.9578 | 5.6 | 7.15 | 406.25 | 0 | 0.0655 | 0 | 0 |  | 29.752 | 90134.268 | 302.9515 | 983.2829 | 1920 | 5.5 | 39.2 | 1 | 1
Natural Gas | SCCT Frame "J" X1, 100H2, BF | 5050 | 302.9515 | 2030 | 4.5036 | 2034.5036 | 40 | 7040.5986 | 2.7162 | 1 | 0 | 79.287 | 0.00033654 | 37.4218 | 9492.9578 | 5.6 | 7.15 | 406.25 | 0 | 0.0655 | 0 | 0 |  | 29.752 | 90134.268 | 302.9515 | 983.2829 | 1920 | 5.5 | 39.2 | 1 | 1
Natural Gas | SCCT Frame "J" X1, 100H2, BF - pipeline Dave Johnston | 5050 | 302.9515 | 2030 | 4.5036 | 2034.5036 | 40 | 1109.2241 | 2.7162 | 1 | 0 | 16.8318 | 0.00033654 | 37.4218 | 9492.9578 | 5.6 | 7.15 | 406.25 | 0 | 0.0655 | 0 | 0 |  | 29.752 | 90134.268 | 302.9515 | 983.2829 | 1920 | 5.5 | 39.2 | 1 | 1
Natural Gas | SCCT Frame "J" X1, 100H2, BF - pipeline Hunter | 5050 | 302.9515 | 2030 | 4.5036 | 2034.5036 | 40 | 1109.2241 | 2.7162 | 1 | 0 | 16.8318 | 0.00033654 | 37.4218 | 9492.9578 | 5.6 | 7.15 | 406.25 | 0 | 0.0655 | 0 | 0 |  | 29.752 | 90134.268 | 302.9515 | 983.2829 | 1920 | 5.5 | 39.2 | 1 | 1
Natural Gas | CCCT Dry "J", 1X1 | 5050 | 458.6518 | 2023 | 5.5035 | 2028.5035 | 40 | 1624.5359 | 1.9184 | 0.99 | 0.93518 | 27.1338 | 0.17694 | 25.0451 | 6234.2609 | 5.6 | 7.15 | 8.2 | 0.001947 | 0.00761 | 0.255 | 118.9 |  | 37.1268 | 170282.6424 | 208 | 291.9131 | 1920 | 14 | 541.1329 | 1 | 1
Natural Gas | CCCT Dry "J", DF, 1x1 | 5050 | 63.0002 | 2023 | 5.5035 | 2028.5035 | 40 | 0 | 1.1452 | 0 | 1 | 0 | 0 | 0 | 8651.5848 | 5.6 | 7.15 | 8.9 | 0.001974 | 0.00762 | 0.255 | 118.9 |  | 32.643 | 170282.6424 | 208 | 291.9131 | 1920 | 14 | 541.1329 | 0 | 0
Natural Gas | SCCT Aero x4 | 6500 | 171.2392 | 2023 | 4.5036 | 2027.5036 | 30 | 2043.57 | 0.37897 | 1 | 0 | 24.9842 | 0.0011959 | 49.3111 | 9208.1 | 0.7 | 2 | 29.8 | 0 | 0.091344 | 0.255 | 118.9 |  | 50 | 21264.5 | 21.55 | 111.2606 | 450 | 3.9333 | 14.7 | 1 | 1
Natural Gas | SCCT Frame "J" x1 | 6500 | 283.017 | 2023 | 4.5036 | 2027.5036 | 40 | 1017.1029 | 2.9075 | 1 | 0 | 17.6295 | 0.0015987 | 28.6449 | 9075.6602 | 5.6 | 7.15 | 0 | 0 | 0.0571 | 0.255 | 118.9 |  | 29.7403 | 84170.1 | 283.017 | 918.2193 | 1920 | 5.5 | 39.2 | 1 | 1
Natural Gas | SCCT Frame "J" x1, 30H2 | 6500 | 269.7 | 2023 | 5.5035 | 2028.5035 | 40 | 4917.7912 | 3.0511 | 1 | 0 | 56.0538 | 0.00050088 | 39.7775 | 9192.1073 | 5.6 | 7.15 | 121.875 | 0 | 0.055 | 0.1785 | 113 |  | 29.7275 | 20043.75 | 269.7 | 874.6364 | 1920 | 5.5 | 39.2 | 1 | 1
Natural Gas | SCCT Frame "J" X1, 100H2 | 6500 | 289.2434 | 2030 | 5.5035 | 2035.5035 | 40 | 8241.4256 | 2.8449 | 1 | 0 | 88.0895 | 0.00031727 | 44.1566 | 9488.5483 | 5.6 | 7.15 | 406.25 | 0 | 0.0654 | 0 | 0 |  | 29.7403 | 86021.8422 | 289.2434 | 938.4201 | 1920 | 5.5 | 39.2 | 1 | 1
Natural Gas | SCCT Frame "J" X1, 100H2, BF | 6500 | 289.2434 | 2030 | 4.0845 | 2034.0845 | 40 | 7374.2731 | 2.8449 | 1 | 0 | 83.0447 | 0.00033654 | 44.1566 | 9488.5483 | 5.6 | 7.15 | 406.25 | 0 | 0.0654 | 0 | 0 |  | 29.7403 | 21505.4605 | 289.2434 | 938.4201 | 1920 | 5.5 | 39.2 | 1 | 1
Natural Gas | SCCT Frame "J" X1, 100H2, BF - pipeline Naughton | 6500 | 289.2434 | 2030 | 4.0845 | 2034.0845 | 40 | 1161.8741 | 2.8449 | 1 | 0 | 17.6295 | 0.00033654 | 44.1566 | 9488.5483 | 5.6 | 7.15 | 406.25 | 0 | 0.0654 | 0 | 0 |  | 29.7403 | 21505.4605 | 289.2434 | 938.4201 | 1920 | 5.5 | 39.2 | 1 | 1
Natural Gas | SCCT Frame "J" X1, 100H2, BF - pipeline Jim Bridger | 6500 | 289.2434 | 2030 | 4.0845 | 2034.0845 | 40 | 1161.8741 | 2.8449 | 1 | 0 | 17.6295 | 0.00033654 | 44.1566 | 9488.5483 | 5.6 | 7.15 | 406.25 | 0 | 0.0654 | 0 | 0 |  | 29.7403 | 21505.4605 | 289.2434 | 938.4201 | 1920 | 5.5 | 39.2 | 1 | 1
Natural Gas | CCCT Dry "J", 1X1 | 6500 | 437.2329 | 2023 | 4.0845 | 2027.0845 | 40 | 1704.1176 | 2.0123 | 0.99 | 0.93518 | 28.463 | 0.17694 | 43.3199 | 6241.3289 | 5.6 | 7.15 | 8.4 | 0 | 0.00761 | 0.255 | 118.9 |  | 37.1002 | 162214.2364 | 198 | 278.0815 | 1920 | 14 | 541.1329 | 1 | 1
Natural Gas | CCCT Dry "J", DF, 1x1 | 6500 | 63.0001 | 2023 | 4.0845 | 2027.0845 | 40 | 0 | 1.1452 | 0 | 1 | 0 | 0 | 0 | 8589.7238 | 5.6 | 7.15 | 9 | 0 | 0.00762 | 0.255 | 118.9 |  | 32.4277 | 40553.5591 | 198 | 278.0815 | 1920 | 14 | 541.1329 | 0 | 0
Coal | PC CCS Oxy-Combustion retrofit @ 100 MW pre-retrofit basis | 5000 | -39 | 2023 | 5 | 2028 | 30 | 4672.7789 | 18.679 | 0 | 0 | 54.2396 | 0.38 | 37 | 18320.7141 | 5 | 5 | 193.1188 | 0.004 | 0.042 | 1.2 | 6.24 |  | - | - | - | - | - | - | - | - | -
Coal | PC CCS retrofit @ 330 MW pre-retrofit basis | 6500 | -99 | 2023 | 5 | 2028 | 20 | 2826.4015 | 21.6972 | 0 | 0 | 32.7099 | 0.38 | 37 | 15632.234 | 5 | 5 | 450 | 0.005 | 0.07 | 1.2 | 20.5352 |  | 0.4 | -39.6 | 70 | 300 | 420 | -7.92 | 2449.7283 | 168 | 48
Coal | PC CCS retrofit @ 700 MW pre-retrofit basis | 6500 | -187 | 2023 | 5 | 2028 | 20 | 1931.7685 | 20.7875 | 0 | 0 | 18.0376 | 0.38 | 37 | 14656.2282 | 5 | 5 | 450 | 0.005 | 0.07 | 1.2 | 20.5352 |  | 0.4 | -74.8 | 70 | 300 | 420 | -14.96 | 2449.7283 | 168 | 48
Storage | Li-Ion, 4-hour, 200 MW | N/A | 200 | 2023 | 2 | 2025 | 20 | 1816.9963 | Included | 0 | 0 | 42.3188 | 0 | 24 | n/a | 0 | 0 | n/a | 0 | 0 | 0 | 0 |  | 0 | 0 | 400 | n/a | 999999 | n/a | 0 | 0 | 0
Storage | Incremental, double energy capacity (L-ion, 4hr, 200MW) | N/A | 200 | 2023 | 2 | 2025 | 20 | 1486.4349 | Included | 0 | 0 | 42.3188 | 0 | 24 | n/a | 0 | 0 | n/a | 0 | 0 | 0 | 0 |  | 0 | 0 | 400 | n/a | 999999 | n/a | 0 | 0 | 0
Storage | Li-Ion, 4-hour, 500 MW | N/A | 500 | 2023 | 2 | 2025 | 20 | 1774.6563 | Included | 0 | 0 | 41.36 | 0 | 24 | n/a | 0 | 0 | n/a | 0 | 0 | 0 | 0 |  | 0 | 0 | 1000 | n/a | 999999 | n/a | 0 | 0 | 0
Storage | Incremental, double energy capacity (L-ion, 4hr, 500MW) | N/A | 500 | 2023 | 2 | 2025 | 20 | 1459.6391 | Included | 0 | 0 | 41.36 | 0 | 24 | n/a | 0 | 0 | n/a | 0 | 0 | 0 | 0 |  | 0 | 0 | 1000 | n/a | 999999 | n/a | 0 | 0 | 0
Storage | Li-Ion, 4-hour, 1000 MW | N/A | 1000 | 2023 | 2 | 2025 | 20 | 1728.659 | Included | 0 | 0 | 40.3084 | 0 | 24 | n/a | 0 | 0 | n/a | 0 | 0 | 0 | 0 |  | 0 | 0 | 2000 | n/a | 999999 | n/a | 0 | 0 | 0
Storage | Incremental, double energy capacity (L-ion, 4hr, 1000MW) | N/A | 1000 | 2023 | 2 | 2025 | 20 | 1422.1217 | Included | 0 | 0 | 40.3084 | 0 | 24 | n/a | 0 | 0 | n/a | 0 | 0 | 0 | 0 |  | 0% | 0% | 200000% | n/a | 999999 | n/a | 0 | 0 | 0
Storage | Flow Battery, 4 hour, 200 MW | N/A | 200 | 2023 | 2 | 2025 | 25 | 2458.1485 | 0.025543 | 0 | 0 | 64.2737 | 0 | 34 | n/a | 0 | 0 | n/a | 0 | 0 | 0 | 0 |  | 0% | 0 | 400 | n/a | 999999 | n/a | 0 | 0 | 0
Storage | Incremental, double energy capacity (Flow, 4hr, 200MW) | N/A | 200 | 2023 | 2 | 2025 | 25 | 2059.6297 | 0 | 0 | 0 | 7 | 0 | 34 | n/a | 0 | 0 | n/a | 0 | 0 | 0 | 0 |  | 0% | 0 | 400 | n/a | 999999 | n/a | 0 | 0 | 0
Storage | Flow Battery, 4 hour, 500 MW | N/A | 500 | 2023 | 2 | 2025 | 25 | 2201.4189 | 0.063857 | 0 | 0 | 54.703 | 0 | 33 | n/a | 0 | 0 | n/a | 0 | 0 | 0 | 0 |  | 0% | 0 | 1000 | n/a | 999999 | n/a | 0 | 0 | 0
Storage | Incremental, double energy capacity (Flow, 4hr, 500MW) | N/A | 500 | 2023 | 2 | 2025 | 25 | 1808.9825 | 0 | 0 | 0 | 3.38 | 0 | 33 | n/a | 0 | 0 | n/a | 0 | 0 | 0 | 0 |  | 0% | 0 | 1000 | n/a | 999999 | n/a | 0 | 0 | 0
Storage | Flow Battery, 4 hour, 1000 MW | N/A | 1000 | 2023 | 2 | 2025 | 25 | 2281.4214 | 0.12771 | 0 | 0 | 54.8615 | 0 | 32 | n/a | 0 | 0 | n/a | 0 | 0 | 0 | 0 |  | 0% | 0 | 2000 | n/a | 999999 | n/a | 0 | 0 | 0
Storage | Incremental, double energy capacity (Flow, 4hr, 1000MW) | N/A | 1000 | 2023 | 2 | 2025 | 25 | 1891.5288 | 0 | 0 | 0 | 1.66 | 0 | 32 | n/a | 0 | 0 | n/a | 0 | 0 | 0 | 0 |  | 0% | 0 | 2000 | n/a | 999999 | n/a | 0 | 0 | 0
Storage | Gravity Battery, 4 hour, | N/A | 200 | 2023 | 2 | 2025 | 50 | 3473.954 | Included | 0 | 0 | 80.9673 | 0 | 0.3 | n/a | 0 | 0 | n/a | 0 | 0 | 0 | 0 |  | 0% | 0 | 400 | n/a | 999999 | n/a | 0 | 0 | 0
Storage | Incremental, double energy capacity (Gravity, 4hr, 200MW) | N/A | 200 | 2023 | 2 | 2025 | 50 | 1893.7849 | Included | 0 | 0 | 0 | 0 | 0.3 | n/a | 0 | 0 | n/a | 0 | 0 | 0 | 0 |  | 0% | 0 | 400 | n/a | 999999 | n/a | 0 | 0 | 0
Storage | Gravity Battery, 4 hour, | N/A | 500 | 2023 | 2 | 2025 | 50 | 3248.8197 | Included | 0 | 0 | 75.7535 | 0 | 0.24 | n/a | 0 | 0 | n/a | 0 | 0 | 0 | 0 |  | 0% | 0 | 1000 | n/a | 999999 | n/a | 0 | 0 | 0
Storage | Incremental, double energy capacity (Gravity, 4hr, 500MW) | N/A | 500 | 2023 | 2 | 2025 | 50 | 1695.4898 | Included | 0 | 0 | 0 | 0 | 0.24 | n/a | 0 | 0 | n/a | 0 | 0 | 0 | 0 |  | 0% | 0 | 1000 | n/a | 999999 | n/a | 0 | 0 | 0
Storage | Gravity Battery, 4 hour, | N/A | 1000 | 2023 | 2 | 2025 | 50 | 2026.093 | Included | 0 | 0 | 47.246 | 0 | 0.18 | n/a | 0 | 0 | n/a | 0 | 0 | 0 | 0 |  | 0% | 0 | 2000 | n/a | 999999 | n/a | 0 | 0 | 0
Storage | Incremental, double energy capacity (Gravity, 4hr, 1000MW) | N/A | 1000 | 2023 | 2 | 2025 | 50 | 987.8641 | Included | 0 | 0 | 0 | 0 | 0.18 | n/a | 0 | 0 | n/a | 0 | 0 | 0 | 0 |  | 0% | 0 | 2000 | n/a | 999999 | n/a | 0 | 0 | 0
Storage | Adiabatic CAES, RESC, 125 MW, 1000 MWh | 6500' | 125 | 2023 | 3 | 2026 | 30 | 2309.6958 | 1.05 | 0.5 | 0 | 16.912 | 0.30013 | 49.3111 | n/a | 0.011 | 0.011 | n/a | 0 | 0 | 0 | 0 |  | 0% | 0 | 265 | 1501 | 1501 | 3 | 0.1666 | 0 | 0
Storage | Adiabatic CAES, RESC, 125 MW, 1250 MWh | 6500' | 125 | 2023 | 3 | 2026 | 30 | 2331.9615 | 1.05 | 0.5 | 0 | 16.952 | 0.30178 | 49.3111 | n/a | 0.011 | 0.011 | n/a | 0 | 0 | 0 | 0 |  | 0% | 0 | 265 | 1501 | 1501 | 3 | 0.1666 | 0 | 0
Storage | Adiabatic CAES, RESC, 125 MW, 1500 MWh | 6500' | 125 | 2023 | 4 | 2027 | 30 | 2574.0575 | 1.05 | 0.5 | 0 | 16.992 | 0.30343 | 49.3111 | n/a | 0.011 | 0.011 | n/a | 0 | 0 | 0 | 0 |  | 0% | 0 | 265 | 1501 | 1501 | 3 | 0.1666 | 0 | 0
Storage | Adiabatic CAES, RESC, 125 MW, 2000 MWh | 6500' | 125 | 2023 | 4 | 2027 | 30 | 2658.9837 | 1.05 | 0.5 | 0 | 17.072 | 0.30669 | 49.3111 | n/a | 0.011 | 0.011 | n/a | 0 | 0 | 0 | 0 |  | 0% | 0 | 265 | 1501 | 1501 | 3 | 0.1666 | 0 | 0
Storage | Adiabatic CAES, RESC, 125 MW, 3000 MWh | 6500' | 125 | 2023 | 4 | 2027 | 30 | 2854.4872 | 1.05 | 0.5 | 0 | 17.232 | 0.31313 | 49.3111 | n/a | 0.011 | 0.011 | n/a | 0 | 0 | 0 | 0 |  | 0% | 0 | 265 | 1501 | 1501 | 3 | 0.1666 | 0 | 0
Storage | Adiabatic CAES, RESC, 125 MW, 6000 MWh | 6500' | 125 | 2023 | 6 | 2029 | 30 | 3867.0133 | 1.05 | 0.5 | 0 | 17.712 | 0.33174 | 49.3111 | n/a | 0.011 | 0.011 | n/a | 0 | 0 | 0 | 0 |  | 0% | 0 | 265 | 1501 | 1501 | 3 | 0.1666 | 0 | 0
Storage | Adiabatic CAES, RESC, 250 MW, 2000 MWh | 6500' | 250 | 2023 | 4 | 2027 | 30 | 2123.3199 | 1.05 | 0.5 | 0 | 12.494 | 0.36203 | 49.3111 | n/a | 0.011 | 0.011 | n/a | 0 | 0 | 0 | 0 |  | 0% | 0 | 560 | 3002 | 3002 | 3 | 0.1666 | 0 | 0
Storage | Adiabatic CAES, RESC, 250 MW, 2500 MWh | 6500' | 250 | 2023 | 4 | 2027 | 30 | 2163.6598 | 1.05 | 0.5 | 0 | 12.534 | 0.36407 | 49.3111 | n/a | 0.011 | 0.011 | n/a | 0 | 0 | 0 | 0 |  | 0% | 0 | 560 | 3002 | 3002 | 3 | 0.1666 | 0 | 0
Storage | Adiabatic CAES, RESC, 250 MW, 3000 MWh | 6500' | 250 | 2023 | 4 | 2027 | 30 | 2203.4775 | 1.05 | 0.5 | 0 | 12.574 | 0.36609 | 49.3111 | n/a | 0.011 | 0.011 | n/a | 0 | 0 | 0 | 0 |  | 0% | 1 | 560 | 3002 | 3002 | 3 | 0.1666 | 0 | 0
Storage | Adiabatic CAES, RESC, 250 MW, 4000 MWh | 6500' | 250 | 2023 | 5 | 2028 | 30 | 2440.1448 | 1.05 | 0.5 | 0 | 12.654 | 0.3701 | 49.3111 | n/a | 0.011 | 0.011 | n/a | 0 | 0 | 0 | 0 |  | 0% | 2 | 560 | 3002 | 3002 | 3 | 0.1666 | 0 | 0
Storage | Adiabatic CAES, RESC, 250 MW, 6000 MWh | 6500' | 250 | 2023 | 6 | 2029 | 30 | 2734.1716 | 1.05 | 0.5 | 0 | 12.814 | 0.37796 | 49.3111 | n/a | 0.011 | 0.011 | n/a | 0 | 0 | 0 | 0 |  | 0% | 3 | 560 | 3002 | 3002 | 3 | 0.1666 | 0 | 0
Storage | Adiabatic CAES, RESC, 250 MW, 12000 MWh | 6500' | 250 | 2023 | 9 | 2032 | 30 | 3659.6689 | 1.05 | 0.5 | 0 | 13.294 | 0.40042 | 49.3111 | n/a | 0.011 | 0.011 | n/a | 0 | 0 | 0 | 0 |  | 0% | 4 | 560 | 3002 | 3002 | 3 | 0.1666 | 0 | 0
Storage | Adiabatic CAES, RESC, 500 MW, 4000 MWh | 6500' | 500 | 2023 | 5 | 2028 | 30 | 2012.9092 | 1.05 | 0.5 | 0 | 10.285 | 0.4207 | 49.3111 | n/a | 0.011 | 0.011 | n/a | 0 | 0 | 0 | 0 |  | 0% | 5 | 1120 | 6004 | 6004 | 3 | 0.1666 | 0 | 0
Storage | Adiabatic CAES, RESC, 500 MW, 5000 MWh | 6500' | 500 | 2023 | 5 | 2028 | 30 | 2027.0888 | 1.05 | 0.5 | 0 | 10.325 | 0.42295 | 49.3111 | n/a | 0.011 | 0.011 | n/a | 0 | 0 | 0 | 0 |  | 0% | 6 | 1120 | 6004 | 6004 | 3 | 0.1666 | 0 | 0
Storage | Adiabatic CAES, RESC, 500 MW, 6000 MWh | 6500' | 500 | 2023 | 6 | 2029 | 30 | 2168.8288 | 1.05 | 0.5 | 0 | 10.365 | 0.42517 | 49.3111 | n/a | 0.011 | 0.011 | n/a | 0 | 0 | 0 | 0 |  | 0% | 7 | 1120 | 6004 | 6004 | 3 | 0.1666 | 0 | 0
Storage | Adiabatic CAES, RESC, 500 MW, 8000 MWh | 6500' | 500 | 2023 | 7 | 2030 | 30 | 2315.0851 | 1.05 | 0.5 | 0 | 10.445 | 0.42958 | 49.3111 | n/a | 0.011 | 0.011 | n/a | 0 | 0 | 0 | 0 |  | 0% | 8 | 1120 | 6004 | 6004 | 3 | 0.1666 | 0 | 0
Storage | Adiabatic CAES, RESC, 500 MW, 12000 MWh | 6500' | 500 | 2023 | 9 | 2032 | 30 | 2631.3459 | 1.05 | 0.5 | 0 | 10.605 | 0.43818 | 49.3111 | n/a | 0.011 | 0.011 | n/a | 0 | 0 | 0 | 0 |  | 0% | 9 | 1120 | 6004 | 6004 | 3 | 0.1666 | 0 | 0
Storage | Adiabatic CAES, RESC, 500 MW, 24000 MWh | 6500' | 500 | 2023 | 12 | 2035 | 30 | 3629.2541 | 1.05 | 0.5 | 0 | 11.085 | 0.46251 | 49.3111 | n/a | 0.011 | 0.011 | n/a | 0 | 0 | 0 | 0 |  | 0% | 10 | 1120 | 6004 | 6004 | 3 | 0.1666 | 0 | 0
Storage | Pumped Hydro, Southern OR | N/A | 400 | 2023 | 5 | 2028 | 100 | 4303 | 0.51 | 0 | 0 | 18 | 0.25 | 485 | 78% | 2 | 4 | n/a | 0 | 0 | 0 | 0 |  | 0% | 0 | 800 | n/a | 12000 | n/a | 0 | 0 | 0
Storage | Pumped Hydro, Portland North Coast | N/A | 400 | 2023 | 5 | 2028 | 100 | 4303 | 0.51 | 0 | 0 | 18 | 0.25 | 485 | 78% | 2 | 4 | n/a | 0 | 0 | 0 | 0 |  | 0% | 0 | 800 | n/a | 12000 | n/a | 0 | 0 | 0
Storage | Pumped Hydro, Central WY | N/A | 400 | 2023 | 5 | 2028 | 100 | 4303 | 0.51 | 0 | 0 | 18 | 0.25 | 485 | 78% | 2 | 4 | n/a | 0 | 0 | 0 | 0 |  | 0% | 0 | 800 | n/a | 12000 | n/a | 0 | 0 | 0
Storage | Pumped Hydro, Eastern WY | N/A | 400 | 2023 | 5 | 2028 | 100 | 4303 | 0.51 | 0 | 0 | 18 | 0.25 | 485 | 78% | 2 | 4 | n/a | 0 | 0 | 0 | 0 |  | 0% | 0 | 800 | n/a | 12000 | n/a | 0 | 0 | 0
Storage | Pumped Hydro, Central UT | N/A | 400 | 2023 | 5 | 2028 | 100 | 4303 | 0.51 | 0 | 0 | 18 | 0.25 | 485 | 78% | 2 | 4 | n/a | 0 | 0 | 0 | 0 |  | 0% | 0 | 800 | n/a | 12000 | n/a | 0 | 0 | 0
Storage | Pumped Hydro, Southern ID | N/A | 400 | 2023 | 5 | 2028 | 100 | 4303 | 0.51 | 0 | 0 | 18 | 0.25 | 485 | 78% | 2 | 4 | n/a | 0 | 0 | 0 | 0 |  | 0% | 0 | 800 | n/a | 12000 | n/a | 0 | 0 | 0
Storage | Pumped Hydro, MT | N/A | 400 | 2023 | 5 | 2028 | 100 | 4303 | 0.51 | 0 | 0 | 18 | 0.25 | 485 | 78% | 2 | 4 | n/a | 0 | 0 | 0 | 0 |  | 0% | 0 | 800 | n/a | 12000 | n/a | 0 | 0 | 0
Solar | Idaho Falls, ID, 20 MW, 26.1% CF | 4700 | 20 | 2023 | 2 | 2025 | 25 | 1426.6277 | 0 | 0 | 0 | 20.8721 | 0.12 | 29.4 | n/a | Included with CF |  | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 0
Solar | Idaho Falls, ID, 200 MW, 26.1% CF | 4700 | 200 | 2023 | 2 | 2023 | 25 | 1152.1202 | 0 | 0 | 0 | 20.8721 | 0.12 | 29.4 | n/a | Included with CF |  | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 0
Solar | Lakeview, OR, 20 MW, 27.6% CF | 4800 | 20 | 2023 | 2 | 2023 | 25 | 1526.6377 | 0 | 0 | 0 | 20.8721 | 0.12 | 31.5 | n/a | Included with CF |  | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 0
Solar | Lakeview, OR, 200 MW, 27.6% CF | 4800 | 200 | 2023 | 2 | 2023 | 25 | 1234.2252 | 0 | 0 | 0 | 20.8721 | 0.12 | 31.5 | n/a | Included with CF |  | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 0
Solar | Milford, UT, 20 MW, 30.2% CF | 5000 | 20 | 2023 | 2 | 2023 | 25 | 1412.3406 | 0 | 0 | 0 | 20.8721 | 0.12 | 29.1 | n/a | Included with CF |  | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 0
Solar | Milford, UT, 200 MW, 30.2% CF | 5000 | 200 | 2023 | 2 | 2023 | 25 | 1140.3909 | 0 | 0 | 0 | 20.8721 | 0.12 | 29.1 | n/a | Included with CF |  | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 0
Solar | Rock Springs, WY, 20 MW, 27.9% CF | 6400 | 20 | 2023 | 2 | 2023 | 25 | 1469.4891 | 0 | 0 | 0 | 20.8721 | 0.12 | 30.3 | n/a | Included with CF |  | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 0
Solar | Rock Springs, WY, 200 MW, 27.9% CF | 6400 | 200 | 2023 | 2 | 2023 | 25 | 1187.3081 | 0 | 0 | 0 | 20.8721 | 0.12 | 30.3 | n/a | Included with CF |  | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 0
Solar | Yakima, WA, 20 MW, 24.2% CF | 1000 | 20 | 2023 | 2 | 2023 | 25 | 1498.0634 | 0 | 0 | 0 | 20.8721 | 0.12 | 30.9 | n/a | Included with CF |  | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 0
Solar | Yakima, WA, 200 MW, 24.2% CF | 1000 | 200 | 2023 | 2 | 2025 | 25 | 1210.7667 | 0 | 0 | 0 | 20.8721 | 0.12 | 30.9 | n/a | Included with CF |  | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 0
Solar + Storage | Idaho Falls, ID, 200 MW, 26.1% CF + BESS: 100% pwr, 4 hours | 4700 | 200 | 2023 | 2 | 2025 | 25 | 2878.7229 | 0 | 0 | 0 | 63.1909 | 0.06 | 54.0556 | 85% | Included with CF |  | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 0
Solar + Storage | Lakeview, OR, 200 MW, 27.6% CF + BESS: 100% pwr, 4 hours | 4800 | 200 | 2023 | 2 | 2025 | 25 | 2863.7457 | 0 | 0 | 0 | 63.1909 | 0.06 | 56.1556 | 85% | Included with CF |  | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 0
Solar + Storage | Milford, UT, 200 MW, 30.2% CF + BESS: 100% pwr, 4 hours | 5000 | 200 | 2023 | 2 | 2025 | 25 | 2880.8346 | 0 | 0 | 0 | 63.1909 | 0.06 | 53.7556 | 85% | Included with CF |  | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 0
Solar + Storage | Rock Springs, WY, 200 MW, 27.9% CF + BESS: 100% pwr, 4 hours | 6400 | 200 | 2023 | 2 | 2025 | 25 | 2902.1398 | 0 | 0 | 0 | 63.1909 | 0.06 | 54.9556 | 85% | Included with CF |  | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 0
Solar + Storage | Yakima, WA, 200 MW, 24.2% CF + BESS: 100% pwr, 4 hours | 1000 | 200 | 2023 | 2 | 2025 | 25 | 2977.2241 | 0 | 0 | 0 | 63.1909 | 0.06 | 55.5556 | 85% | Included with CF |  | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 0
Wind | Pocatello, ID, 20 MW, CF: 37.1% | 4500 | 20 | 2023 | 2.5 | 2025.5 | 30 | 2161.1032 | 0 | 0 | 0 | 43 | 0.35 | 59.4619 | n/a | Included with CF |  | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 0
Wind | Pocatello, ID, 200 MW, CF: 37.1% | 4500 | 200 | 2023 | 2.5 | 2025.5 | 30 | 1596.7174 | 0 | 0 | 0 | 43 | 0.35 | 59.4619 | n/a | Included with CF |  | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 0
Wind | Arlington, OR, 20 MW, CF: 37.1% | 1500 | 20 | 2023 | 2.5 | 2025.5 | 30 | 2149.2758 | 0 | 0 | 0 | 43 | 0.35 | 59.4619 | n/a | Included with CF |  | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 0
Wind | Arlington, OR, 200 MW, CF: 37.1% | 1500 | 200 | 2023 | 2.5 | 2025.5 | 30 | 1566.924 | 0 | 0 | 0 | 43 | 0.35 | 59.4619 | n/a | Included with CF |  | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 0
Wind | Monticello, UT, 20 MW, CF: 29.5% | 4500 | 20 | 2023 | 2.5 | 2025.5 | 30 | 2186.0348 | 0 | 0 | 0 | 43 | 0.35 | 59.4619 | n/a | Included with CF |  | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 0
Wind | Monticello, UT, 200 MW, CF: 29.5% | 4500 | 200 | 2023 | 2.5 | 2025.5 | 30 | 1626.0388 | 0 | 0 | 0 | 43 | 0.35 | 59.4619 | 85% | Included with CF |  | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 0
Wind | Medicine Bow, WY, 20 MW, CF: 43.6% | 6500 | 20 | 2023 | 2.5 | 2025.5 | 30 | 2129.3224 | 0 | 0 | 0 | 43 | 0.35 | 59.4619 | 85% | Included with CF |  | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 0
Wind | Medicine Bow, WY, 200 MW, CF: 43.6% | 6500 | 200 | 2023 | 2.5 | 2025.5 | 30 | 1567.5293 | 0 | 0 | 0 | 43 | 0.35 | 59.4619 | 85% | Included with CF | Included with CF | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 0
Wind | Goldendale, WA, 20 MW, CF: 37.1% | 1500 | 20 | 2023 | 2.5 | 2025.5 | 30 | 2273.7542 | 0 | 0 | 0 | 43 | 0.35 | 59.4619 | 85% | Included with CF | Included with CF | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 0
Wind | Goldendale, WA, 200 MW, CF: 37.1% | 1500 | 200 | 2023 | 2.5 | 2025.5 | 30 | 1660.3374 | 0 | 0 | 0 | 43 | 0.35 | 59.4619 | 0.85 | Included with CF | Included with CF | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 0
Wind | Offshore, Northern, CA, CF: 47.0% | 0 | 200 | 2023 | 5 | 2028 | 30 | 4635.7362 | 0 | 0 | 0 | 103 | 0.35 | 158.2254 | n/a | Included with CF | Included with CF | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 0
Wind | Offshore, Northern, CA, 1GW, CF: 47.0% | 0 | 1000 | 2023 | 5 | 2028 | 30 | 4633.3938 | 0 | 0 | 0 | 103 | 0.35 | 158.2254 | n/a | Included with CF | Included with CF | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 0
Wind + Storage | Pocatello, ID, 200 MW, CF: 37.1% + BESS: 100% pwr, 4 hours | 4500 | 200 | 2023 | 2.5 | 2025.5 | 30 | 3290.3621 | 0 | 0 | 0 | 85.3188 | 0.175 | 83.4619 | 85% | Included with CF | Included with CF | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 0
Wind + Storage | Arlington, OR, 200 MW, CF: 37.1% + BESS: 100% pwr, 4 hours | 1500 | 200 | 2023 | 2.5 | 2025.5 | 30 | 3165.7181 | 0 | 0 | 0 | 85.3188 | 0.175 | 83.4619 | 0.85 | Included with CF | Included with CF | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 0
Wind + Storage | Monticello, UT, 200 MW, CF: 29.5% + BESS: 100% pwr, 4 hours | 4500 | 200 | 2023 | 2.5 | 2025.5 | 30 | 3331.5687 | 0 | 0 | 0 | 85.3188 | 0.175 | 83.4619 | 85% | Included with CF | Included with CF | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 0
Wind + Storage | Medicine Bow, WY, 200 MW, CF: 43.6% + BESS: 100% pwr, 4 hours | 6500 | 200 | 2023 | 2.5 | 2025.5 | 30 | 3252.1696 | 0 | 0 | 0 | 85.3188 | 0.175 | 83.4619 | 0.85 | Included with CF | Included with CF | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 0
Wind + Storage | Goldendale, WA, 200 MW, CF: 37.1% + BESS: 100% pwr, 4 hours | 1500 | 200 | 2023 | 2.5 | 2025.5 | 30 | 3388.7556 | 0 | 0 | 0 | 85.3188 | 0.175 | 83.4619 | 0.85 | Included with CF | Included with CF | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 0
Wind + Storage | Offshore, Northern, CA, CF: 47.0% + BESS: 100% pwr, 4 hours | 0 | 200 | 2023 | 5 | 2028 | 30 | 6544.8001 | 0 | 0 | 0 | 145.3188 | 0.175 | 182.2254 | 85% | Included with CF | Included with CF | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 0
Solar+Wind+Storage | Idaho Falls, ID Solar + Wind + BESS: 100% pwr, 4 hours | 4700 | 200 | 2023 | 2.5 | 2025.5 | 25 | 6193.6182 | 0 | 0 | 0 | 148.5097 | 0.15667 | 113.5174 | 85% | Included with CF | Included with CF | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 0
Solar+Wind+Storage | Lakeview, OR Solar + Wind + BESS: 100% pwr, 4 hours | 4800 | 200 | 2023 | 2.5 | 2025.5 | 25 | 6051.5808 | 0 | 0 | 0 | 148.5097 | 0.15667 | 115.6174 | 0.85 | Included with CF | Included with CF | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 0
Solar+Wind+Storage | Milford, UT Solar + Wind + BESS: 100% pwr, 4 hours | 5000 | 200 | 2023 | 2.5 | 2025.5 | 25 | 6237.6274 | 0 | 0 | 0 | 148.5097 | 0.15667 | 113.2174 | 85% | Included with CF | Included with CF | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 0
Solar+Wind+Storage | Rock Springs, WY Solar + Wind + BESS: 100% pwr, 4 hours | 6400 | 200 | 2023 | 2.5 | 2025.5 | 25 | 5703.0246 | 0 | 0 | 0 | 148.5097 | 0.15667 | 114.4174 | 85% | Included with CF | Included with CF | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 0
Solar+Wind+Storage | Yakima, WA Solar + Wind + BESS: 100% pwr, 4 hours | 1000 | 200 | 2023 | 2.5 | 2025.5 | 25 | 5897.71 | 0 | 0 | 0 | 148.5097 | 0.15667 | 115.0174 | 85% | Included with CF | Included with CF | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 0
Geothermal | Dual Flash Expansion of Blundell Plant | 4500 | 200 | 2023 | 2.5 | 2025.5 | 40 | 3835.4167 | 0 | 0 | 0 | 115 | 0.060741 | 117 | n/a | 2.5 | 2.5 | 1453.3827 | n/a | n/a | n/a | n/a | 0.17391 | 0.17391 | 34.7826 | 15 | 90 | 90 | n/a | 24 | 6 | 0
Geothermal | Greenfield Binary Plant | 4500 | 200 | 2023 | 2.5 | 2025.5 | 40 | 5567.5641 | 0 | 0 | 0 | 115 | 0.060741 | 117 | n/a | 2.5 | 2.5 | 1453.3827 | n/a | n/a | n/a | n/a | 0.4 | 0.4 | 80 | 15 | 90 | 90 | n/a | 24 | 6 | 0
Nuclear | Small Modular Reactor x 12 | 5000 | 853.75 | 2021 | 7 | 2028 | 60 | 5706.1693 | 7.1056 | 0 | 0 | 68.7739 | 0.77 | 763.0685 | N/A | 5 | 5 | na | 767.1587 | 0 | 0 | 0 | 0 | 10% | 51.84 | 60 | 360 | 360 | 8.64 | 16 | 48 | 0