## Sheet1
Data request for | PacifiCorp
Date sent | 2020-03-13
Response requested by | 2020-03-18
Should you need clarification on this data request, please contact Ryan Arba (ryan.arba@cpuc.ca.gov)
This data request shall be completed according to the process outlined in Resolution WSD 001. In particular: 1. Any discovery or data requests and responses shall be posted on the responding electrical corporation’s website in an easy to follow format that identifies what the discovery was about, what the responses were about, and links to any documents produced. The electrical corporations shall update the website weekly, with an e-mail to the service list of R.18-10-007 with the relevant link and discussion of what is new on the website. The website (or portion of webpage) shall be labeled “2020 Wildfire Mitigation Plan Discovery/Data requests” for each electrical corporation. 2. Electrical corporations must copy any data requests received from or responses to Commission staff to the e-mail address wildfiresafetydivision@cpuc.ca.gov. Requests from staff to the electrical corporations may also come from this address or from individual e-mail addresses. 3. Each electrical corporation shall send to wildfiresafetydivision@cpuc.ca.gov the name of their single point of contact for all data requests and response matters for Commission staff use. 4. Electrical corporations must respond to all data and discovery requests within 3 business days of the request. Both requests and responses shall be sent by e-mail. Exceptions to the 3-business-day requirement will require a letter to the Division Director and a strong showing of the specific reason for the delay. In your response to each data request please specify the relevant item index being responded to, found here in column B. 5. Parties conducting discovery must first analyze the significant data that will be submitted with 2020 WMPs along with the Supplemental Data Request.2 Entities submitting data requests should avoid submissions where such information is contained in the electrical corporations’ WMP filings. 6. All documents the electrical corporation references in its WMP plans shall be collected on the above website in an easy to follow format, with notice to the service list of the location of such documents. This will be in addition to the posting of WMPs on the Commission’s website as required by Pub. Util. Code § 8386(d).
A. Item Index [For CPUC tracking purposes. Please reference this item index with the response provided.] | C. Relevant section of WMP (if applicable) | D. Relevant question in Maturity Survey (if applicable) | E. Relevant meeting or call (if applicable) | F. Specific Data request | G. Format in which the data is to be provided | PacifiCorp Response
PC-43900-Z -651 | 6.4: Current baseline state of service territory and utility equipment | NA | NA | Regarding requests PC-43879-Z -253, PC-43879-Z -260, and PC-43879-Z -261, submit equipment age information in whatever formats are available. Despite not being readily available in a GIS format, it would still be useful to have. | GIS file | Per this request, PacifiCorp has submitted what attribute information is available in GIS format. See PC-43900-Z -660 and the attachmen file: 2020 WMP Attachment PC-43900-Z-651_656_660 CONFIDENTIAL.gdb. Please treat this submission as confidential. For non spatial information, See PC-43900-Z -661.
PC-43900-Z -652 | 6.1: Recent weather patterns | NA | NA | Regarding request PC-43879-Z -267, are direction values provided in any fields of the wind layers? | GIS file | No, there are no wind vectors in the provided information.
PC-43900-Z -653 | 6.2: Recent drivers of ignitions | NA | NA | In future ignitions data submissions (later in 2020 and 2021 and beyond), include fully spelled-out values for various fields instead of numerical codes. | GIS file | The company believed it provided complete data elements, however will endeavor to augment in the future.
PC-43900-Z -654 | NA | NA | NA | Submit data for circuit risk levels for all transmission lines and distribution lines. | GIS file | PacifiCorp does not calculate a circuit risk level. Fire risk was determined only based upon the Fire Threat Tier and its quantity of overhead line exposure.
PC-43900-Z -655 | Various | NA | NA | Submit locations for near misses (areas where damage and/or faults nearly caused a fire). | GIS file | PacifiCorp has no near miss database so to assess ignition probability it treated forced fault events as a proxy.
PC-43900-Z -656 | Various | NA | NA | Submit locations of asset faults. | GIS file | Per this request, PacifiCorp has submitted fault information in GIS format. See attachment file 2020 WMP Attachment PC-43900-Z-651_656_660 CONFIDENTIAL.gdb. Please treat this submission as confidential.
PC-43900-Z -657 | 5.3.5 | NA | NA | Submit locations of vegetation projects (completed in the last 5 years and planned for the future). | GIS file | Regarding PacifiCorp's vegetation management program activities vegetation in distribution circuit rights-of-way are managed on a scheduled four year cycle in California with interim work conducted halfway through the four-year cycle. In addition to cycle and interim work, circuits in HFTD are inspected annually and identified conditions then corrected. Therefore considering cycle, interim, and off cycle inspection and correction activities in HFTD (i.e. vegetation management activities conducted in accordance with the WMP in years between cycle and interim in HFTD), vegetation management activities take place on all circuits within HFTD on an annual basis. Furthermore, all of PacifiCorp's lines are inspected within a 5-year period, which includes identification of imminent vegetation threats. Therefore, the GIS file submitted which includes PacifiCorp's entire service territory within CA would be the best representation of locations where PacifiCorp has conducted vegetation management program work in the last 5 years. Specific to projects, as included in Section 5.3.1, PacifiCorp partnered with CALFIRE in Big Springs, California on the Lake Shastina Fuels Reduction Project to improve escape routes for residents and access for emergency responders. This project involved clearing 100 feet on each side of road of State Highway 97, Big Springs Road and 2 miles west on Jackson Rach Road. However, PacifiCorp does not have spatial data to support submission of a GIS file to describe this project.
PC-43900-Z -658 | 5.3.5 | NA | NA | Submit vegetation risk index data as attributes associated with transmission and distribution lines. | GIS file | PacifiCorp does not calculate a circuit vegetation risk score. Its priority is established based on the presence of any overhead portion of the circuit lying within the HFTD.
PC-43900-Z -659 | 6.4: Current baseline state of service territory and utility equipment | NA | NA | Submit line data showing the current locations of covered conductors. | GIS file | At this time in California the only location that covered conductor exists is outside the HFTD beginning at 06147005.0060201 (41.9395032538202,-121.457117956291) and ending at 06146005.0060400 (41.8561097490604,-121.457154573752).
PC-43900-Z -660 | 6.4: Current baseline state of service territory and utility equipment | NA | NA | Submit additional asset data (fuses, reclosers, splices, transformers, capacitor banks, etc.) beyond what was previously shared and include full field values. The CPUC and CAL FIRE are sensitive to confidentiality concerns, and we are asking for confidential data if that is what is needed to provide available GIS data for all assets. Various other IOUs submitted confidential data as part of their 2020 WMP submissions. The data are intended to be used for internal agency purposes, and we can further discuss confidentiality concerns in the future. Not all data submitted as part of the WMP process are expected to be available to the public or posted online. | GIS file | To accommodate the request, PacifiCorp has pulled all asset information that are currently mapped features and included as a new GIS layer. See attachment file 2020 WMP Attachment PC-43900-Z-651_656_660 CONFIDENTIAL.gdb. This submission shall be treated as confidential. It is critical to note that as PacifiCorp does not actively use the GIS database as a system or records for attribute information, the attribute information in this mapped system may not be consistent across all assets or up to date. Additional asset information that is not spatial has been included in responses to PC-43900-Z -651 & PC-43900-Z -661. Furthermore, GIS databases are consistently updates and amended and, therefore, comparisons of GIS data snapshots from different points in time can prove challenging. PacifiCorp cautions against drawing specific conclusions between comparisons over time. Changes could reflect new and updated information, data QA/QC or changes to asset profile.
PC-43900-Z -661 | 6.4: Current baseline state of service territory and utility equipment | NA | NA | Submit existing non-spatial age data for assets. |  | While many of PacifiCorp’s assets are mapped and included in the GIS submission, PacifiCorp does not necessarily use spatial data to manage the assets attributes such as age, model, type, etc. PacifiCorp uses a combination of the company’s mainframe and FPI, or Facility Point Inspection program, and SAP to manage attributes of poles/structures and substation assets. Assets in FPI, such as distribution facilities, typically correlate to the GIS system. These attributes have been included in the GIS data per PC-43900-Z -660. Asset information regarding pertinent assets managed in SAP has also been pulled and provided in the attachment 2020 WMP- WSD Set 3 - PC-43900-Z-661 Attachment - CONFIDENTIAL.xlsb, including requested attributes to the extent that these attributes are known and populated in the company’s system of record. This submission shall be treated as Confidential.
PC-43900-Z -662 | 6.4: Current baseline state of service territory and utility equipment | NA | NA | Submit any remaining data (not previously submitted) for circuit risk levels (including vegetation risk index data) for all transmission lines and distribution lines | GIS file | PacifiCorp does not calculate a circuit risk level. Fire risk was determined only based upon the Fire Threat Tier and its quantity of overhead line exposure.
PC-43900-​I-685 | 5.3.5 | NA | NA | Provide the current versions of all procedures and bulletins relating to enhanced vegetation management or vegetation management practices for both distribution and transmission facilities in relation to wildfire mitigation, including (but not limited to) PacifiCorp’s Transmission & Distribution Vegetation Management Program Standard Operating Procedures. | Narrative | This has been provided through previous submittal of the Standard Operating Procedures and Wildfire Mitigation Plan.
PC-43900-​I-686 | 5.3.5 | NA | NA | In section 5.3.5 on page 212, PacifiCorp states that “In areas without an elevated risk, regular vegetation management work on any particular circuit is done every two years”. In this instance, does PacifiCorp mean “elevated risk” to mean within a HFTD? What else would qualify as an “elevated risk”? | Narrative | Yes. In this instance "elevated risk" is synonymous with HFTD.
PC-43900-​I-687 | 5.3.5 | NA | NA | In section 5.3.5 on page 212, PacifiCorp states that “wider rights-of-way allow PacifiCorp to generally maintain clearances well in excess of the Minimum Vegetation Clearance Distance (MVCD)”. What “wider rights-of-way” does PacifiCorp maintain (i.e. what distances does PacifiCorp follow for such clearances)? | Narrative | The reference to wider rights-of-way in this context is inferring that in general, clearances in excess of the Minimum Vegetation Clearance Distance (MVCD) required in Table 2 of FAC-003-04 for transmission lines are able to be maintained due to the wider rights-of-way for transmission lines in comparison to distribution lines.
PC-43900-​I-688 | 5.3.5 | NA | NA | In section 5.3.5 on page 212, PacifiCorp states that VM work for transmission lines is “scheduled on an as-needed basis.” Provide all procedures PacifiCorp uses in determining whether or not VM transmission work is needed. | Narrative | Applicable processes are identified within the Standard Operating Procedures.
PC-43900-​I-689 | 5.3.5 | NA | NA | In section 5.3.5 on page 213, PacifiCorp states that VM crews “receive training related to fire prevention and suppression.” Provide all materials used for such training. | Narrative | The vegetation management contractor provides basic fire prevention and suppression training to their crews when working in fire prone rural areas. PacifiCorp does not have copies of contractor developed training material at this time.
PC-43900-​I-690 | 5.3.5 | NA | NA | Provide all procedures PacifiCorp has regarding IVM, as discussed on pages 212 and 213 in section 5.3.5. | Narrative | Miller, Randall. Best Management Practices Integrated Vegetation Management. International Society of Arboriculture (available for purchase through ISA); and Standard Operating Procedures section 6.5.
PC-43900-​I-691 | 5.3.5 | NA | NA | Provide all of the “Many other strategies and tactics described in the Standard Operating Procedures” that support reduction of vegetation-related faults, as discussed in section 5.3.5 on page 213. | Narrative | PacifiCorp’s vegetation management program is modeled on the industry’s best practices, including systematic maintenance, scientifically-based pruning, tree removal, tree replacement, cover type conversion, herbicide use and tree growth regulator applications, and the use of specialized tools and equipment. Implementing these best practices support reduction of vegetation-related faults and are incorporated within the Standard Operating Procedure.
PC-43900-​I-692 | 5.3.5 | NA | NA | Provide a list of all dates in which the VM Standard Operating Procedures, as discussed in section 5.3.5, have been revised | Narrative | Appendix B of the Standard Operating Procedures contains a revision history, including the dates of when revisions were made.
PC-43900-​I-693 | 5.3.5 | NA | NA | Provide a description of all of the revisions completed for Revision 07 to the Standard Operating Procedures, as discussed in section 5.3.5. | Narrative | Appendix B of the Standard Operating Procedures contains a revision history, including a summary of revisions that were made.
PC-43900-​I-694 | 5.3.5 | NA | NA | 10) In section 5.3.5 on page 213, PacifiCorp states that it “has implemented other new elements to its vegetation management program. Along these lines, PacifiCorp performed specific wildfire mitigation projects in 2018 and 2019.” a. List all “other new elements” PacifiCorp implemented to its VM program. b. Describe how any such elements exceed current regulations. c. Provide a list of all “specific wildfire mitigation projects” relating to VM performed in 2018 and 2019 respectively. | Narrative | a.) PacifiCorp's vegetation management programs continue to evolve alongside regulation, which often requires the company implement new or enhanced elements of its existing vegetation management programs, or introduce new programs altogether. At times, PacifiCorp takes additional steps due which are not specifically required through regulation, to either address elevated risk or because the additional steps reflect the most effective way to meet the new regulations. Examples of these new elements include enhanced and additional vegetation management inspections (as described further in Section 5.5.5.2, 5.3.5.3, and 5.3.5.6), expansion of subject pole clearing beyond SRA to LRA as discussed in Section 5.3.5.9, progression of LiDAR pilot projects to understand effectiveness of using new technology to inform and optimize vegetation management programs as described in Section 5.3.4.7, and additional parallel activities to realize additional benefits through enhanced data analytics to inform vegetation density, vegetation diversity, and overall risk as identified as a lesson learned in 2019 in Section 5.0. These particular elements are not specifically required by regulation and, therefore, PacifiCorp views these as exceeding regulation. As regulation continues to evolve, PacifiCorp anticipates that the company's vegetation management programs will change. b.) See (a.) c). See response to PC-43900-Z -657 and Section 5.3.1.
PC-43900-​I-695 | 5.3.5 | NA | NA | Provide a list of all vegetation management related permits PacifiCorp received in 2018 and 2019, including dates and participating entities. | Narrative | In the context of collaborating with local land managers, "permits", refers to approval received from the land manager to conduct requested vegetation management activities on agency managed lands. PacifiCorp does not centrally track "permit" acquisition and therefore does not have a list to provide at this time. Additional review time would be required.
PC-43900-​I-696 | 5.3.5 | NA | NA | Provide a list with dates and participants of all “Annual meetings” that PacifiCorp “held with some agencies to enhance communication” regarding vegetation management work in 2018 to 2020, as described on pages 213 to 214 in section 5.3.5. | Narrative | PacifiCorp coordinates with land managing agencies on an as needed basis during the course of a calendar year to communicate vegetation management activities. The form (email, phone, in person) of communication may vary. Participants typically include a realty specialist who then coordinate with applicable resource specialists. Examples include coordination with Six Rivers National Forest forester Brenda Devalin in April 2018 and California State Parks in June 2019. PacifiCorp does not centrally track meeting/correspondence dates and participants and therefore does not have a list to provide at this time. Additional review time would be required.
PC-43900-​I-697 | 5.3.5 | NA | NA | Provide the MOU on Vegetation Management for Powerline Rights-of-Way, as described on page 214 in section 5.3.5. Has the MOU changed at all as a result of new vegetation management efforts for the WMP? | Narrative | The MOU may be downloaded from the Edison Electric Institute website at: https://www.eei.org/issuesandpolicy/environment/land/Pages/VegManagement.aspx The MOU was finalized in 2016.
PC-43900-​I-698 | 5.3.5 | NA | NA | 14) In section 5.3.5 on page 215, PacifiCorp states that it “anticipates completion of an O&M Plan with the Klamath National Forest by end of year, 2020.” a. Is PacifiCorp planning on using the same O&M Plan for other agencies? b. Provide a list of all other agencies either working in collaboration on this O&M Plan, or in which PacifiCorp is developing an O&M Plan. c. How does this O&M Plan differ from the Standard Operating Procedures? d. Will the O&M Plan replace, supplement, or cause need to revise the Standard Operating Procedures? | Narrative | a. Yes. The intent is to utilize the same O&M Plan for consistency. b. At this stage of development, Klamath National Forest is the entity PacifiCorp is collaborating with. c. The purpose of the O&M Plan will be to streamline the approval process for conducting O&M activities, including vegetation management, on agency managed land. d. The O&M Plan incorporates by reference the Standard Operating Procedures. Updates to the Standard Operating Procedures are not anticipated at this time.
PC-43900-​I-699 | 5.3.5 | NA | NA | How is PacifiCorp performing community outreach regarding vegetation management? | Narrative | PacifiCorp's foresters are involved with local communities during Arbor Day celebrations, coordinate with city foresters on community events, participate in and sponsor tree planting events, attend wildfire community meetings and county fire safe council meetings, or support Regional Business Managers' community outreach efforts. PacifiCorp has a variety of educational materials about tree-power line conflicts and planting the right tree in the right place, which are available to communities. PacifiCorp also makes available to the community information explaining the need for line clearance work, as well as natural target pruning.
PC-43900-​I-700 | 5.3.5 | NA | NA | Hoe does PacifiCorp track engagement and input from the community regarding vegetation management practices? | Narrative | PacifiCorp provides property owners (or tenants) with a survey card on each property on which utility tree work is performed. Surveys provide customers the opportunity to provide feedback regarding vegetation management performance. Survey responses are received, logged, and foresters follow-up with identified customer concerns as needed.
PC-43900-​I-701 | 5.3.5 | NA | NA | Provide all procedures relating to a Level 1 and Level 2 assessment, as described in section 5.3.5.2 on page 217. | Narrative | PacifiCorp follows guidance as outlined in ANSI 300 (Part 9) regarding Level 1 and Level 2 assessments and the International Society of Arboriculture's Tree Risk Assessment guide.
PC-43900-​I-702 | 5.3.5 | NA | NA | How does PacifiCorp define an “Action Threshold”? Provide all procedures relating to determining such. | Narrative | Action thresholds are designed to trigger vegetation management action and provide roughly a ten-foot buffer from the Minimum Vegetation Clearance Distance. Clearance work is performed, anytime vegetation is located within the Action Threshold distance from the conductor.
PC-43900-​I-703 | 5.3.5 | NA | NA | In section 5.3.5.3 under the “Prioritization Approach,” PacifiCorp includes “New inspection elements focused on HFTD locations.” Describe what this entails. | Narrative | "New inspection elements focused on HFTD locations" is referring to the annual vegetation management inspections for overhead lines in HFTD.
PC-43900-​I-704 | 5.3.5 | NA | NA | How and what is PacifiCorp tracking to demonstrate effectiveness of the detailed inspections outlined in 5.3.5.2 and 5.3.5.3? | Narrative | Demonstrated effectiveness of inspections is the identification of corrective work and reduction in ignition potential through the identification and mitigation of vegetation related conditions. PacifiCorp conducts post work audits to identify and correct exceptions.
PC-43900-​I-705 | 5.3.5 | NA | NA | In section 5.3.5.4 on page 223, PacifiCorp stats that “vegetation management is involved to support the emergency event, generally performing additional inspections and vegetation management or clearing activity with qualified personnel and crews as required by operations.” a. Provide all procedures relating to such involvement. b. Provide all examples of such work performed by PacifiCorp in 2019. c. How does PacifiCorp determine what work will be completed during these times? d. How does PacifiCorp allocate crews and staff to be available or on-standby for such events? | Narrative | a. PacifiCorp conducts vegetation management inspections in conjunction with potential emergency events (i.e. potential PSPS events) under the direction of local management. Refer to section 5.3.6.3 and 5.6.2. b. Examples of this work include the removal of hazard trees and correction of potential clearance encroachments. c. Vegetation management actions are determined as the result of inspections. d. On the onset of a potential emergency event, tree crew resources are reviewed and vegetation contractors are notified of potential resource needs.
PC-43900-​I-706 | 5.3.5 | NA | NA | Is PacifiCorp intending to develop specific Emergency response vegetation management, as described in section 5.3.5.4 on page 223? If so, what is the timeline for that? | Narrative | PacifiCorp’s emergency response programs and grid operations and protocols, the emergency response vegetation management due to red flag warning or other urgent conditions is a subset and component of both the company’s general emergency response plans and the company’s grid operations and protocols wildfire mitigation program focused on personnel work procedures and training conditions of elevation fire risk.
PC-43900-​I-707 | 5.3.5 | NA | NA | How does PacifiCorp dispose of slash properly? Provide all supporting procedures. Does PacifiCorp currently have any coordination with other entities or agencies for such work? | Narrative | Slash is disposed of in accordance with the Standard Operating Procedures unless otherwise required by the landowner or land managing agency.
PC-43900-​I-708 | 5.3.5 | NA | NA | What fuel reduction activities adjacent to or within their corridors or around infrastructure does PacifiCorp perform? Provide all such procedures. | Narrative | Through implementing the Standard Operating Procedures and WMP, PacifiCorp identifies and removes hazard trees in and along corridors, conducts pole clearing activities, and implements IVM practices that result in lower growing species compatible with electrical infrastructure thereby reducing inventory.
PC-43900-​I-709 | 5.3.5 | NA | NA | Provide the analysis performed on the 2018 pilot trials discussed on page 225 in section 5.3.5.6 to determine effectiveness of PacifiCorp’s VM program, and discuss how the pilot was different from PacifiCorp's practices and procedures before. | Narrative | PacifiCorp identified three new elements into its long-term vegetation management program that had not been emphasized in the past, including overhang reduction, off-cycle inspections, and higher risk tree removals. These new pilot trials informed the evolution of PacifiCorp's vegetation management programs to meet the growing risk of wildfire related events as well as changing regulation. Additional elements are described in response to PC-43900-​I-694.
PC-43900-​I-710 | 5.3.5 | NA | NA | Regarding page 225 in section 5.3.5.6, what “minimum ending distances applicable to distribution cycle work completed in the HFTD” did PacifiCorp have before and after increasing it as part of the VM program? | Narrative | For current clearance distances please refer to tables 5.1 and 5.2 of the Standard Operating Procedure current clearance differences. Compared to previous clearance distances identified in the past version of the Standard Operating Procedure, clearance distances either remained the same or were increased anywhere from 2 to 4 feet.
PC-43900-​I-711 | 5.3.5 | NA | NA | Regarding page 225 in section 5.3.5.6, how did PacifiCorp expand annual pole clearing and on what subject poles as part of the VM program? | Narrative | Pole clearing activities were expanded to include subject poles located in Local Response Areas in addition to State Response Areas.
PC-43900-​I-712 | 5.3.5 | NA | NA | Does PacifiCorp plan on implementing any discretionary inspections of vegetation for distribution or transmission equipment, as described in sections 5.3.5.8 and 5.3.5.9? If so, provide a list of such inspections PacifiCorp is evaluating. If not, provide justification as to why. | Narrative | PacifiCorp is currently evaluating the applicability and use of LiDAR as a means to conduct and/or augment vegetation management and inspections. At this time, PacifiCorp does not have any other discretionary inspection of vegetation around transmission electric lines and equipment, beyond inspections mandated by rules and regulations, and other described programs.
PC-43900-​I-713 | 5.3.5 | NA | NA | What percentage of VM work is audited, as described in section 5.3.5.13? | Narrative | PacifiCorp conducts audits of all vegetation management cycle work conducted within HFTD to ensure specifications are met.
PC-43900-​I-714 | 5.3.5 | NA | NA | Provide all VM training materials described in section 5.3.5.14, as provided by PacifiCorp. | Narrative | PacifiCorp provides environmental awareness, Migratory Bird Treaty Act training, and safety trainings (e.g. CPR and first aid) to PacifiCorp foresters. Training provided to PacifiCorp foresters specific to implementing vegetation management activities (e.g. tree risk assessments)is delivered by third parties in the form of certifications and ongoing education opportunities.
PC-43900-​I-715 | 5.3.5 | NA | NA | In regards to seciong 5.3.5.14: a. Regarding VM personnel, what certifications does PacifiCorp require for both inspectors and tree crew? b. How does PacifiCorp verify contractors and subcontractors meet such criteria? c. What is the number of both inspectors and tree crew PacifiCorp had contracted or employed in 2019? d. What is the number of both inspectors and tree crew PacifiCorp currently has contracted and employed? e. Has PacifiCorp run into constraints due to lack of workforce resources? If so, how does PacifiCorp intend to tackle such contraints moving forward? | Narrative | a.Please refer to sections 1.2 and 1.2.1 of the Standard Operating Procedures. b. Requirements as identified in the Standard Operating Procedures are incorporated into contracts vegetation management providers. Other certifications include herbicide applicator license, and a first aid/CPR card. Journeyman certification is monitored by the local union. Tree crew certifications are verified during crew visits conducted by PacifiCorp foresters. c. During the course of the year (2019) PacifiCorp, the number of inspectors and crews varied between 2-4 inspectors and 10-25 crews. d. In California the company currently has 4 inspectors and 15 crews. e. Yes. PacifiCorp is exploring additional contractor options including contractors that PacifiCorp has not historically used and out of state or country contractors. PacifiCorp is also reviewing contracting strategies (including firm fixed, T&E and unit) to provide a stable contract environment that keeps contractors in place for longer durations, and entices newer employees to see this as a stable career path.
PC-43900-​I-716 | 5.3.5 | NA | NA | How does PacifiCorp determine whether or not a tree has "strike potential" as described in section 5.3.5.16? | Narrative | Trees with the potential to strike the conductors are identified by our ISA certified arborists and ISA certified utility specialist utilizing applicable ISA guidance.
PC-43900-​I-717 | 5.3.5 | NA | NA | Regardubg section 5.3.5.19: a. When does PacifiCorp intend to implement an electronic tracking system, as described in section 5.3.5.2 on pg 219? b. What system does PacifiCorp currently use to track VM work? c. If PacifiCorp does not have a defined inventory currently, describe the inventory system PacifiCorp currently has to track VM and inspections. | Narrative | a. PacifiCorp is currently utilizing the electronic tracking system to track vegetation management work through completion and is continually working to improve capabilities of the tracking system. Full roll out and use of the tracking system by all tree crews is anticipated by the end of Q2. b. and c. PacifiCorp utilizes an in-house developed Vegetation Management system and also utilizes Map It Fast (referenced in part a of response).
PC-43900-​I-718 | 5.3.5 | NA | NA | Provide a list of all of PacifiCorp's vegetation species' known growth rates, as described in section 5.3.5.20. | Narrative | PacifiCorp employs vegetation management personnel who meet certification criteria as presented in the Standard Operating Procedures. Trees are pruned to applicable clearance distances for slow, moderate, or fast growing species based on vegetation management personnel expertise. As indicated in the company's 2020 WMP, PacifiCorp does not currently have an electronic database that preserves the data in a way required to answer this question. However, PacifiCorp has incorporated the need for an electronic solution into a program described in Section 5.3.5.6.
PC-43900-​I-719 | 5.3.5 | NA | NA | In what cases and by how much would PacifiCorp apply an increased clearance for moderate and fast growing species, respectively? | Narrative | Clearances are outlined in the Standard Operating Procedure as provided. If a moderate or fast growing tree species is located directly under conductor increased clearances or total removal would be pursued.
PC-43900-​I-720 | 5.3.5 | NA | NA | What sort of VM training on safety, fire prevention, best practices, etc. is provided to employees or contractors? Provide all such training procedures and documents. | Narrative | Please refer to response for question PC-43900-​I-714.
PC-43900-​I-721 | 5.3.5 | NA | NA | Provide the data and explanation showing PacifiCorp's "historic succss" as described on pg 244 of section 5.3.5.20. | Narrative | "Historic success" in this context is referring to minimal findings during CPUC audits. Additional review time would be needed to compile historical audit results.
PC-43900-​I-722 | 5.3.5 | NA | NA | What percentage of property owners have prevented VM work from being completed? Provide all procedures and materials on property owner refusals. | Narrative | PacifiCorp is currently implementing a system and process to track this information electronically. Roll out and implementation of this system is currently ongoing.
PC-43900-​I-723 | 5.3.5 | NA | NA | How does PacifiCorp intend to "be more aggressive in generally reducing total inventory"? How will PacifiCorp change current assessments to better identify, address, and remediate hazard trees? | Narrative | As PacifiCorp has increased the frequency and scope of its inspections of overhead lines within the HFTD, PacifiCorp fully anticipates that additional vegetation will be identified as either hazardous or in need of corrective work. Furthermore, PacifiCorp will direct inspectors to identify more removal opportunities to reduce inventory. Through this and increased frequency of inspections, a higher volume of high risk trees will be removed. In an effort to augment hazard tree identification, PacifiCorp is assessing LiDAR technology as a potential tool.
PC-43900-​I-724 | 5.3.5 | NA | NA | What are "cycle buster trees" as described on pg 245 of section 5.3.5.20 and what species would fall under such category? Provide all procedures PacifiCorp has on identification and remediation of such trees. | Narrative | "Cycle busters" are trees that grow at a rate that, when identified during interim vegetation management activities, will not hold for the duration of the cycle and are at higher risk of encroaching upon clearance distances if left untreated until the next cycle. Management procedures include ongoing pruning, whole tree removal, and use of chemical treatments such as TGR (Tree Growth Regulator).
PC-43900-​I-725 | 5.3.5 | NA | NA | How many poles is PacifiCorp intending to implement pole clearing for, as described in section 5.3.5.21? | Narrative | PacifiCorp vegetation management has expanded pole clearing to include 2,768 Local Responsibility Area (LRA) subject equipment poles located in the HFTD in additional to its existing program in compliance with regulations of clearing 12,292 State Responsibility Area (SRA) subject poles.
PC-43900-​D-759 | 5.3.2 | NA | NA | In the table under section 5.3.2.1 on page 121 under Description, PacifiCorp states that it intends on “placing needed stations to support needed level of granularity”. Has PacifiCorp calculated the “needed level of granularity”? If so, provide such in terms of weather stations needed, location, and number per circuit mile. | Narrative | PacifiCorp has not yet established the level of granularity required to support fire risk management. As asset hardening takes place such situational awareness and weather station saturation becomes less important. Peer utilities have suggested that one or more weather station per circuit is needed to make important operational decisions, such as PSPS. In such a case it could be expected that 30 or more stations may be needed to support these actions.
PC-43900-​D-760 | 5.3.2 | NA | NA | In the table under section 5.3.2.1 on page 121 under Description, provide all “appropriate triggers to initiate specific responses” that PacifiCorp has identified so far, including amounts and responses. | Narrative | At this time PacifiCorp's triggers rely on KBDI, FFWI6 and wind speed (either sustained or gust levels). Historically it had found that KBDI >= 622, FFWI6 >=30, sustained wind of 16 mph or gusts of 31 mph could result in large fires in far northern California (north of the 40th latitude).
PC-43900-​D-761 | 5.3.2 | NA | NA | How is PacifiCorp prioritizing areas within Tier 2, as described under the Prioritization Approach section of the table for section 5.3.2.1 on page 121? | Narrative | PacifiCorp has generally prioritized based upon overhead line exposure (for each Tier), numbers of poles, devices and customers.
PC-43900-​D-762 | 5.3.2 | NA | NA | Regarding the table in section 5.3.2.1 on page 122 under the section titled “General”: a. If the current 10 weather stations installed are not RAWS-quality stations, what do the micro-station installations measure and how do they differ from RAWS stations? b. Would augmenting entail enhancing granularity or would RAWS stations be installed nearby or adjacent to existing micro-stations? | Narrative | The current 10 weather stations deployed by PacifiCorp in 2019 measure Temperature, Relative Humidity, Wind Speed and Wind Direction, Precipitation and approximately half of them have Fuel Moisture Sensors to measure dead fuel. From the two sensors on each station additional variables (Dew Point and Wet Bulb Temperature) are calculated. This data is reported every 10 minutes using MesoWest and then used internally to PacifiCorp to inform its operations. A RAWS by contrast measures the following variables: Temperature, Relative Humidity, Wind Speed and Wind Direction, Solar Radiation, Precipitation, Fuel Moisture and Fuel Temperature. All of the sensors used must meet the accuracy specs, collection requirements, calibration requirements and measurement intervals specified by the National Wildland Coordinating Group (NWCG) in PMS426-3 (standards for fire weather RAWS). https://nwcg.gov/sites/default/files/publications/pms426-3.pdf Additional variables that can be calculated from RAWS data can include those from above, but also importantly include 10 hour, 100 hour and 1000 hour fine dead fuel measurements which are a critical measurement in assessing wildfire risk and fire behavior. The data reported by a RAWS is collected hourly using the GOES Wildland Fire Management Information system and is used to inform decisions made by interagency wildland fire management. This includes fire behavior assessments and National Fire Danger Rating System fire hazard levels. National preparedness levels are only set using data from verified and calibrated RAWS and those national preparedness levels dictate what resources are going to be available from State and Federal agencies to prepare for and respond to wildfire in a given region. Essentially the data from a micro station is used locally within PacifiCorp to make decisions, and by widely sharing the data collected through MesoWest, academics and other scientists. The data from a RAWS can be used locally too, but is also used at a national level and by alignment with that standard supports the broader mission of wildland fire science. Without extensibility of the RAWS system across PacifiCorp assets there is limited preparedness and response resources available from agencies like CalFire, USFS, BLM, etc. Essentially these stations ensure alignment between our response planning efforts and other agencies. By adding RAWS stations to the existing micro-station network PacifiCorp will be enhancing the granularity to support PacifiCorp's decision making systems, and providing a highly referenceable (ground-truth) data set to validate existing micro stations, study which could be conducted via PacifiCorp or academic institutions. The company will review the siting recommendations in PMS426-3 to propose locations to stakeholders, which may mean locating them close to the existing stations, but may also be not near micro stations. If the best sites for the RAWS were in pre-existing micro station locations PacifiCorp can consider moving the micro station to another location to increase coverage in that way, but it's likely that at least one of the new RAWS quality stations will be near a micro station location.
PC-43900-​D-763 | 5.3.2 | NA | NA | Regarding the table in section 5.3.2.1 on page 122, under the “Before the next annual update” section: a. How many weather stations does PacifiCorp intend to install in 2020? b. Where will the weather stations be located and how were locations determined? c. Will such stations be RAWS-quality? | Narrative | PacifiCorp plans to install 10 additional weather stations, 3 of which are intended to be RAWS quality, while the remaining would be micro stations consistent with those installed during 2019. The locations have not yet been identified precisely but are generally expected to be informed by the weather professionals who previously offered input to their siting, specifically the National Weather Service, Western Weather and REAX engineering. In addition, the RAWS quality stations will be informed by input from the United States Forest Service and the National Interagency Fire Center. It is not anticipated that the RAWS sites will be adjacent to the company's micro stations, but rather that they will be placed in manner to complement existing RAWS stations and be useful in developing more granular analysis for weather patterns relating to fire risks.
PC-43900-​D-764 | 5.3.2 | NA | NA | When does PacifiCorp intend to complete its DFA pilot, as described in section 5.3.2.2? | Narrative | PacifiCorp is working with the DFA vendor to resolve IT security issues with setting a relay within the substation boundary. It is anticipated that the equipment will be able to be installed later this year and the pilot will require at least one year of assessment to determine the viability of the technology and its expansion across the system.
PC-43900-​D-765 | 5.3.2 | NA | NA | In the table for section 5.3.2.4 on page 125 under the “Rationale for Program section, PacifiCorp states that “metrics can play an important role in limiting operations that could be inappropriate under elevated fire risk conditions”. a. What are all of the operations that would fall under this category? b. Provide all procedures PacifiCorp enforces for operations under high fire risk. | Narrative | The operations which fall under this category include but are not limited to non-reclose policies, altered work schedules and needed equipment (such as water tanks) alternate protection settings and PSPS. The specific operational actions are detailed in 5.3.6 on pages 257-265.
PC-43900-​D-766 | 5.3.2 | NA | NA | What “fire science and weather professionals” evaluated PacifiCorp’s data, as described in the “Plan for audits/quality checks” section in the table for section 5.3.2.4 on page 125? Why is PacifiCorp not planning on any additional audits? | Narrative | The company's weather data analysis and approaches were evaluated by REAX engineering, Western Weather and representatives from the National Weather Service. At this time it has not been established that such an "audit" would serve any particular purpose. PacifiCorp does intend to continue to evaluate weather data and is participating in several industry venues to support peer review, including participating as a member of the Technical Advisory Committee on the California Energy Commission's EPIC-funded study to develop "Next Generation Wildfire Risk Modeling", participation at the California Utilities' Forecaster Meeting and with the Edison Electric Institute's (EEI) Wildfire Technology Group.
PC-43900-​D-767 | 5.3.2 | NA | NA | If PacifiCorp is not using an FPI, what, in detail, is PacifiCorp’s approach? | Narrative | PacifiCorp uses fire weather data to establish elevated risk. This includes the impact of dryness on live fuel (Keetch Byram Drought Index) in combination with Fosberg Fire Weather Index, averaged over 6 hours, in addition to winds, either sustained or gusts. As discussed in the Smalls Call on 3/11/2020 this combination functions similar to an FPI.
PC-43900-​D-768 | 5.3.2 | NA | NA | Regarding section 5.3.2.5 on pages 127 and 128: a. When would staff be activated to monitor equipment during elevated risk periods? i.e. provide any triggers or decision-making tree PacifiCorp uses to determine the need for such. b. Provide all procedures PacifiCorp uses for evaluations during elevated risk periods. c. How many such evaluations did PacifiCorp use in 2018 and 2019? Provide the number of circuit miles monitored, summaries or notes from such evaluations, dates, and weather at the time of such monitoring activities. | Narrative | Staff would be activated to monitor equipment during elevated risk periods based on the thresholds described in section 4.4.3 (page 79) which describes the weather triggers for PSPS Watch Level 1 and 2. The procedure for evaluation is to conduct a standard visual assurance inspection of the facilities, note any conditions that require correction, prioritize the correction, and complete work as required. PacifiCorp has not had a PSPS event; however on September 12, 2019 resources were deployed for learning purposes and an over abundance of caution to the Weed area as weather thresholds were approaching triggers. Forty five miles of circuits had a visual inspection conducted with minimal conditions found requiring correction. Since this was not part of an official event, notes were not aggregated; however as part of on-going enhancements all future activities will have a summary report published for reporting purposes.
PC-43900-​D-769 | 5.3.2 | NA | NA | Provide screenshots of PacifiCorp's weather monitoring systems, including those used for PSPS decisions, as described on the phone call with WSD, CPUC, and CALFIRE on March 12, 2020. | Narrative | Please refer to PacifiCorp's response to WSD Verbal Request 1 provided March 16, 2020.
PC-43900-​E-783 | 5.3.9 Emergency Planning and Preparedness | NA | NA | “As part of these events, individuals identified with primary or secondary responsibility within the command center structure complete an annual review of the overall disaster response and recovery plan. These individuals are required to contribute to post-crisis and emergency reporting, outlining any issues or concerns regarding their role and responsibilities”. (p304-5 & 307) Describe how PacifiCorp accesses the success of these annual trainings specifically has the annual refresher training deemed adequate? | Narrative | Please refer to PacifiCorp's response to WSD Index Item PC-43895-E-396.
PC-43900-​E-784 | 5.3.9 Emergency Planning and Preparedness | NA | NA | Provide the number of emergency planning meetings and trainings PacifiCorp attends, include community based organizational meetings. | Narrative | Please refer to PacifiCorp's response to WSD Index Item PC-43895-E-397.
PC-43900-​E-785 | 5.3.9 Emergency Planning and Preparedness | NA | NA | Detail an example where PacifiCorp has incorporated “existing customer service processes and local leaders:” feedback in the 2020 WMP 2020 California Wildfire Mitigation Plan. | Narrative | Please refer to PacifiCorp's response to WSD Index Item PC-43895-E-398.
PC-43900-​E-786 | 5.3.9 Emergency Planning and Preparedness | NA | NA | Provide an updated Table 29 which contains the missing column heading titled “Total per initiative spend”. | Narrative | Please refer to PacifiCorp's response to WSD Index Item PC-43895-E-399.
PC-43900-​E-787 | 5.3.9 Emergency Planning and Preparedness | NA | NA | Provide additional details on “information provided to customers regarding wildfire prevention and response to customers” (page 300). Specify topics addressed. For example, if PacifiCorp address wildfire resilience and awareness with their customers? | Narrative | Please refer to PacifiCorp's response to WSD Index Item PC-43895-E-400.
PC-43900-​E-792 | 5.3.9 Emergency Planning and Preparedness | NA | NA | “As part of these events, individuals identified with primary or secondary responsibility within the command center structure complete an annual review of the overall disaster response and recovery plan. These individuals are required to contribute to post-crisis and emergency reporting, outlining any issues or concerns regarding their role and responsibilities”. (p304-5 & 307) Describe how PacifiCorp accesses the success of these annual trainings specifically has the annual refresher training deemed adequate? | Narrative | Please refer to PacifiCorp's response to WSD Index Item PC-43895-E-396.
PC-43900-​E-793 | 5.3.9 Emergency Planning and Preparedness | NA | NA | Provide the number of emergency planning meetings and trainings PacifiCorp attends, include community based organizational meetings. | Narrative | Please refer to PacifiCorp's response to WSD Index Item PC-43895-E-397.
PC-43900-​E-794 | 5.3.9 Emergency Planning and Preparedness | NA | NA | Detail an example where PacifiCorp has incorporated “existing customer service processes and local leaders:” feedback in the 2020 WMP 2020 California Wildfire Mitigation Plan. | Narrative | Please refer to PacifiCorp's response to WSD Index Item PC-43895-E-398.
PC-43900-​E-795 | 5.3.9 Emergency Planning and Preparedness | NA | NA | Provide an updated Table 29 which contains the missing column heading titled “Total per initiative spend”. | Narrative | Please refer to PacifiCorp's response to WSD Index Item PC-43895-E-399.
PC-43900-​E-796 | 5.3.9 Emergency Planning and Preparedness | NA | NA | Provide additional details on “information provided to customers regarding wildfire prevention and response to customers” (page 300). Specify topics addressed. For example, if PacifiCorp address wildfire resilience and awareness with their customers? | Narrative | Please refer to PacifiCorp's response to WSD Index Item PC-43895-E-400.
PC-43903-Y-11 | 6.6: Planned 2020 WMP initiative activity per year | NA | NA | Provide planned initiative data at the most granular level possible for each initiative activity (e.g., each asset location for each activity under an initiative). The exact schema for the spatial data can be found in the attaced excel file, "20200311_Initiative_schema", in the sheet "Initiative schema for utilities". The priority for each field is listed in the "priority" column. An example of the table is provided in the sheet "Initiative Template". Table should be organized as shown in "Initiative Template" sheet with the column names matching "Field Name Shapefile" column in the "Schema" sheet. Each field is explained in the "Field description" column, and type of data for each field is in the "Field Type". Attached to this dataset should be lat/lon points corresponding to each row in the data | GIS File with same schema as attached (see specfic data request)
PC-43903-Y-12 | 5.3.4 Asset management and inspections | NA | NA | Provide asset spatial data at the individual asset level for each of the asset categories listed (substations, weather stations, capacitor banks, conductors, poles, transmission lines and distribution lines). The exact schema for the spatial data can be found in the attaced excel file, "20200311_Asset_schema", in the sheets "Asset schema for utils - points" and "Asset schema for utils - lines". The priority for each field is listed in the "priority" column. An example of the table is provided in the "Asset Template" sheets. Table should be organized as shown in "Asset Template" sheets with the column names matching "Field Name Shapefile" column in the "Schema" sheet. Each field is explained in the "Field description" column, and type of data for each field is in the "Field Type". Attached should be two spatial files, one for points data and one for lines data, where each dataset should have its respective shape features (lat/lon points or lines) corresponding to each row in the data | GIS Files with same schema as attached (see specfic data request) - one for lines and one for points
PC-43903-Y-21 | 6.1 Recent weather patterns and use of PSPS | NA | NA | Provide PSPS event data at the circuit level (i.e., each circuit shut-off in an event should have its own row in the shapefile dataset). The exact schema for the spatial data can be found in the attaced excel file, "20200303_PSPS_schema", in the sheet "PSPS Schema for utilities". "Risk drivers" should be the same across circuits in an event, but all other values should be unique to each circuit. The priority for each field is listed in the "priority" column. An example of the table is provided in the sheet "PSPS Event Template". Table should be organized as shown in "Example onlyPSPS Event Template" sheet with the column names matching "Field Name Shapefile" column in the "Schema" sheet. Each field is explained in the "Field description" column, and type of data for each field is in the "Field Type", and priority of data being received by CPUC is in the "Priority" column | GIS File with same schema as attached (see attached excel file - 20200202_PSPS_schema). | PacifiCorp has not had a PSPS event; therefore no event data can be provided. However, the schema provided will be retained for future reporting if required.
PC-43903-Y-22 | 6.4: Current baseline state of service territory and utility equipment | NA | From WMP: Summarized risk map: Operation wildfire risk reduction model used to prioritize long-term hardening efforts. Referred to on page 5—43, section 5.3.1.1. From the section: “PG&E has leveraged the FMEA that was used to inform its 2019 accelerated and enhanced inspections to develop.” 1. “ignition probabilities for each of the various electric overhead equipment types for electric distribution, transmission and substation facilities” 2. “Likelihood of failure: Relative risk of a circuit causing an outage and ensuing ignition” 3. “Likelihood of wildfire spread and consequence score: Relative ability ignition spread and quantity of homes or timber affected if ignition occurs” | Provide the most recent map of overhead distribution, transmission, and substation facilities (as was provided earlier) in high-fire threat regions with additional fields for… 1. Ignition probability – projected likelihood of target asset causing an ignition in the next year (0.0 – 1.0) 2. Failure probability – projected likelihood of target asset failing in the next year (0.0 – 1.0) 3. Wildfire spread and consequence score (normalized from 0.0 – 1.0) – relative ability ignition spread and quantity of homes or timber affected if ignition occurs 4. Prioritization ranking of assets for maintenance – calculated ranking of assets for prioritizing asset maintenance, upgrades, and equipment replacement. This is a percentile ranking with 99th percentile being highest priority and 0th percentile being lowest priority for asset maintenance | GIS File | Per this request, PacifiCorp has submitted what attribute information is available in GIS format. The attributes as outlined are not ones PacifiCorp has developed and thus do not exist.