## CPUC 3
Feeder | Outage ID | Source | JobNo | BU | State | OpArea | Substation | Operating Equipment | Year | Before/After Project | Interrupted | Restored | CI | CMI | mCI | mCMI | RestorationStages | ReportableFlag | RareIncidentFlag | SafetyHoldFlag | LockoutFlag | MajorEventFlag | MajorEventName | DirectCauseCat | DirectCause | contributoryCauseCat | contributoryCause | Component | DamagedComponentCode1 | DamagedComponentCode2 | DamagedComponentCode3 | Comments | OutageClass | OutageSubclass | EstOverride | EstRepair | OutageStatus | SwitchOrders | CreatedPST | UpdatedPST | ArchivedPST | Longitude | Latitude
4W8 | 597228 | CPCC | CPCC392272 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_299920_304570087 | 2007 | Before | 2007-01-05 17:21 | 2007-01-05 18:37 | 45 | 3431.25 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: blown line fuse patrol no cause found | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.208 | 45.2782
4W8 | 598589 | CPCC | CPCC392498 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_090700_69740155 | 2007 | Before | 2007-01-06 21:11 | 2007-01-06 22:13 | 1 | 62.033 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: cut out replaced | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 603014 | CPCC | CPCC396826 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_199704_101040273 | 2007 | Before | 2007-01-27 17:56 | 2007-01-27 19:33 | 46 | 4357.167 | 0 | 0 | 2 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | CONNECTOR OH |  |  |  | PROSPER: Line down, fuses open on pole 199704. Isolated trouble on pole 199503, pump bank will remain off until repairs are complete, sometime next week | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.23 | 45.3769
4W8 | 617725 | CPCC | CPCC420241 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_040201_69740119 | 2007 | Before | 2007-06-02 20:13 | 2007-06-02 21:07 | 1 | 53.933 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Found fuse blown, patrolled found nothing, refused, OK | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 621369 | CPCC | CPCC423166 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_120702_1560029373 | 2007 | Before | 2007-06-21 18:42 | 2007-06-21 20:16 | 6 | 563.1 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Line fuses open, cause unknown. Re fused and customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.146 | 45.4073
4W8 | 614598 | CPCC | CPCC417469 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_030004_69740156 | 2007 | Before | 2007-05-11 09:41 | 2007-05-11 10:37 | 25 | 1391.25 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (PROTECTED SPECIES) (BMTS) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused tapline at pole# 030004 and it held, the cause was a hawk, serviceman will fill out the report. Customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.1872 | 45.4116
4W8 | 617203 | CPCC | CPCC416528 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_299700_304570145 | 2007 | Before | 2007-05-03 11:17 | 2007-05-03 12:15 | 1 | 58.783 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: Crew changed out a B/O transformer cutout on pole# 299700, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 617204 | CPCC | CPCC416531 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_280903_304570156 | 2007 | Before | 2007-05-03 11:22 | 2007-05-03 12:15 | 1 | 53.7 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: Associate to outage# 416528. Crew changed out a B/O transformer cutout on pole# 299700, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 625610 | CPCC | CPCC425497 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_123902_789340153 | 2007 | Before | 2007-07-06 11:54 | 2007-07-06 12:40 | 1 | 46.117 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 010000 and it held, the cause was a starling, customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 626502 | CPCC | CPCC426304 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_137201_852830232 | 2007 | Before | 2007-07-10 10:04 | 2007-07-10 11:09 | 1 | 65.067 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | LIGHTNING ARRESTER OH |  |  |  | PROSPER: Serviceman made replaced a B/O lightning arrestor that went bad and also caused damage to the cutout and jumpers, customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 628552 | CPCC | CPCC430306 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_144101_163440224 | 2007 | Before | 2007-07-18 09:51 | 2007-07-18 10:45 | 1 | 54.15 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused transformer# 144101 and it held, the cause is unknown, pump is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 625342 | CPCC | CPCC425360 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_045000_69740158 | 2007 | Before | 2007-07-06 08:43 | 2007-07-06 10:07 | 1 | 84 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | SECTIONALIZER B/O OH |  |  |  | PROSPER: Associate to outage# 425337. B/o connectivity in cadops, mapping change made, The cause was a B/O field recloser. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 625344 | CPCC | CPCC425377 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_027305_750140175 | 2007 | Before | 2007-07-06 08:32 | 2007-07-06 10:09 | 1887 | 182032.6 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | SECTIONALIZER B/O OH |  |  |  | PROSPER: Crew bypassed B/O field recloser # 4W12, customers are all back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2771 | 45.4161
4W8 | 629038 | CPCC | CPCC429596 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_219503_101040198 | 2007 | Before | 2007-07-15 15:10 | 2007-07-15 16:39 | 1 | 89.017 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | INTENTIONAL TO CLEAR TROUBLE |  |  | PLANNED OUTAGE |  |  |  | PROSPER: 1612 Cooney will be disconnecting service, tree trimming crew on way to clear tree, will reconnect when cleared. CADOPS shows pole #219503, FARR = 220540. Customer will call for reconnect, new ticket. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 627893 | CPCC | CPCC432270 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_210900_579890083 | 2007 | Before | 2007-07-28 22:27 | 2007-07-28 23:27 | 1 | 60.217 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: bird blown fuse | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 629582 | CPCC | CPCC428592 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_030004_69740156 | 2007 | Before | 2007-07-13 09:45 | 2007-07-13 11:03 | 31 | 2424.717 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused the tapline fuse at pole# 030004 and it held, the cause is unknown, customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.1872 | 45.4116
4W8 | 625601 | CPCC | CPCC425467 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | EPS_CB4W8 | 2007 | Before | 2007-07-06 09:50 | 2007-07-06 10:09 | 338 | 6433.267 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | B/O EQUIPMENT | SECTIONALIZER B/O OH |  |  |  | PROSPER: Associate to outage# 425337. Crew took outage on breaker so they could bypass B/O field recloser# 4W12. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2827 | 45.4182
4W8 | 607588 | CPCC | CPCC408762 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_169701_1560029376 | 2007 | Before | 2007-02-28 10:35 | 2007-02-28 11:17 | 9 | 381.3 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: svcman replaced 2 blown line fuses and customers are back in full service. cuase is unknown. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.1886 | 45.3928
4W8 | 606932 | CPCC | CPCC411285 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_220500_101040204 | 2007 | Before | 2007-03-23 10:53 | 2007-03-23 11:58 | 22 | 1432.933 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: Serviceman made repairs to a B/O jumper and refused tapline at pole# 220500. Customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.1874 | 45.3744
4W8 | 606933 | CPCC | CPCC411288 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_220500_101040204 | 2007 | Before | 2007-03-23 11:46 | 2007-03-23 11:58 | 14 | 175 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | B/O EQUIPMENT | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: Associate to outage# 411285. Serviceman took outage on tapline fuse at pole# 220500 to make repairs to a burnt off cutout jumper. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.1874 | 45.3744
4W8 | 608714 | CPCC | CPCC409977 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_200701_1560039959 | 2007 | Before | 2007-03-12 04:02 | 2007-03-12 05:00 | 18 | 1034.7 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: blown line fuse restored time 04:59:00 | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2296 | 45.3778
4W8 | 648144 | CPCC | CPCC453329 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_320803_997300263 | 2007 | Before | 2007-11-12 09:32 | 2007-11-13 00:02 | 1 | 870.317 | 0 | 0 | 1 | Y | N | N | N | Y | 686 - 2007-11-12 to 2007-11-12 OR Enterprise | WEATHER | WIND |  |  | SECONDARY CONDUCTOR OH |  |  |  |  | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 648151 | CPCC | CPCC453355 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_055922_221510259 | 2007 | Before | 2007-11-12 09:40 | 2007-11-13 03:38 | 1 | 1077.967 | 0 | 0 | 1 | Y | N | N | N | Y | 686 - 2007-11-12 to 2007-11-12 OR Enterprise | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  |  | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 648165 | CPCC | CPCC453726 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_309005_933390243 | 2007 | Before | 2007-11-12 11:44 | 2007-11-12 22:24 | 1 | 639.967 | 0 | 0 | 1 | Y | N | N | N | Y | 686 - 2007-11-12 to 2007-11-12 OR Enterprise | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: restored 21:09 | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 648168 | CPCC | CPCC453736 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_197701_340370052 | 2007 | Before | 2007-11-12 11:50 | 2007-11-12 20:50 | 1 | 540.5 | 0 | 0 | 1 | Y | N | N | N | Y | 686 - 2007-11-12 to 2007-11-12 OR Enterprise | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | NO DISTRIBUTION DAMAGE |  |  |  |  | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 648178 | CPCC | CPCC454354 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_368002_163440203 | 2007 | Before | 2007-11-12 17:40 | 2007-11-13 06:01 | 1 | 740.7 | 0 | 0 | 1 | Y | N | N | N | Y | 686 - 2007-11-12 to 2007-11-12 OR Enterprise | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  |  | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 648179 | CPCC | CPCC454355 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_180000_340370060 | 2007 | Before | 2007-11-12 17:35 | 2007-11-12 21:24 | 1 | 229.05 | 0 | 0 | 1 | Y | N | N | N | Y | 686 - 2007-11-12 to 2007-11-12 OR Enterprise | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  |  | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 648180 | CPCC | CPCC454357 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_280002_163440165 | 2007 | Before | 2007-11-12 17:43 | 2007-11-13 06:00 | 1 | 736.583 | 0 | 0 | 1 | Y | N | N | N | Y | 686 - 2007-11-12 to 2007-11-12 OR Enterprise | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  |  | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 648182 | CPCC | CPCC454361 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_294201_933390360 | 2007 | Before | 2007-11-12 17:49 | 2007-11-13 09:41 | 1 | 952.3 | 0 | 0 | 1 | Y | N | N | N | Y | 686 - 2007-11-12 to 2007-11-12 OR Enterprise | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: customer back in service | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 648184 | CPCC | CPCC454370 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_289020_163440156 | 2007 | Before | 2007-11-12 18:06 | 2007-11-13 21:10 | 1 | 1624.017 | 0 | 0 | 1 | Y | N | N | N | Y | 686 - 2007-11-12 to 2007-11-12 OR Enterprise | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: customer in service | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 646580 | CPCC | CPCC447870 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_117904_789340113 | 2007 | Before | 2007-10-18 09:27 | 2007-10-18 09:52 | 1 | 25.367 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: bird - refused and held. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 648193 | CPCC | CPCC454398 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_292205_933390359 | 2007 | Before | 2007-11-12 18:54 | 2007-11-13 09:47 | 1 | 892.9 | 0 | 0 | 1 | Y | N | N | N | Y | 686 - 2007-11-12 to 2007-11-12 OR Enterprise | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: customer back in service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 649799 | CPCC | CPCC454807 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_296701_304570086 | 2007 | Before | 2007-11-14 12:51 | 2007-11-14 19:08 | 1 | 377.267 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: power restored | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 649807 | CPCC | CPCC456544 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_296701_304570086 | 2007 | Before | 2007-11-23 12:39 | 2007-11-23 14:53 | 1 | 133.733 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: tree took out service | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 648232 | CPCC | CPCC448435 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_309504_933390282 | 2007 | Before | 2007-10-18 14:05 | 2007-10-18 14:30 | 7 | 173.833 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: limb blew into line and caused line fuse to open. no damage done, svcman replaced the blown fuse and all customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2311 | 45.3594
4W8 | 644595 | CPCC | CPCC453546 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_319805_997300389 | 2007 | Before | 2007-11-12 11:01 | 2007-11-12 21:29 | 18 | 11304.3 | 0 | 0 | 1 | Y | N | N | N | Y | 686 - 2007-11-12 to 2007-11-12 OR Enterprise | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: power on 21:29 - Line fuse closed | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2313 | 45.3506
4W8 | 647888 | CPCC | CPCC453314 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_307400_933390293 | 2007 | Before | 2007-11-12 09:27 | 2007-11-13 04:04 | 1 | 1116.65 | 0 | 0 | 1 | Y | N | N | N | Y | 686 - 2007-11-12 to 2007-11-12 OR Enterprise | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: REMOVED TYPAR FROM LINES | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 644614 | CPCC | CPCC453847 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_118900_750140204 | 2007 | Before | 2007-11-12 12:26 | 2007-11-13 04:25 | 14 | 13429.5 | 0 | 0 | 1 | Y | N | N | N | Y | 686 - 2007-11-12 to 2007-11-12 OR Enterprise | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Mtn Power Crew - Hugh Preston on site. Made reparis to primary wire and customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2748 | 45.4105
4W8 | 647906 | CPCC | CPCC454122 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_309501_933390316 | 2007 | Before | 2007-11-12 15:13 | 2007-11-13 00:05 | 1 | 532.283 | 0 | 0 | 1 | Y | N | N | N | Y | 686 - 2007-11-12 to 2007-11-12 OR Enterprise | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  |  | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 649510 | CPCC | CPCC453096 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_299920_304570087 | 2007 | Before | 2007-11-12 08:41 | 2007-11-14 09:16 | 45 | 131197.5 | 0 | 0 | 1 | Y | N | N | N | Y | 686 - 2007-11-12 to 2007-11-12 OR Enterprise | WEATHER | WIND | TREES | TREE - NON-PREVENTABLE | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | PROSPER: Crew made repairs to the overhead primary that was taken down by a tree. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.208 | 45.2782
4W8 | 649169 | CPCC | CPCC461229 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_299920_304570087 | 2007 | Before | 2007-12-02 23:38 | 2007-12-03 17:35 | 45 | 48459.75 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Primary wire down, line fuses are blown. (crew vehicle broke down on Tollgate 11:30 AM) Hawkeye arrived in Enterprise 14:20. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.208 | 45.2782
4W8 | 647643 | CPCC | CPCC453971 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | Line Cut-26066 | 2007 | Before | 2007-11-12 10:10 | 2007-11-13 08:36 | 9 | 12066.733 | 0 | 0 | 2 | Y | N | N | N | Y | 686 - 2007-11-12 to 2007-11-12 OR Enterprise | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Wire down isolated at pole 302401. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2459 | 45.3586
4W8 | 648471 | CPCC | CPCC454284 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_193780_1170000050 | 2007 | Before | 2007-11-12 16:45 | 2007-11-12 20:56 | 1 | 251.25 | 0 | 0 | 1 | Y | N | N | N | Y | 686 - 2007-11-12 to 2007-11-12 OR Enterprise | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  |  | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 643203 | CPCC | CPCC444261 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_055001_69740107 | 2007 | Before | 2007-09-30 14:38 | 2007-09-30 15:46 | 156 | 10704.2 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Field recloser locked open. Serviceman patrolled and found a tree limb that might have been going phase to phase. Close Field recloser and picked up all customers. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2181 | 45.4112
4W8 | 638412 | CPCC | CPCC438656 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | JOS_CB5W21 | 2007 | Before | 2007-08-31 16:44 | 2007-08-31 18:16 | 839 | 76712.567 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: 230 KV line wraped together. sub and feeder changed to JOSEPH and 5W21. P44577. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2316 | 45.3486
4W8 | 642944 | CPCC | CPCC444230 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_030004_69740156 | 2007 | Before | 2007-09-30 13:34 | 2007-09-30 14:34 | 19 | 1141.9 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Line fuse is open. Serviceman is patrolling line. No cause found. Refused and customers are back on. Serviceman reports its real windy. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.1872 | 45.4116
4W8 | 638931 | CPCC | CPCC441168 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_289901_163440168 | 2007 | Before | 2007-09-05 14:53 | 2007-09-05 15:57 | 3 | 189.3 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: svcman replaced a blown cutout fuse at a 3 phase tap line and customers are back in full service. cause is unknown. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.1877 | 45.3668
4W8 | 639445 | CPCC | CPCC440834 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_220500_101040204 | 2007 | Before | 2007-09-04 08:45 | 2007-09-04 09:56 | 23 | 1640.283 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - TRIMMABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Line fuse is open. Found tree limb that had been on line, cleared | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.1874 | 45.3744
4W8 | 652228 | CPCC | CPCC461191 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_309504_933390282 | 2007 | Before | 2007-12-02 23:21 | 2007-12-03 00:35 | 12 | 896.2 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Line fuses blown, had phase slapping. Refused and customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2311 | 45.3594
4W8 | 650986 | CPCC | CPCC454174 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_290605_933390406 | 2007 | Before | 2007-11-12 15:31 | 2007-11-12 17:50 | 1 | 139.033 | 0 | 0 | 1 | Y | N | N | N | Y | 686 - 2007-11-12 to 2007-11-12 OR Enterprise | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: on at 17:50 | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 651836 | CPCC | CPCC453364 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | SB_212600_1560039015 | 2007 | Before | 2007-11-12 09:14 | 2007-11-14 19:15 | 294 | 628898.284 | 0 | 0 | 10 | Y | N | N | N | Y | 686 - 2007-11-12 to 2007-11-12 OR Enterprise | WEATHER | WIND |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2019 | 45.2871
4W8 | 652243 | CPCC | CPCC461563 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_280900_163440171 | 2007 | Before | 2007-12-03 07:47 | 2007-12-03 09:57 | 1 | 130.267 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Customer back in service | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 652247 | CPCC | CPCC461575 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_220000_101040194 | 2007 | Before | 2007-12-03 07:58 | 2007-12-03 10:03 | 1 | 125.083 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Customer is back in service | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 652250 | CPCC | CPCC461584 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_285900_163440170 | 2007 | Before | 2007-12-03 08:06 | 2007-12-03 10:01 | 1 | 115.167 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Customer back in service | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 652251 | CPCC | CPCC461587 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_240404_163440214 | 2007 | Before | 2007-12-03 08:09 | 2007-12-03 10:00 | 1 | 111.05 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Customer back in service | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 653085 | CPCC | CPCC461860 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_309504_933390282 | 2007 | Before | 2007-12-03 10:00 | 2007-12-03 12:23 | 11 | 1570.8 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: Crew made repairs to the overhead primary that was taken down by a tree, customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2311 | 45.3594
4W8 | 653086 | CPCC | CPCC461873 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_290605_933390406 | 2007 | Before | 2007-12-03 10:04 | 2007-12-03 12:24 | 1 | 139.45 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Wire needs to be re-sagged | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 651023 | CPCC | CPCC454709 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_298721_304570141 | 2007 | Before | 2007-11-13 20:34 | 2007-11-13 20:37 | 0 | 0 | 31 | 84.733 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2106 | 45.274
4W8 | 651420 | CPCC | CPCC461400 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_309504_933390282 | 2007 | Before | 2007-12-03 05:58 | 2007-12-03 07:10 | 12 | 869.8 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2311 | 45.3594
4W8 | 653115 | CPCC | CPCC463181 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_304503_933390209 | 2007 | Before | 2007-12-04 11:55 | 2007-12-04 13:05 | 1 | 70.267 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Serviceman replaced a B/O secondary connection at the transformer, custoemr is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 655234 | CPCC | CPCC467337 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_220000_101040194 | 2007 | Before | 2007-12-20 17:49 | 2007-12-20 19:02 | 1 | 72.967 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | OTHER, KNOWN CAUSE |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: Serviceman found loose connections in the 3 phase, he called out Seth McKern to assist. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 653183 | CPCC | CPCC456157 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_137101_852830185 | 2007 | Before | 2007-11-20 16:00 | 2007-11-20 16:24 | 2 | 47.4 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: Overlap transf issue with 456128. Changed OFF time, 1531 to 1600. P44577 | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2559 | 45.3847
4W8 | 651109 | CPCC | CPCC460253 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_247900_852830189 | 2007 | Before | 2007-12-02 15:49 | 2007-12-02 22:46 | 16 | 6674.933 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Crew made repairs to the overhead primary that was taken down by a tree, customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2563 | 45.3817
4W8 | 652391 | CPCC | CPCC455463 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_299920_304570087 | 2007 | Before | 2007-11-17 15:27 | 2007-11-17 16:10 | 45 | 1904.25 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Crew on site making repairs leftover from the storm. Wire was sagging real bad from strom into neutral. Work complete. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.208 | 45.2782
4W8 | 652400 | CPCC | CPCC454557 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_237700_852830223 | 2007 | Before | 2007-11-13 08:02 | 2007-11-13 16:59 | 1 | 537.317 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: wire back up customer in service | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 652844 | CPCC | CPCC463160 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_290113_933390203 | 2007 | Before | 2007-12-04 10:07 | 2007-12-04 12:59 | 24 | 4131.2 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | POLE OH |  |  |  | PROSPER: pole about to fall over opened field recloser 4w11 to set pole | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2287 | 45.3543
4W8 | 654535 | CPCC | CPCC471782 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | EPS_CB4W8 | 2008 | Before | 2008-01-04 09:30 | 2008-01-04 10:30 | 1410 | 84882 | 0 | 0 | 1 | Y | N | N | N | Y | 709 - 2008-01-04 to 2008-01-04 OR Enterprise | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Loss of transmission line due to high winds in the area. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2827 | 45.4182
4W8 | 652488 | CPCC | CPCC459508 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_042000_221510143 | 2007 | Before | 2007-12-02 14:43 | 2007-12-02 17:01 | 339 | 46838.5 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman removed tree limbs from the overhead primary, customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2031 | 45.3237
4W8 | 656740 | CPCC | CPCC469589 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_169701_1560029376 | 2008 | Before | 2008-01-03 10:15 | 2008-01-03 10:57 | 9 | 383.25 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused the tapline fuse at pole# 169701 and ti held, the cause was high wind in the area, customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.1886 | 45.3928
4W8 | 652528 | CPCC | CPCC461616 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_193201_196250029 | 2007 | Before | 2007-12-03 08:28 | 2007-12-03 11:19 | 1 | 171.167 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Spruce tree took neutral down to the house. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 652529 | CPCC | CPCC461619 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_225500_101040207 | 2007 | Before | 2007-12-03 08:29 | 2007-12-03 10:00 | 1 | 90.983 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Customer back in service | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 652532 | CPCC | CPCC461628 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_227802_101040209 | 2007 | Before | 2007-12-03 08:35 | 2007-12-03 09:58 | 1 | 83.167 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Customer back in service | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 652533 | CPCC | CPCC461635 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_297900_933390413 | 2007 | Before | 2007-12-03 07:43 | 2007-12-03 10:08 | 9 | 1299.45 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Customer back in service. Closed in fuse on Rancho Road. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2126 | 45.3668
4W8 | 653367 | CPCC | CPCC469778 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_174903_594930035 | 2008 | Before | 2008-01-03 23:10 | 2008-01-04 01:29 | 1 | 138.767 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 655905 | CPCC | CPCC469807 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_174903_594930035 | 2008 | Before | 2008-01-04 01:29 | 2008-01-04 01:29 | 0 | 0 | 1 | 0.467 | 1 | Y | N | N | N | Y | 709 - 2008-01-04 to 2008-01-04 OR Enterprise | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 651307 | CPCC | CPCC454883 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_299920_304570087 | 2007 | Before | 2007-11-15 01:13 | 2007-11-15 03:24 | 44 | 5759.6 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: re-fused ok. no cause found | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.208 | 45.2782
4W8 | 655926 | CPCC | CPCC472327 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_309121_933390202 | 2008 | Before | 2008-01-04 10:41 | 2008-01-04 11:25 | 1 | 44.167 | 0 | 0 | 1 | Y | N | N | N | Y | 709 - 2008-01-04 to 2008-01-04 OR Enterprise | WEATHER | WIND |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: Serviceman made repairs to the B/O hot line clamp that came loose in the wind, customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 651335 | CPCC | CPCC456128 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_027305_750140175 | 2007 | Before | 2007-11-20 15:31 | 2007-11-20 16:00 | 1064 | 30536.8 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | RECLOSER-NORMAL OPERATION OH (NO CAUSE FOUND) |  |  |  | PROSPER: EMR on site investigating Closed recloser 4W12 on test and held | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2771 | 45.4161
4W8 | 636724 | CPCC | CPCC439131 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_055001_69740107 | 2007 | Before | 2007-08-31 19:02 | 2007-09-01 03:35 | 154 | 78986.6 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: field recloser tripped open | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2181 | 45.4112
4W8 | 632670 | CPCC | CPCC434192 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_232501_163440225 | 2007 | Before | 2007-08-09 07:30 | 2007-08-09 08:01 | 1 | 31.5 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused transformer bank on pole# 232501 and it held, the cause is unknown, pump is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 636456 | CPCC | CPCC439052 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_207100_267850161 | 2007 | Before | 2007-08-31 18:52 | 2007-09-01 08:11 | 1 | 798.933 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: called customer & power was back on | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 636459 | CPCC | CPCC439060 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_028500_673650162 | 2007 | Before | 2007-08-31 18:58 | 2007-09-01 04:54 | 303 | 180689 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: Making repairs to loose jumper at Field recloser 4W40 | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2751 | 45.4191
4W8 | 635663 | CPCC | CPCC433625 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_144101_163440224 | 2007 | Before | 2007-08-07 09:09 | 2007-08-07 09:54 | 1 | 45.033 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer bank on pole# 144101 and it held, the cause was a starling, pump is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 632454 | CPCC | CPCC435315 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_294004_579890064 | 2007 | Before | 2007-08-15 06:36 | 2007-08-15 07:15 | 1 | 38.917 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | LIGHTNING ARRESTER OH |  |  |  | PROSPER: Serviceman cut lightning arrestor in the clear and refused transformer ok. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 636213 | CPCC | CPCC438647 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | EPS_CB4W8 | 2007 | Before | 2007-08-31 16:43 | 2007-08-31 18:16 | 1397 | 129245.783 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: 230 KV line wraped together | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2827 | 45.4182
4W8 | 672996 | CPCC | CPCC496074 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_027305_750140175 | 2008 | Before | 2008-04-14 21:59 | 2008-04-14 23:18 | 1059 | 83943.4 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | RECLOSER-NORMAL OPERATION OH (NO CAUSE FOUND) |  |  |  | PROSPER: Serviceman, Becker found recloser 4W12 locked out, no targets. disabled recloser and giving a test, No Good, had to bypass. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2771 | 45.4161
4W8 | 672998 | CPCC | CPCC496121 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | EPS_CB4W8 | 2008 | Before | 2008-04-14 23:09 | 2008-04-14 23:12 | 0 | 0 | 336 | 1008 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | PLANNED OUTAGE |  |  |  | PROSPER: Opened at 23:09:00, closed at 23:12:00, drop and pick, facilitate to pick up Joseph Sub with bypass to field recloser 4W12. (times from auto email) | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2827 | 45.4182
4W8 | 675393 | CPCC | CPCC498135 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_011601_633620135 | 2008 | Before | 2008-04-27 15:49 | 2008-04-27 16:33 | 9 | 399.75 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2696 | 45.4198
4W8 | 673557 | CPCC | CPCC496143 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_042000_221510143 | 2008 | Before | 2008-04-15 01:39 | 2008-04-15 02:33 | 338 | 18133.7 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman found recloser 4W43 open on Pole # 042000. 338 customers out. Believe this was from earlier outage at 2159 Monday. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2031 | 45.3237
4W8 | 672843 | CPCC | CPCC496448 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_198100_101040290 | 2008 | Before | 2008-04-15 20:27 | 2008-04-15 21:22 | 1 | 55.167 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: blown line fuses no cause found replaced fuses and it held | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 672844 | CPCC | CPCC496449 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_205004_101040240 | 2008 | Before | 2008-04-15 20:30 | 2008-04-15 21:19 | 10 | 489.833 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: blown line fuse no cause found replaced fuses and it held | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2201 | 45.3669
4W8 | 672845 | CPCC | CPCC496451 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_199000_101040275 | 2008 | Before | 2008-04-15 20:33 | 2008-04-15 21:20 | 17 | 791.35 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: blown line fuse no cause found replaced fuses and it held | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2302 | 45.367
4W8 | 672846 | CPCC | CPCC496452 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_200101_101040169 | 2008 | Before | 2008-04-15 20:41 | 2008-04-15 21:22 | 1 | 41.317 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: blown line fuses no cause found replaced fuses and it held | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 672847 | CPCC | CPCC496456 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_199704_101040273 | 2008 | Before | 2008-04-15 21:04 | 2008-04-15 21:21 | 12 | 202.8 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: blown line fuse no cause found | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.23 | 45.3769
4W8 | 664374 | CPCC | CPCC488635 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_118300_789340096 | 2008 | Before | 2008-02-11 08:52 | 2008-02-11 09:35 | 1 | 42.617 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: crew to replace bad trf cutout. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 670139 | CPCC | CPCC492855 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_027305_750140175 | 2008 | Before | 2008-03-13 20:34 | 2008-03-13 22:33 | 1059 | 71325 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | INSULATOR OH |  |  |  | PROSPER: replaces 492353 | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2771 | 45.4161
4W8 | 665324 | CPCC | CPCC488069 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | SUB_SW_750140012 | 2008 | Before | 2008-02-07 05:24 | 2008-02-07 05:39 | 1393 | 20546.75 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: loss of 230 start time 0524 of outage | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2827 | 45.4182
4W8 | 679407 | CPCC | CPCC505545 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_030004_69740156 | 2008 | Before | 2008-06-10 04:53 | 2008-06-10 05:55 | 25 | 1555.417 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Line fuse blown, patrolled line and did not find a cause. Refused and customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.1872 | 45.4116
4W8 | 681535 | CPCC | CPCC507842 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_111202_69740204 | 2008 | Before | 2008-06-26 10:26 | 2008-06-26 13:28 | 1 | 182.4 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: transformer fuse | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 682015 | CPCC | CPCC506417 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_283904_163440173 | 2008 | Before | 2008-06-18 08:09 | 2008-06-18 08:53 | 2 | 88.7 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: serviceman refused transformer 283904 in and holding no cause found | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 680426 | CPCC | CPCC507718 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_107801_69740174 | 2008 | Before | 2008-06-25 08:14 | 2008-06-25 09:16 | 1 | 62.067 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: bad order sec. connector | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 678424 | CPCC | CPCC503166 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_309009_933390244 | 2008 | Before | 2008-05-22 23:02 | 2008-05-23 00:20 | 1 | 77.75 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 678481 | CPCC | CPCC504343 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_119080_594930028 | 2008 | Before | 2008-05-30 09:23 | 2008-05-30 12:09 | 1 | 166.117 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE ONLY -UG ( NO CAUSE FOUND) |  |  |  | PROSPER: Serviceman is out of Radio and Phone service. Fuse in pad mount transformer was out. Replaced and customer back in service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 680120 | CPCC | CPCC507373 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_055001_69740107 | 2008 | Before | 2008-06-22 05:02 | 2008-06-22 06:32 | 154 | 13729.1 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | RECLOSER-NORMAL OPERATION OH (NO CAUSE FOUND) |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2181 | 45.4112
4W8 | 680604 | CPCC | CPCC506116 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_200101_101040169 | 2008 | Before | 2008-06-14 14:09 | 2008-06-14 14:41 | 1 | 32.35 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: Bad order cutout. Replaced cutout and customer is back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 660197 | CPCC | CPCC482614 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_027305_750140175 | 2008 | Before | 2008-01-26 20:30 | 2008-01-26 21:36 | 1057 | 68881.167 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: high wind recloser tripped open | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2771 | 45.4161
4W8 | 662309 | CPCC | CPCC488871 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_127003_789340132 | 2008 | Before | 2008-02-13 14:49 | 2008-02-13 15:45 | 22 | 1237.867 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: serviceman patrolled line found nothing, closed in fuses and they held | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2547 | 45.3965
4W8 | 660658 | CPCC | CPCC479027 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_220500_101040204 | 2008 | Before | 2008-01-14 16:41 | 2008-01-14 17:47 | 37 | 2409.317 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Wind, blown line fuses, refused, held good | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.1874 | 45.3744
4W8 | 659011 | CPCC | CPCC479036 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_207001_101040231 | 2008 | Before | 2008-01-14 17:17 | 2008-01-14 17:29 | 8 | 101.6 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Wind, blown fuses, refused, OK. Overlaping Transformer issue, changed On time from 1822 to 1729. P44577 | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2127 | 45.3678
4W8 | 658249 | CPCC | CPCC483540 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_247900_852830189 | 2008 | Before | 2008-01-27 15:48 | 2008-01-27 16:23 | 2 | 70.1 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Line fuse blew. No cause found. Refused and customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2563 | 45.3817
4W8 | 657053 | CPCC | CPCC472714 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_238700_163440210 | 2008 | Before | 2008-01-04 12:28 | 2008-01-04 14:27 | 1 | 118.933 | 0 | 0 | 1 | Y | N | N | N | Y | 709 - 2008-01-04 to 2008-01-04 OR Enterprise | WEATHER | WIND |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: Broken Jumper | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 662097 | CPCC | CPCC481667 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_053102_69740120 | 2008 | Before | 2008-01-22 11:26 | 2008-01-22 12:02 | 1 | 36.017 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: Crew changed out a B/O cutout on transformer# 053102, customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 657924 | CPCC | CPCC481689 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_330600_579890067 | 2008 | Before | 2008-01-22 14:26 | 2008-01-22 15:24 | 27 | 1579.05 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | LIGHTNING ARRESTER OH |  |  |  | PROSPER: Serviceman refused the tapline fuses at pole# 330600 and they held, the cause was some B/O lightning arrestors to a pump bank that is not in use at this time. Customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2092 | 45.4353
4W8 | 660452 | CPCC | CPCC480689 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_298904_304570105 | 2008 | Before | 2008-01-18 18:36 | 2008-01-18 20:28 | 1 | 111.667 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | CONNECTOR OH |  |  |  | PROSPER: Broken neutral loose in the meter base due to tree. Made new connection and customer is back on. Serviceman said it looked like it was left over from the last storm. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 660922 | CPCC | CPCC479035 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_289901_163440168 | 2008 | Before | 2008-01-14 17:29 | 2008-01-14 19:54 | 20 | 2894 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: replaced fuse | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.1877 | 45.3668
4W8 | 696417 | CPCC | CPCC523394 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_172801_101040323 | 2008 | Before | 2008-09-20 06:55 | 2008-09-20 08:41 | 1 | 105.833 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: replaced transformer fuse | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 696978 | CPCC | CPCC523551 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_028500_673650162 | 2008 | Before | 2008-09-21 01:07 | 2008-09-21 05:17 | 305 | 34118.317 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | POLE OH |  |  |  | PROSPER: Pole fire burnt top of pole off. Reframed pole and customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2749 | 45.4191
4W8 | 695864 | CPCC | CPCC523297 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_028402_750140219 | 2008 | Before | 2008-09-19 08:12 | 2008-09-19 08:34 | 1 | 21.733 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Starling caused fuse to blow. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 693081 | CPCC | CPCC516070 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_330600_579890067 | 2008 | Before | 2008-08-07 16:38 | 2008-08-07 17:22 | 21 | 328.1 | 0 | 0 | 2 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused the tapline fuse at pole# 330600 and they held the cause was lightning. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2092 | 45.4353
4W8 | 693089 | CPCC | CPCC516087 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_191601_1560039145 | 2008 | Before | 2008-08-07 16:32 | 2008-08-07 17:21 | 1 | 49.517 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Associate to outage# 516070, serviceman refused the tapline fuse at pole# 330600 and they held the cause was lightning. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 690772 | CPCC | CPCC518559 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | Line Cut-30637 | 2008 | Before | 2008-08-20 19:32 | 2008-08-20 20:35 | 1405 | 88515 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Outage start time was 19:32 | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2826 | 45.4182
4W8 | 692804 | CPCC | CPCC516048 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_330000_353200014 | 2008 | Before | 2008-08-07 15:42 | 2008-08-07 16:52 | 8 | 561.6 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Refer to outage# 516070, serviceman refused the tapline fuse at pole# 330600 and they held the cause was lightning. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2087 | 45.5149
4W8 | 695695 | CPCC | CPCC510608 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_120702_1560029373 | 2008 | Before | 2008-07-05 09:32 | 2008-07-05 10:12 | 7 | 283.267 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: blown line fuse | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.146 | 45.4074
4W8 | 696107 | CPCC | CPCC522783 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_016401_633620100 | 2008 | Before | 2008-09-16 08:03 | 2008-09-16 09:11 | 1 | 68.05 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 016401 and it held, the cause was a starling, customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 689969 | CPCC | CPCC520644 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_070003_69740114 | 2008 | Before | 2008-09-01 19:05 | 2008-09-01 20:16 | 3 | 211.35 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2505 | 45.3965
4W8 | 693294 | CPCC | CPCC521518 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_261704_163440182 | 2008 | Before | 2008-09-05 10:16 | 2008-09-05 10:55 | 1 | 39.483 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused and it held, the cause is unknown, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 708898 | CPCC | CPCC549730 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_191601_1560039145 | 2009 | Before | 2009-01-20 17:06 | 2009-01-20 19:35 | 1 | 148.267 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 706879 | CPCC | CPCC553804 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_117200_1170000174 | 2009 | Before | 2009-02-21 01:00 | 2009-02-21 03:10 | 2 | 260.167 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTORS UG |  |  |  | PROSPER: Broken underground dip. Crew is: Cooney, Becker. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2763 | 45.3998
4W8 | 704918 | CPCC | CPCC550868 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_118501_789340121 | 2009 | Before | 2009-01-30 10:15 | 2009-01-30 11:04 | 1 | 48.5 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: Crew needed to replace a B/O cutout on pole# 118501. Customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 705316 | CPCC | CPCC555326 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_048200_69740166 | 2009 | Before | 2009-03-02 06:49 | 2009-03-02 07:45 | 1 | 56.45 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: CAT BLOWN TRANSFORMER FUSE | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 705768 | CPCC | CPCC549922 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_220500_101040204 | 2009 | Before | 2009-01-21 15:10 | 2009-01-21 15:45 | 31 | 1081.383 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman patrolled line out and found no cause. He closes in on test and it held. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.1873 | 45.3744
4W8 | 685608 | CPCC | CPCC511908 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_053102_69740120 | 2008 | Before | 2008-07-11 14:18 | 2008-07-11 15:22 | 1 | 64.017 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: Serviceman changed out the B/O secondary connections at the weatherhead and the pole, customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 683241 | CPCC | CPCC509815 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_055001_69740107 | 2008 | Before | 2008-06-30 19:40 | 2008-06-30 20:09 | 154 | 4602.033 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2181 | 45.4112
4W8 | 688194 | CPCC | CPCC507369 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_030004_69740156 | 2008 | Before | 2008-06-22 04:51 | 2008-06-22 05:02 | 36 | 411.6 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: blown line fuse. Overlap transf issue, changed On time from 0550 to 0502. P44577 | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.1872 | 45.4116
4W8 | 686733 | CPCC | CPCC512125 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_240404_163440214 | 2008 | Before | 2008-07-13 08:11 | 2008-07-13 10:29 | 1 | 138.817 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 725410 | CPCC | CPCC575302 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_264700_1560098495 | 2009 | Before | 2009-07-13 07:11 | 2009-07-13 08:10 | 6 | 355.5 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: patrolling. refused line fuse, power on | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.1567 | 45.3633
4W8 | 726971 | CPCC | CPCC578464 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_144101_163440224 | 2009 | Before | 2009-07-29 13:52 | 2009-07-29 15:31 | 1 | 99.583 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | PROSPER: serviceman found some bad connections on service, will repair and call back. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 726618 | CPCC | CPCC574378 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_117500_69740184 | 2009 | Before | 2009-07-06 08:24 | 2009-07-06 09:04 | 1 | 39.583 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (PROTECTED SPECIES) (BMTS) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Owl blew xfmr fuse. Serviceman replaced fuse and customer is back in service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 726709 | CPCC | CPCC578439 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_040001_69740157 | 2009 | Before | 2009-07-29 10:02 | 2009-07-29 10:57 | 3 | 164.95 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (PROTECTED SPECIES) (BMTS) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused the tapline fuses at pole# 040001 and they held, the cause a hawk, pumps are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2097 | 45.4118
4W8 | 726768 | CPCC | CPCC563804 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_298800_304570098 | 2009 | Before | 2009-05-04 12:42 | 2009-05-04 13:21 | 1 | 39.683 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: Serviceman replaced the B/O secondary connector at the transformer, customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 723570 | CPCC | CPCC564319 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_299603_304570152 | 2009 | Before | 2009-05-07 08:52 | 2009-05-07 10:19 | 1 | 87.183 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: Per serviceman B/O connector at weather head. Serviceman replaced connector. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 716371 | CPCC | CPCC536754 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_319723_997300391 | 2008 | Before | 2008-12-17 15:00 | 2008-12-17 15:55 | 5 | 276.167 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused transformer# 319723 and it held, the cause is unknown, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 720020 | CPCC | CPCC569498 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_335100_579890072 | 2009 | Before | 2009-06-04 18:17 | 2009-06-04 19:12 | 1 | 55.3 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused the tapline fuse at pole# 330502 and it held, the cause was tree limbs. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 720022 | CPCC | CPCC569500 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_330502_579890068 | 2009 | Before | 2009-06-04 18:23 | 2009-06-04 19:12 | 13 | 635.05 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Associate to outage# 564498. Serviceman refused the tapline fuse at pole# 330502 and it held, the cause was tree limbs. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2076 | 45.4338
4W8 | 720825 | CPCC | CPCC569894 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_219503_101040198 | 2009 | Before | 2009-06-04 22:23 | 2009-06-04 23:42 | 4 | 317.067 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Transformer fuse blew due to tree limbs. Refused and customers are back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 715575 | CPCC | CPCC536256 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_209000_101040221 | 2008 | Before | 2008-12-17 06:08 | 2008-12-17 06:56 | 1 | 48.367 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Blown transformer fuse. Cause was due to cold. Refused and customer is back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 717654 | CPCC | CPCC532583 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_118880_789340122 | 2008 | Before | 2008-11-21 16:57 | 2008-11-21 23:56 | 1 | 419.2 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: repaired pri UG cable | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 720490 | CPCC | CPCC566887 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_203900_101040722 | 2009 | Before | 2009-05-29 13:14 | 2009-05-29 13:39 | 1 | 25.15 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 203900 and it held, the cause was a willow limb, pump is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 719070 | CPCC | CPCC533847 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_135401_852830227 | 2008 | Before | 2008-12-04 15:18 | 2008-12-04 15:56 | 1 | 37.667 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: Serviceman replaced a B/O secondary connection at the transformer, customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 729675 | CPCC | CPCC574814 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_232501_163440225 | 2009 | Before | 2009-07-09 14:13 | 2009-07-09 14:51 | 1 | 38.15 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused transformer# 232501 and it held, the cause is unknown, pump is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 734515 | CPCC | CPCC572564 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_087200_69740433 | 2009 | Before | 2009-06-25 08:01 | 2009-06-25 08:45 | 1 | 43.967 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused transformer# 087200 and it held, the cause is unknown, pump is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 734595 | CPCC | CPCC570037 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_220500_101040204 | 2009 | Before | 2009-06-05 14:49 | 2009-06-05 15:37 | 36 | 1739.4 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Lightning blew two line fuses. Serviceman replaced. All customers back in service. See outage 570028 for crew times. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.1873 | 45.3744
4W8 | 734601 | CPCC | CPCC570048 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_144101_163440224 | 2009 | Before | 2009-06-05 17:54 | 2009-06-05 21:07 | 1 | 193.4 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | PROSPER: Crew completed replacing B/O O/H transformer. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 733838 | CPCC | CPCC575871 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_246100_852830211 | 2009 | Before | 2009-07-15 07:29 | 2009-07-15 09:50 | 1 | 140.35 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | PROSPER: Crew needed to change out a B/O transformer on pole# 246100. Customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 733841 | CPCC | CPCC575875 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_120702_1560029373 | 2009 | Before | 2009-07-15 07:55 | 2009-07-15 09:19 | 3 | 251.5 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | LIGHTNING ARRESTER OH |  |  |  | PROSPER: Serviceman cut a B/O lightning arrestor in the clear at pole# 121803 and refused the tapline fuse at pole# 120702 and it held, customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.146 | 45.4074
4W8 | 733942 | CPCC | CPCC577108 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_120702_1560029373 | 2009 | Before | 2009-07-23 10:15 | 2009-07-23 11:36 | 3 | 244.85 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Original outage (577093) was modeled incorrectly. This is the remodeling of the outage as it was. Line fuse blown on pole# 120702, (no cause found). Serviceman re-fused and fuse held. Customers back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.146 | 45.4074
4W8 | 710311 | CPCC | CPCC552800 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_019480_633620096 | 2009 | Before | 2009-02-11 21:33 | 2009-02-12 02:30 | 1 | 296.867 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: repaired bad ug pri cable | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 713225 | CPCC | CPCC546728 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_299880_304570096 | 2009 | Before | 2009-01-03 09:25 | 2009-01-03 11:04 | 1 | 99.367 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | PROSPER: connection at transformer | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 712469 | CPCC | CPCC559844 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_247900_852830189 | 2009 | Before | 2009-04-07 18:47 | 2009-04-07 19:23 | 16 | 572.8 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Unknown cause. Refused and holding. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2563 | 45.3817
4W8 | 712473 | CPCC | CPCC559859 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_242800_852830219 | 2009 | Before | 2009-04-07 20:16 | 2009-04-07 21:32 | 1 | 76.45 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | LIGHTNING ARRESTER OH |  |  |  | PROSPER: Blown lightning arrestor. Refused | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 712884 | CPCC | CPCC557173 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_309005_933390243 | 2009 | Before | 2009-03-16 08:29 | 2009-03-16 09:23 | 1 | 53.3 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: Serviceman repalced b/o connector at the xfmr. Customer back in service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 713688 | CPCC | CPCC557257 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_191901_101040303 | 2009 | Before | 2009-03-16 14:27 | 2009-03-16 17:25 | 1 | 177.983 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 709299 | CPCC | CPCC558071 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_053102_69740120 | 2009 | Before | 2009-03-23 16:23 | 2009-03-23 17:27 | 1 | 63.667 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: replaced connector | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 709315 | CPCC | CPCC558358 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_204004_101040238 | 2009 | Before | 2009-03-28 06:57 | 2009-03-28 07:38 | 1 | 41.333 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 710125 | CPCC | CPCC559105 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_011601_633620135 | 2009 | Before | 2009-03-31 20:49 | 2009-03-31 21:04 | 32 | 476.8 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2696 | 45.4198
4W8 | 752360 | CPCC | CPCC598735 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_027305_750140175 | 2009 | Before | 2009-11-17 04:36 | 2009-11-18 00:50 | 1072 | 1091019.883 | 0 | 0 | 6 | Y | N | N | N | Y | 856 - 2009-11-17 to 2009-11-17 OR Enterprise | WEATHER | WIND |  |  | POLE OH |  |  |  | PROSPER: Broken primary pole due to wind. Wire down. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2771 | 45.4161
4W8 | 749208 | CPCC | CPCC598977 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_027305_750140175 | 2009 | Before | 2009-11-17 20:33 | 2009-11-18 00:50 | 152 | 39026 | 0 | 0 | 1 | Y | N | N | N | Y | 856 - 2009-11-17 to 2009-11-17 OR Enterprise | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | POLE OH |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2771 | 45.4161
4W8 | 750447 | CPCC | CPCC595088 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_299922_304570090 | 2009 | Before | 2009-10-26 17:18 | 2009-10-26 19:48 | 6 | 895.7 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: Broken cutout. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2088 | 45.2769
4W8 | 752439 | CPCC | CPCC596578 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_322504_997300326 | 2009 | Before | 2009-11-06 07:12 | 2009-11-06 07:54 | 4 | 167.667 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: B/O cut-out on pole# 322504. Serviceman replaced cut-out. All customers back in service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 750610 | CPCC | CPCC596921 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_118501_789340121 | 2009 | Before | 2009-11-08 21:19 | 2009-11-08 22:38 | 1 | 79.65 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: replaced transformer fuse | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 749462 | CPCC | CPCC598986 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | SW_309108_933391130 | 2009 | Before | 2009-11-18 00:28 | 2009-11-18 00:50 | 162 | 3577.5 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.231 | 45.3543
4W8 | 749463 | CPCC | CPCC598987 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | SB_270001_1170000191 | 2009 | Before | 2009-11-18 00:34 | 2009-11-18 00:51 | 23 | 387.933 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.1872 | 45.3519
4W8 | 751478 | CPCC | CPCC598981 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | SW_321721_997301124 | 2009 | Before | 2009-11-17 21:24 | 2009-11-18 01:02 | 376 | 82043.2 | 0 | 0 | 1 | Y | N | N | N | Y | 856 - 2009-11-17 to 2009-11-17 OR Enterprise | WEATHER | WIND |  |  | POLE OH |  |  |  | PROSPER: Overlap trafnsf issue, cahanged Off time from 2024 to 2124. P44577 | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2261 | 45.3486
4W8 | 752640 | CPCC | CPCC598802 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_055001_69740107 | 2009 | Before | 2009-11-17 06:43 | 2009-11-17 11:01 | 159 | 40982.25 | 0 | 0 | 1 | Y | N | N | N | Y | 856 - 2009-11-17 to 2009-11-17 OR Enterprise | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Crew made repairs to the overhead primary that was damaged by a tree, customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2181 | 45.4112
4W8 | 752280 | CPCC | CPCC594889 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_264700_1560098495 | 2009 | Before | 2009-10-25 11:26 | 2009-10-25 11:27 | 0 | 0 | 6 | 5.4 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.1567 | 45.3633
4W8 | 749925 | CPCC | CPCC594989 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_296300_579890065 | 2009 | Before | 2009-10-26 11:37 | 2009-10-26 12:24 | 1 | 46.467 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused transformer# 296300 and it held, the cause is unknown, customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 749930 | CPCC | CPCC595008 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_210104_1560038602 | 2009 | Before | 2009-10-26 12:37 | 2009-10-26 16:25 | 328 | 38956.167 | 0 | 0 | 3 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Serviceman found all 3 tapline fuses open at pole# 210104 and a tree thru the overhead primary. Crew needed to make repairs | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2064 | 45.28
4W8 | 746803 | CPCC | CPCC585332 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_048200_69740166 | 2009 | Before | 2009-09-02 06:08 | 2009-09-02 06:57 | 3 | 145.75 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Cat caused xfmr fuse to blow. Serviceman replaced fuse and all customers are back in service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 742502 | CPCC | CPCC582268 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_335100_579890072 | 2009 | Before | 2009-08-13 10:11 | 2009-08-13 11:10 | 1 | 59.117 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: Serviceman made repairs to the B/O jumper on pole# 335100 and refused the tapline fuse at pole# 330502 and it held, B/O connectivity in cadops, mapping change made. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 742503 | CPCC | CPCC582270 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_330502_579890068 | 2009 | Before | 2009-08-13 10:26 | 2009-08-13 11:11 | 11 | 490.417 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: Associate to outage# 582268. Serviceman made repairs to the B/O jumper on pole# 335100 and refused the tapline fuse at pole# 330502 and it held. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2076 | 45.4338
4W8 | 743463 | CPCC | CPCC590802 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_298901_304570107 | 2009 | Before | 2009-10-04 09:09 | 2009-10-04 10:06 | 4 | 228.2 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | SNOW, SLEET AND BLIZZARD | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 746703 | CPCC | CPCC581859 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_010501_69740193 | 2009 | Before | 2009-08-11 12:59 | 2009-08-11 13:33 | 1 | 34.267 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: transformer fuse | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 746729 | CPCC | CPCC582715 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_127003_789340132 | 2009 | Before | 2009-08-17 19:23 | 2009-08-17 20:23 | 25 | 1509.167 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | INTERFERENCE | VEHICLE ACCIDENT | POLE OH |  |  |  | PROSPER: Car hit a pole. De-energized line to try and make temperary repairs | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2547 | 45.3965
4W8 | 742770 | CPCC | CPCC582279 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_110900_69740201 | 2009 | Before | 2009-08-13 11:15 | 2009-08-13 12:00 | 3 | 134 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: Blown line fuse on pole# 110900 due to b/o x-fmr cut-out on pole# 111800. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.1672 | 45.4102
4W8 | 742775 | CPCC | CPCC582289 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_111800_69740200 | 2009 | Before | 2009-08-13 11:30 | 2009-08-13 14:49 | 1 | 198.183 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: B/O x-fmr cutouts on pole # 111800. Crew enroute to replace cutouts. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 741583 | CPCC | CPCC590364 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_309009_933390244 | 2009 | Before | 2009-10-03 17:35 | 2009-10-03 21:15 | 12 | 2637.6 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | SNOW, SLEET AND BLIZZARD |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: snow laoding | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 741585 | CPCC | CPCC590368 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_299920_304570087 | 2009 | Before | 2009-10-03 18:02 | 2009-10-04 03:12 | 38 | 20902.15 | 0 | 0 | 2 | Y | N | N | N | N |  | WEATHER | SNOW, SLEET AND BLIZZARD |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: wire down | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.208 | 45.2782
4W8 | 741588 | CPCC | CPCC590373 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_055001_69740107 | 2009 | Before | 2009-10-03 19:10 | 2009-10-03 23:48 | 159 | 20705.8 | 0 | 0 | 2 | Y | N | N | N | N |  | WEATHER | SNOW, SLEET AND BLIZZARD |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: wire down beyond fuses on pole 030004 | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2181 | 45.4112
4W8 | 741589 | CPCC | CPCC590376 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_299920_304570087 | 2009 | Before | 2009-10-03 19:16 | 2009-10-04 03:12 | 12 | 5715 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | SNOW, SLEET AND BLIZZARD |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: wire down | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.208 | 45.2782
4W8 | 756228 | CPCC | CPCC617380 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_169701_1560029376 | 2010 | Before | 2010-02-06 10:52 | 2010-02-06 11:30 | 8 | 302.267 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD SUSPECTED, NO MORTALITY |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: blown line fuse, patrol | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.1886 | 45.3928
4W8 | 756229 | CPCC | CPCC617381 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_169701_1560029376 | 2010 | Before | 2010-02-06 11:37 | 2010-02-06 12:35 | 8 | 469.333 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (PROTECTED SPECIES) (BMTS) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: blown line fuse Hawk pole 162200 | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.1886 | 45.3928
4W8 | 758662 | CPCC | CPCC627246 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_309505_933390214 | 2010 | Before | 2010-04-08 16:23 | 2010-04-08 17:46 | 1 | 82.417 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: Crew to replace b/o cut-outs on dip pole # 309505 | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2306 | 45.3593
4W8 | 754759 | CPCC | CPCC628617 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_299880_304570096 | 2010 | Before | 2010-04-19 14:12 | 2010-04-19 15:17 | 1 | 65.483 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: Serviceman replaced the B/O secondary connection at the transformer, customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 757488 | CPCC | CPCC611046 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_309300_933390198 | 2010 | Before | 2010-01-07 17:04 | 2010-01-07 18:03 | 47 | 2768.3 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Blown dip fuse. Patrolled and could not find a cause. Refused and customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2301 | 45.3573
4W8 | 757887 | CPCC | CPCC627667 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_308242_933390255 | 2010 | Before | 2010-04-10 15:35 | 2010-04-10 16:28 | 1 | 52.233 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: Broken cutout. Repairs made and customer is back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 757192 | CPCC | CPCC621600 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_127003_789340132 | 2010 | Before | 2010-03-12 08:56 | 2010-03-12 09:17 | 25 | 506.667 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | B/O EQUIPMENT | INSULATOR OH |  |  |  | PROSPER: Serviceman opened fuses on pole# 127003 to replace a broken side stack on pole# 188900. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2547 | 45.3965
4W8 | 759586 | CPCC | CPCC606281 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_172801_101040323 | 2009 | Before | 2009-12-12 19:14 | 2009-12-12 19:51 | 1 | 37.817 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: REPLACED TRANSFORMER FUSE | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 757211 | CPCC | CPCC625744 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_120702_1560029373 | 2010 | Before | 2010-04-01 08:42 | 2010-04-01 09:18 | 7 | 254.8 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused the tapline fuse at pole# 120702 and it held, the cause is unknown, customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.146 | 45.4074
4W8 | 757602 | CPCC | CPCC626365 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_308401_933390284 | 2010 | Before | 2010-04-04 13:21 | 2010-04-04 14:09 | 1 | 48.8 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: changed connector at wx / head | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 758086 | CPCC | CPCC618169 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_106900_69740175 | 2010 | Before | 2010-02-14 09:38 | 2010-02-14 11:08 | 8 | 718.4 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: on site patrolling, could not find any problems, refused, power on | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.1738 | 45.4113
4W8 | 740799 | CPCC | CPCC591343 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_018340_633620094 | 2009 | Before | 2009-10-02 14:17 | 2009-10-02 18:31 | 1 | 254 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: crew made repairs to bad ug primary cable. customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2552 | 45.4161
4W8 | 735701 | CPCC | CPCC575036 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_214700_101040193 | 2009 | Before | 2009-07-11 13:17 | 2009-07-11 16:50 | 1 | 212.917 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 737362 | CPCC | CPCC587107 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_054900_69740133 | 2009 | Before | 2009-09-13 17:17 | 2009-09-13 17:48 | 3 | 94.15 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Blown transformer fuse, no cause found. Refused and customer is back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 739386 | CPCC | CPCC581525 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_330502_579890068 | 2009 | Before | 2009-08-09 12:13 | 2009-08-09 12:57 | 11 | 479.6 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (PROTECTED SPECIES) (BMTS) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Blown line fuse, found owl at pole 335301. Refused and customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2076 | 45.4338
4W8 | 740162 | CPCC | CPCC581061 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_309015_933390246 | 2009 | Before | 2009-08-06 13:43 | 2009-08-06 17:11 | 11 | 2282.683 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | PROSPER: Per serviceman: B/O x-frm on pole# 309015. Crew needed to replace xfmr. Crew on another job but will head here next. Crew has to go to another pole fire and then will get to this job. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 740166 | CPCC | CPCC581087 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_302502_933390306 | 2009 | Before | 2009-08-06 14:27 | 2009-08-06 16:04 | 10 | 971.167 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | POLE OH |  |  |  | PROSPER: Crew needed to make repairs to pole# 300100 that caught fire due to an Osprey nest. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2458 | 45.3599
4W8 | 740167 | CPCC | CPCC581090 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_302502_933390306 | 2009 | Before | 2009-08-06 14:43 | 2009-08-06 16:04 | 3 | 243.55 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | POLE FIRE | POLE OH |  |  |  | PROSPER: Serviceman took outage on the A & B phase tapline fuses at pole# 302502 to clear a pole fire, the fire was started by an Osprey nest on pole# 300100 | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2458 | 45.3599
4W8 | 738606 | CPCC | CPCC581442 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_219504_101040192 | 2009 | Before | 2009-08-08 12:59 | 2009-08-08 13:40 | 1 | 41.6 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Blown tap fuse. No cause found. Refused and customer is back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.1885 | 45.3744
4W8 | 738356 | CPCC | CPCC581428 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_074604_69740135 | 2009 | Before | 2009-08-08 09:48 | 2009-08-08 11:14 | 1 | 85.15 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Service wire was down, customers mast was tore down as well. Disconnect transformer untill customer repairs are complete. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 735129 | CPCC | CPCC570139 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_200001_1560001075 | 2009 | Before | 2009-06-05 21:38 | 2009-06-05 22:40 | 15 | 750.5 | 0 | 0 | 2 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused both tap line and dip pole fuses ok. Cause was lightning. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2295 | 45.3668
4W8 | 735130 | CPCC | CPCC570140 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_264700_1560098495 | 2009 | Before | 2009-06-05 22:42 | 2009-06-05 23:44 | 5 | 310 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused tap line ok. Cause was lightning. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.1567 | 45.3633
4W8 | 778570 | CPCC | CPCC644077 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_218801_101040201 | 2010 | Before | 2010-07-15 18:51 | 2010-07-15 20:30 | 1 | 99.317 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: refused xfmr, no cause found | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 777905 | CPCC | CPCC647199 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_290005_933390367 | 2010 | Before | 2010-07-28 13:09 | 2010-07-28 13:36 | 8 | 215.867 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Blown x-fmr fus edue to lightning. Serviceman replaced fuse and it held. Customers back in service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 777906 | CPCC | CPCC647200 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_320916_997300257 | 2010 | Before | 2010-07-28 13:14 | 2010-07-28 15:07 | 3 | 339.8 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | TRANSFORMER OH |  |  |  | PROSPER: Crew needed to change out a B/O transformer on pole# 320916, the cause was lightning | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 778720 | CPCC | CPCC647406 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_210200_579890079 | 2010 | Before | 2010-07-28 19:56 | 2010-07-28 20:45 | 2 | 97.567 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Blow line fuse, cause was lightning. Refused and customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2083 | 45.4601
4W8 | 774364 | CPCC | CPCC647491 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_140701_163440206 | 2010 | Before | 2010-07-29 11:26 | 2010-07-29 12:36 | 1 | 69.917 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: Crew replaced b/o cut-outs on this x-fmr bank. Customer back in service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 778346 | CPCC | CPCC647655 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_092300_579890054 | 2010 | Before | 2010-07-30 16:45 | 2010-07-30 19:34 | 1 | 169.383 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: lightning caused padmount fuse to blow, relaced | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 778831 | CPCC | CPCC646825 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_100201_69740171 | 2010 | Before | 2010-07-26 17:13 | 2010-07-26 18:30 | 1 | 76.783 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: repaired service | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 778101 | CPCC | CPCC636084 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_019101_633620091 | 2010 | Before | 2010-05-21 07:59 | 2010-05-21 08:23 | 2 | 47.433 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: customer checked breakers on IVR call back. Blown transformer fuse (no cause found). Serviceman replaced fuse and fuse held. Customers back in service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 775345 | CPCC | CPCC639312 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_198500_101040292 | 2010 | Before | 2010-06-15 13:05 | 2010-06-15 13:33 | 1 | 28.017 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: Serviceman replaced a b/o connector and customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 776196 | CPCC | CPCC647921 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_087200_69740433 | 2010 | Before | 2010-08-02 10:42 | 2010-08-02 11:19 | 1 | 36.917 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused transformer# 087200 and it held, the cause is unknown, customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 769417 | CPCC | CPCC620088 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | EPS_CB4W8 | 2010 | Before | 2010-03-02 14:15 | 2010-03-02 14:21 | 1419 | 7686.25 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Loss of transmission line | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2827 | 45.4182
4W8 | 771885 | CPCC | CPCC639238 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_308400_933390287 | 2010 | Before | 2010-06-14 19:15 | 2010-06-14 20:55 | 2 | 198.367 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: Bad order Cutout. Replaced cutout and customers have power. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 767951 | CPCC | CPCC623627 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | Line Cut-41906 | 2010 | Before | 2010-03-27 10:15 | 2010-03-27 10:56 | 4 | 161.933 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | LIGHTNING ARRESTER OH |  |  |  | PROSPER: closed in error, line fuse open. Bad lightning arrestor | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2471 | 45.3799
4W8 | 767953 | CPCC | CPCC623634 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | Line Cut-41907 | 2010 | Before | 2010-03-27 11:02 | 2010-03-27 11:21 | 4 | 78.733 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | LIGHTNING ARRESTER OH |  |  |  | PROSPER: Serviceman cleared a bad lightning arrestor | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2471 | 45.3799
4W8 | 768326 | CPCC | CPCC618495 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_057903_69740151 | 2010 | Before | 2010-02-17 09:55 | 2010-02-17 10:58 | 1 | 62.617 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: Serviceman replaced the B/O secondary connections at the weatherhead, customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 770743 | CPCC | CPCC642003 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_212000_101040180 | 2010 | Before | 2010-07-05 16:56 | 2010-07-05 17:33 | 1 | 36.517 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: bad secondary conn at pole | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 767353 | CPCC | CPCC620757 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_028300_750140221 | 2010 | Before | 2010-03-07 12:35 | 2010-03-07 13:14 | 4 | 154.6 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Blown transformer fuse. Melted out fuse, refused and customer is back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 782918 | CPCC | CPCC639816 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_120702_1560029373 | 2010 | Before | 2010-06-20 15:51 | 2010-06-20 16:42 | 7 | 355.483 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Blown line fuse, no cause found. Refused and customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.146 | 45.4074
4W8 | 780566 | CPCC | CPCC647138 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_330600_579890067 | 2010 | Before | 2010-07-27 18:39 | 2010-07-27 22:18 | 30 | 6570 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Blown line fuse, lightning struck insulator and threw phase on the ground. Repairs made and customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2092 | 45.4353
4W8 | 782194 | CPCC | CPCC633373 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_124401_69740186 | 2010 | Before | 2010-05-14 08:29 | 2010-05-14 09:40 | 1 | 70.917 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Refused transformer. no cause found | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 784617 | CPCC | CPCC632980 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_175900_101040321 | 2010 | Before | 2010-05-10 06:46 | 2010-05-10 07:10 | 2 | 48.233 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (PROTECTED SPECIES) (BMTS) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: dead owl on the pump house - Serviceman refused xfmr and customer is back in service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 780298 | CPCC | CPCC647075 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_308242_933390255 | 2010 | Before | 2010-07-27 14:37 | 2010-07-27 18:15 | 1 | 217.683 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | PROSPER: b/o xfmr. Crew to replace. Crew repalced and customer are back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 780302 | CPCC | CPCC647096 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_106900_69740175 | 2010 | Before | 2010-07-27 15:26 | 2010-07-27 16:33 | 7 | 463.05 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman found an open tapline fuse, he will patrol. Lightning blew fuse. Serviceman replaced fue and all customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.1738 | 45.4113
4W8 | 783895 | CPCC | CPCC633779 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_191901_101040303 | 2010 | Before | 2010-05-18 08:15 | 2010-05-18 09:23 | 1 | 68.033 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused transformer# 191901 and it held, the cause is unknown, customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 785480 | CPCC | CPCC636764 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_220000_101040194 | 2010 | Before | 2010-05-26 07:18 | 2010-05-26 07:56 | 2 | 76.967 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (PROTECTED SPECIES) (BMTS) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 220000 and it held, the cause was an Owl, customers are back in full service. Serviceman will fill out the report and properly dispose of the bird. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 785495 | CPCC | CPCC643141 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_124401_69740186 | 2010 | Before | 2010-07-10 09:58 | 2010-07-10 11:57 | 1 | 118.967 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD SUSPECTED, NO MORTALITY |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: refused cut out | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 783528 | CPCC | CPCC640976 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_283904_163440173 | 2010 | Before | 2010-06-29 15:27 | 2010-06-29 16:27 | 2 | 120.967 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused the transformer and it held, the cause was lightning, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 781690 | CPCC | CPCC638042 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_135401_852830227 | 2010 | Before | 2010-06-07 07:32 | 2010-06-07 09:42 | 2 | 259.167 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | PROSPER: Blown x-fmr fuses on this x-fmr bank. Per crew: B/O x-fmr. Customer states they do not need these pumps for a couple of days. Crew to make repairs at a later time. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 760569 | CPCC | CPCC612558 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_169701_1560029376 | 2010 | Before | 2010-01-17 08:10 | 2010-01-17 09:06 | 8 | 448.8 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Patrolled, no cause found. Re-fused and customers are back in service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.1886 | 45.3928
4W8 | 766158 | CPCC | CPCC616533 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_166700_1560039176 | 2010 | Before | 2010-01-27 20:55 | 2010-01-27 22:07 | 1 | 71.983 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: replaced transformer fuse | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 800023 | CPCC | CPCC660809 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_201000_101040247 | 2010 | Before | 2010-10-24 09:18 | 2010-10-24 10:19 | 1 | 60.95 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: replaced deteriorated fuse | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 799256 | CPCC | CPCC657293 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_289901_163440168 | 2010 | Before | 2010-10-07 07:02 | 2010-10-07 07:57 | 19 | 1034.55 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused tap line and it held at structure #289901 no cause found | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.1877 | 45.3668
4W8 | 800123 | CPCC | CPCC665531 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_137101_852830185 | 2010 | Before | 2010-11-20 11:09 | 2010-11-20 11:49 | 2 | 80.1 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Tree down through Primary wire. No one avaliable to make repairs, customer says it's ok that we come back later today to make repairs. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2559 | 45.3847
4W8 | 803698 | CPCC | CPCC659817 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_330600_579890067 | 2010 | Before | 2010-10-19 14:35 | 2010-10-19 15:46 | 30 | 2130.5 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | POLE FIRE | POLE OH |  |  |  | PROSPER: Crew took outage on the tapline fuses at pole# 330600 to replace a pole that caught fire. Customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2092 | 45.4353
4W8 | 800226 | CPCC | CPCC654869 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_299980_304570091 | 2010 | Before | 2010-09-18 17:44 | 2010-09-18 18:51 | 1 | 67.433 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: serviceman refused, no cause found | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 798638 | CPCC | CPCC652783 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_144101_163440224 | 2010 | Before | 2010-09-02 14:13 | 2010-09-02 16:27 | 1 | 134.05 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | PROSPER: Crew needed to change out a B/O transformer on pole# 144101. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 802653 | CPCC | CPCC660304 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_237500_852830222 | 2010 | Before | 2010-10-22 18:12 | 2010-10-22 18:56 | 1 | 44.05 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 237500 and it held, the cause was a sparrow, customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 804540 | CPCC | CPCC688459 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_027305_750140175 | 2011 | Before | 2011-03-13 13:53 | 2011-03-13 15:20 | 1076 | 94150 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Found Limb on line, removed limb, line enrgized and holding | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2771 | 45.4161
4W8 | 799898 | CPCC | CPCC656292 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_106900_69740175 | 2010 | Before | 2010-09-26 17:22 | 2010-09-26 18:43 | 8 | 645.2 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD SUSPECTED, NO MORTALITY |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: patroled, no cause fund, replaced fuse | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.1738 | 45.4113
4W8 | 804223 | CPCC | CPCC687600 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_320911_997300261 | 2011 | Before | 2011-03-10 09:14 | 2011-03-11 00:47 | 3 | 2798.1 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | POLE OH |  |  |  | PROSPER: Crew needed to replace a pole that caught fire. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 804226 | CPCC | CPCC687604 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | SB_319801_1560102474 | 2011 | Before | 2011-03-10 09:32 | 2011-03-10 11:29 | 18 | 2102.7 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | POLE FIRE | POLE OH |  |  |  | PROSPER: Serviceman took outage on the tapline fuse at pole# 319801 to make temp repairs to a pole fire, customers are back in full service at this time. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2299 | 45.3502
4W8 | 800376 | CPCC | CPCC665535 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_138101_852830230 | 2010 | Before | 2010-11-20 11:51 | 2010-11-20 11:58 | 1 | 7.167 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Associated with outage 665531. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 793621 | CPCC | CPCC653225 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_027305_750140175 | 2010 | Before | 2010-09-07 09:47 | 2010-09-07 10:08 | 1071 | 22383.9 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman found an open FR, no cause found for the lockout but the recloser had a battery alarm and did not operate. The instantaneous relays have been disabled due to the battery problem. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2771 | 45.4161
4W8 | 792917 | CPCC | CPCC664786 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_010506_673650378 | 2010 | Before | 2010-11-16 03:31 | 2010-11-16 13:21 | 3 | 1768.85 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Tree fell through service crew cut service to 806 and 804 , will return later. Customer's back in service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 792923 | CPCC | CPCC664794 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_220500_101040204 | 2010 | Before | 2010-11-16 04:46 | 2010-11-16 07:21 | 23 | 3571.133 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Blown line fuse. Serviceman patrolled and found limbs on the ground (had cleared themselves). Serviceman replaced fuse and it held. Customers back in service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.1873 | 45.3744
4W8 | 792924 | CPCC | CPCC664798 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_027305_750140175 | 2010 | Before | 2010-11-16 05:24 | 2010-11-16 05:46 | 1072 | 23530.4 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | INTENTIONAL TO CLEAR TROUBLE | TREES | TREE - NON-PREVENTABLE | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: serviceman opened field recloser, tree burning on line | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2771 | 45.4161
4W8 | 796527 | CPCC | CPCC652109 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_330600_579890067 | 2010 | Before | 2010-08-28 19:45 | 2010-08-28 23:12 | 30 | 6209 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | POLE OH |  |  |  | PROSPER: pole burnt off. Crew made repairs | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2092 | 45.4353
4W8 | 798153 | CPCC | CPCC656906 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_308301_933390257 | 2010 | Before | 2010-10-04 07:42 | 2010-10-04 08:33 | 2 | 102.033 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 308301 and it held, the cause was a starling, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 793360 | CPCC | CPCC653173 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_027305_750140175 | 2010 | Before | 2010-09-07 09:09 | 2010-09-07 09:30 | 1071 | 23205 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman found an open FR, he will patroll, no cause found for the lockout but the recloser had a battery alarm and did not operate. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2771 | 45.4161
4W8 | 795747 | CPCC | CPCC656631 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_240404_163440214 | 2010 | Before | 2010-09-30 08:09 | 2010-09-30 08:56 | 1 | 47.083 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 240404 and it held, the cause was a starling, customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 793429 | CPCC | CPCC657543 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_309303_933390280 | 2010 | Before | 2010-10-08 09:05 | 2010-10-08 10:18 | 1 | 72.483 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: Serviceman is onsite replacing a B/O secondary connection at the transformer, customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 792665 | CPCC | CPCC664744 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | Line Cut-46497 | 2010 | Before | 2010-11-16 01:39 | 2010-11-16 02:24 | 2 | 88.467 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind slapped phases together | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2688 | 45.3961
4W8 | 792797 | CPCC | CPCC650221 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_232501_163440225 | 2010 | Before | 2010-08-17 09:36 | 2010-08-17 10:16 | 1 | 39.783 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 232501 and it held, the cause was a squirrel, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 796766 | CPCC | CPCC649282 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_289901_163440168 | 2010 | Before | 2010-08-12 09:57 | 2010-08-12 10:44 | 19 | 877.483 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused the tapline fuse at pole# 289901 and it held, the cause is unknown, customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.1877 | 45.3668
4W8 | 807027 | CPCC | CPCC698245 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_169701_1560029376 | 2011 | Before | 2011-03-25 07:46 | 2011-03-25 08:54 | 8 | 537.6 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused the tapline fuses at pole# 169701 and they held, the cause is unknown, customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.1886 | 45.3928
4W8 | 809822 | CPCC | CPCC700194 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_169701_1560029376 | 2011 | Before | 2011-04-04 18:16 | 2011-04-04 19:12 | 8 | 448.667 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: A phase cutout open at Pole 169701, serviceman patrolling. No cause found, fuse replaced and good, customer power restored. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.1886 | 45.3928
4W8 | 806647 | CPCC | CPCC691277 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_295600_304570113 | 2011 | Before | 2011-03-13 15:12 | 2011-03-13 15:44 | 1 | 32.65 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Part of Outage # 688940 | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 805136 | CPCC | CPCC697138 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_320803_997300263 | 2011 | Before | 2011-03-19 19:46 | 2011-03-19 20:43 | 3 | 170.7 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: Broken transformer cutout. Made repairs and customers are back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 807131 | CPCC | CPCC671425 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_136000_852830228 | 2010 | Before | 2010-12-19 03:26 | 2010-12-19 04:21 | 2 | 109.4 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: replaced transformer fuse | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 805595 | CPCC | CPCC689665 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_270101_163440166 | 2011 | Before | 2011-03-13 14:48 | 2011-03-13 15:48 | 1 | 60.5 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Associate with outage # 688940 | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 806910 | CPCC | CPCC691614 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_319806_997300390 | 2011 | Before | 2011-03-13 15:30 | 2011-03-13 15:42 | 1 | 11.983 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Power back on, part of Outage #688949 | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 807741 | CPCC | CPCC696848 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_210200_579890079 | 2011 | Before | 2011-03-18 11:13 | 2011-03-18 12:09 | 2 | 111.933 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: Serviceman onsite making repairs to the highside jumper to the cutout on pole# 210200. Repairs complete. Customers back in service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2083 | 45.4601
4W8 | 786536 | CPCC | CPCC643369 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_304601_933390317 | 2010 | Before | 2010-07-11 12:39 | 2010-07-11 13:25 | 1 | 46.067 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | PROSPER: replaced deteriorated secondary connections. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 789370 | CPCC | CPCC651732 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_210104_1560038602 | 2010 | Before | 2010-08-26 15:32 | 2010-08-26 16:18 | 172 | 7848.933 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman removed a limb from the overhead primary and refused the tapline fuse at pole# 210104, customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2064 | 45.28
4W8 | 786357 | CPCC | CPCC637074 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | EPS_CB4W8 | 2010 | Before | 2010-05-28 08:04 | 2010-05-28 08:16 | 1420 | 16590.333 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | B/O EQUIPMENT | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | PROSPER: Crew took outage on CB 4W8 to bypass FR# 4W13 that is on fire. Customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2827 | 45.4182
4W8 | 789619 | CPCC | CPCC651583 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_248501_852830212 | 2010 | Before | 2010-08-25 09:32 | 2010-08-25 10:54 | 1 | 82.85 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: Servicemen called for help to change out a B/O cutout on a transformer bank. Customer one site and said this will not be used for the rest of the day, servicemen will replace the cutout as soon as possible. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 789622 | CPCC | CPCC651736 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_298704_304570142 | 2010 | Before | 2010-08-26 15:41 | 2010-08-26 16:18 | 1 | 36.517 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Associate to outage# 651732. Serviceman removed a limb from the overhead primary and refused the tapline fuse at pole# 210104, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 787629 | CPCC | CPCC649602 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_232501_163440225 | 2010 | Before | 2010-08-14 10:48 | 2010-08-14 11:20 | 1 | 32.75 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: refused xfmr, no cause found | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 827862 | CPCC | CPCC705329 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_283901_163440172 | 2011 | Before | 2011-05-14 06:47 | 2011-05-14 08:06 | 1 | 79.55 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: Broken Cut-out, temporary jumper installed, customer power restored. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 827863 | CPCC | CPCC705330 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_218700_101040199 | 2011 | Before | 2011-05-14 07:34 | 2011-05-14 08:32 | 1 | 57.6 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | LIGHTNING ARRESTER OH |  |  |  | PROSPER: bad order lightning arrester caused outage | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 827866 | CPCC | CPCC705333 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_219800_101040178 | 2011 | Before | 2011-05-14 08:20 | 2011-05-14 08:31 | 2 | 21.633 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | LIGHTNING ARRESTER OH |  |  |  | PROSPER: bad order lightning arrester | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.1882 | 45.3791
4W8 | 828234 | CPCC | CPCC706283 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_047701_69740163 | 2011 | Before | 2011-05-22 18:36 | 2011-05-22 19:18 | 1 | 41.917 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: replaced transformer fuse, no cause found | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 828235 | CPCC | CPCC706288 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_110900_69740201 | 2011 | Before | 2011-05-22 21:48 | 2011-05-22 22:50 | 5 | 310.417 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: patrolled and replaced line fuse, no cause found | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.1672 | 45.4102
4W8 | 828237 | CPCC | CPCC706290 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_110900_69740201 | 2011 | Before | 2011-05-22 22:54 | 2011-05-23 01:28 | 5 | 769.583 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: isolated pump bank, replaced line fuse | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.1672 | 45.4102
4W8 | 826726 | CPCC | CPCC703738 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_137201_852830232 | 2011 | Before | 2011-04-29 13:27 | 2011-04-29 14:41 | 1 | 74.567 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: Serviceman will call for help to replace a B/O cutout on pole# 137201.Customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 819428 | CPCC | CPCC670666 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_169701_1560029376 | 2010 | Before | 2010-12-15 18:31 | 2010-12-15 20:32 | 8 | 966.933 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Blown line fuse, service man is patrolling. Service man found no cause, replaced fuse. Customer power restored | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.1886 | 45.3928
4W8 | 821810 | CPCC | CPCC705655 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_110900_69740201 | 2011 | Before | 2011-05-16 06:55 | 2011-05-16 08:15 | 5 | 401.417 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: serviceman located open Fuse @ FP# 110900, patroling for cause(08:00), none found/located, refused on test, outage restored | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.1672 | 45.4102
4W8 | 818287 | CPCC | CPCC699540 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_247900_852830189 | 2011 | Before | 2011-03-31 02:39 | 2011-03-31 04:48 | 13 | 1681.55 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | LIGHTNING ARRESTER OH |  |  |  | PROSPER: A phase fuse blown at pole #247900. Replaced bad lightning arrestor and then replaced fuse, customer power restored. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2563 | 45.3817
4W8 | 822074 | CPCC | CPCC705685 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_203500_101040258 | 2011 | Before | 2011-05-16 09:24 | 2011-05-16 10:29 | 2 | 130.067 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | TRANSFORMER OH |  |  |  | PROSPER: Blown xfmr fuses. Serviceman investigating. Lighting damged xfmr bank and custmer's equipment. Customer will make reparis to their equipment and then crew will replace xfmr bank and energize customer. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 818505 | CPCC | CPCC677833 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_140702_163440205 | 2011 | Before | 2011-01-29 17:25 | 2011-01-29 18:38 | 1 | 72.7 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Found cutout door open, no cause found, will re-fuse. Replaced fuse, customer power restored. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 818522 | CPCC | CPCC696299 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_289901_163440168 | 2011 | Before | 2011-03-16 06:39 | 2011-03-16 07:51 | 19 | 1374.65 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman found open tap line fuse. Serviceman patrolled it out and found no cause. He replaced fuse and it held. All customers back in service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.1877 | 45.3668
4W8 | 822110 | CPCC | CPCC707675 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_309007_933390239 | 2011 | Before | 2011-06-06 11:51 | 2011-06-06 13:31 | 3 | 297.7 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: servicman reporting while responding to antoher outage, located failed OH Primary Jumper contacted OH Transformer at saome FP# 309007, crew to maker repairs/restore(11:53), completed, restored | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 823765 | CPCC | CPCC712843 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_087000_69740433 | 2011 | Before | 2011-07-18 08:18 | 2011-07-18 08:46 | 1 | 27.333 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 087000 and it held, the cause was lighting, pump is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 823773 | CPCC | CPCC715820 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_303101_933390295 | 2011 | Before | 2011-08-01 19:30 | 2011-08-01 23:19 | 3 | 686.95 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | TRANSFORMER OH |  |  |  | PROSPER: crew replaced transformer | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 822554 | CPCC | CPCC708829 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_110900_69740201 | 2011 | Before | 2011-06-16 17:18 | 2011-06-16 17:57 | 5 | 194.083 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: blown line fuse , serviceman on site Tree limb on cutout. Outage restored | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.1672 | 45.4102
4W8 | 822972 | CPCC | CPCC715679 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_308301_933390257 | 2011 | Before | 2011-08-01 06:54 | 2011-08-01 07:48 | 2 | 108.8 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Blown x-fmr fuse, cause was a starling, serviceman replaced fuse and it held. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 818996 | CPCC | CPCC676101 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_027305_750140175 | 2011 | Before | 2011-01-16 22:34 | 2011-01-16 23:02 | 1075 | 30386.667 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Field Recloser 4W12 is locked open, serviceman is patrolling. Remove tree limb on all 3 phases. Closed FR 4W12, all customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2771 | 45.4161
4W8 | 835686 | CPCC | CPCC712524 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_120100_69740181 | 2011 | Before | 2011-07-15 07:23 | 2011-07-15 08:35 | 1 | 72.15 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused transformer# 120100 and it held, the cause is unknown, customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 831368 | CPCC | CPCC701569 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_259700_1560000907 | 2011 | Before | 2011-04-18 07:11 | 2011-04-18 08:57 | 1 | 106.067 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | OVERLOAD |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: response located OH Secondary Triplex burnt in the clear at midspan due to load, upgraded to 4/0 triplex, outage restored | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 834186 | CPCC | CPCC714074 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_054900_69740133 | 2011 | Before | 2011-07-28 06:22 | 2011-07-28 07:39 | 1 | 77.383 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused transformer# 055601 and it held, the cause was a rotted fuse, pump is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 835871 | CPCC | CPCC713071 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_129200_789340144 | 2011 | Before | 2011-07-19 17:44 | 2011-07-19 19:06 | 1 | 81.417 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman arrived and found blown fuses will replace and close on test, and report. closed in and it held outage restored. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 834682 | CPCC | CPCC702118 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_010202_69740111 | 2011 | Before | 2011-04-21 20:11 | 2011-04-21 22:05 | 3 | 342.85 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: patrolled line, no cause found. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.1457 | 45.4149
4W8 | 831607 | CPCC | CPCC711979 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_057901_69740153 | 2011 | Before | 2011-07-09 12:59 | 2011-07-09 13:53 | 1 | 54.133 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE ONLY -UG ( NO CAUSE FOUND) |  |  |  | PROSPER: Serviceman arrived and found blown fuse possible melt out. Re fused and it held. Outage restored | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 836014 | CPCC | CPCC703377 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_280103_1560060764 | 2011 | Before | 2011-04-27 17:52 | 2011-04-27 18:43 | 1 | 51.267 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: Serviceman arrived and found b/o cutout. made temp repairs.. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 831657 | CPCC | CPCC712424 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_234302_163440222 | 2011 | Before | 2011-07-14 06:21 | 2011-07-14 07:24 | 1 | 62.583 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: starling, replaced transformer fuse | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 830495 | CPCC | CPCC706360 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_280600_579890077 | 2011 | Before | 2011-05-23 18:33 | 2011-05-23 18:40 | 1 | 7.183 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | POLE OH |  |  |  | PROSPER: Replaced fuses and repaired guy wire. Pumps were not in service yet. Damage was caused by bulls in the field, Times are not correct due to work completed before outage verified. Customer called serviceman. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 849292 | CPCC | CPCC725312 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_210107_267850135 | 2011 | Before | 2011-10-11 11:13 | 2011-10-11 12:05 | 11 | 576.217 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | B/O EQUIPMENT | CUT-OUT B/O OH |  |  |  | SOURCE: Serviceman took outage on the dip at pole# 210107 due to a B/o cutout that caused the pole to burn, customers are back in full service. completed & restored | DISTRIBUTION | DEVICE | MANUAL | 2011-10-11 14:13 | COMPLETED |  | 2011-10-11 11:13 | 2011-10-11 12:05 | 2011-10-11 12:14 | -117.2075 | 45.2798
4W8 | 854545 | CPCC | CPCC727494 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_110900_69740201 | 2011 | Before | 2011-10-27 14:59 | 2011-10-27 22:40 | 6 | 2767.8 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | B/O EQUIPMENT | INSULATOR OH |  |  |  | SOURCE: crew created emergency damage repair outage to replace failed/broken OH Primary Insulators Crew made repairs, Outage restored. | DISTRIBUTION | DEVICE | MANUAL | 2011-10-27 17:00 | COMPLETED |  | 2011-10-27 14:59 | 2011-10-27 22:40 | 2011-10-28 05:30 | -117.1672 | 45.4102
4W8 | 847810 | CPCC | CPCC724658 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_110900_69740201 | 2011 | Before | 2011-10-06 06:03 | 2011-10-06 07:03 | 6 | 359.5 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman refused the tapline fuse at pole# 110900 and it held, the cause is unknown, customers are back in full service. | DISTRIBUTION | DEVICE | AUTO | 2011-10-06 08:30 | COMPLETED |  | 2011-10-06 06:03 | 2011-10-06 07:03 | 2011-10-06 07:40 | -117.1672 | 45.4102
4W8 | 849265 | CPCC | CPCC725256 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_110900_69740201 | 2011 | Before | 2011-10-11 08:42 | 2011-10-11 10:48 | 5 | 630.917 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman located open fuse, investigated for cause, none found, refused, outage restored | DISTRIBUTION | DEVICE | AUTO | 2011-10-11 11:30 | COMPLETED |  | 2011-10-11 08:42 | 2011-10-11 10:48 | 2011-10-11 10:49 | -117.1672 | 45.4102
4W8 | 849172 | CPCC | CPCC725167 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_191601_1560039145 | 2011 | Before | 2011-10-10 18:22 | 2011-10-10 19:37 | 1 | 75.367 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: patroled & refused, no cause | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2011-10-10 20:45 | COMPLETED |  | 2011-10-10 18:22 | 2011-10-10 19:37 | 2011-10-10 19:49 | -117.2454 | 45.4644
4W8 | 861403 | CPCC | CPCC732908 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_247900_852830189 | 2011 | Before | 2011-11-23 14:02 | 2011-11-23 16:50 | 15 | 2525 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: blown line fus no cause found | DISTRIBUTION | DEVICE | AUTO | 2011-11-23 17:15 | COMPLETED |  | 2011-11-23 14:02 | 2011-11-30 11:09 | 2011-11-23 17:46 | -117.2563 | 45.3817
4W8 | 861405 | CPCC | CPCC732847 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_055921_221510262 | 2011 | Before | 2011-11-23 11:45 | 2011-11-23 16:18 | 1 | 272.767 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: B/O secondary connector. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2011-11-23 14:45 | COMPLETED |  | 2011-11-23 11:45 | 2011-11-23 16:18 | 2011-11-23 17:46 | -117.2159 | 45.3356
4W8 | 861414 | CPCC | CPCC732836 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_247900_852830189 | 2011 | Before | 2011-11-23 11:34 | 2011-11-23 12:53 | 2 | 158.667 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman refused the tapline fuse at pole# 247900 and it held, the cause was wind, customers are back in full service. | DISTRIBUTION | DEVICE | AUTO | 2011-11-23 14:45 | COMPLETED |  | 2011-11-23 11:34 | 2011-11-23 12:53 | 2011-11-23 17:46 | -117.2563 | 45.3817
4W8 | 843211 | CPCC | CPCC718402 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_057901_69740153 | 2011 | Before | 2011-08-24 07:56 | 2011-08-24 08:28 | 1 | 32.133 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 057901 and it held, the cause was a starling, pump is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 849231 | CPCC | CPCC725232 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_110900_69740201 | 2011 | Before | 2011-10-11 06:14 | 2011-10-11 07:20 | 5 | 327.333 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman refused the tapline fuse at pole# 110900 and it held, the cause is unknown, customers are back in full service. | DISTRIBUTION | DEVICE | AUTO | 2011-10-11 08:45 | COMPLETED |  | 2011-10-11 06:14 | 2011-10-11 07:20 | 2011-10-11 08:14 | -117.1672 | 45.4102
4W8 | 844587 | CPCC | CPCC717132 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_057901_69740153 | 2011 | Before | 2011-08-13 10:51 | 2011-08-13 11:01 | 1 | 9.7 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Customer called aserviceman directly has blown fuse on bank. Serviceman arrived and found blown fuse, replaced it outage restored. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 843102 | CPCC | CPCC717455 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_232501_163440225 | 2011 | Before | 2011-08-16 14:21 | 2011-08-16 15:04 | 1 | 43.533 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused transformer# 232501 and it held, the cause is unknown, customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 858736 | CPCC | CPCC729972 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_188401_101040309 | 2011 | Before | 2011-11-14 12:29 | 2011-11-14 13:13 | 1 | 44.55 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: Serviceman made repairs to the B/O highside transformer jumper, customer is back in full service. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2011-11-14 15:30 | COMPLETED |  | 2011-11-14 12:29 | 2011-11-14 13:13 | 2011-11-14 13:53 | -117.2333 | 45.3882
4W8 | 855784 | CPCC | CPCC728101 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_220500_101040204 | 2011 | Before | 2011-11-02 19:47 | 2011-11-02 21:28 | 15 | 1527.25 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown fuse, cause was tree limb. Refused and customers are back on. | DISTRIBUTION | DEVICE | AUTO | 2011-11-02 23:00 | COMPLETED |  | 2011-11-02 19:47 | 2011-11-02 21:28 | 2011-11-03 06:49 | -117.1873 | 45.3744
4W8 | 857932 | CPCC | CPCC729275 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_298901_304570107 | 2011 | Before | 2011-11-11 11:24 | 2011-11-11 13:04 | 1 | 100.35 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman made repairs to the overhead secondary service that was damaged by a tree limb, customer is back in full service. | DISTRIBUTION | CUSTOMER | AUTO |  | COMPLETED |  | 2011-11-11 11:24 | 2011-11-11 13:04 | 2011-11-11 13:43 | -117.212 | 45.2777
4W8 | 861402 | CPCC | CPCC732921 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_245901_1560029747 | 2011 | Before | 2011-11-23 14:39 | 2011-11-23 16:50 | 1 | 131.45 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: high winds no cause found | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2011-11-23 17:45 | COMPLETED |  | 2011-11-23 14:39 | 2011-11-30 11:21 | 2011-11-23 17:46 | -117.2604 | 45.3816
4W8 | 839222 | CPCC | CPCC722722 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_169701_1560029376 | 2011 | Before | 2011-09-20 08:46 | 2011-09-20 09:20 | 8 | 272.933 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused the tapline fuses at pole# 169701 and they held, the cause is unknown, customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.1886 | 45.3928
4W8 | 841190 | CPCC | CPCC717572 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_220500_101040204 | 2011 | Before | 2011-08-17 16:22 | 2011-08-17 17:16 | 31 | 1674.517 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman found open tapline fuses at pole# 220500, he will patrol | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.1873 | 45.3744
4W8 | 841294 | CPCC | CPCC718199 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_057901_69740153 | 2011 | Before | 2011-08-22 07:51 | 2011-08-22 08:20 | 1 | 29.067 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman located open fuse, investigated for cause, none found, refused, outage restored | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 837761 | CPCC | CPCC712310 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_054701_69740434 | 2011 | Before | 2011-07-12 22:29 | 2011-07-12 23:55 | 57 | 4894.4 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - TRIMMABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman arrived and found tripped recloser, patrolled line and found blown fuse with weed across a&b phase. remove refused and closed recloser on test and it held. outage restored. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2196 | 45.4226
4W8 | 840563 | CPCC | CPCC720260 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_022000_69740196 | 2011 | Before | 2011-09-03 09:03 | 2011-09-03 09:44 | 1 | 41.8 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: unknow. suspects lightning. Customer has been gone for a week. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 839791 | CPCC | CPCC718792 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_030003_1560029384 | 2011 | Before | 2011-08-26 06:19 | 2011-08-26 06:58 | 7 | 269.967 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Blown line fuse, serviceman is patrolling. No cause found, fuse replaced and holding, customer pwoer restored. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.1887 | 45.4124
4W8 | 837474 | CPCC | CPCC703027 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_296300_579890065 | 2011 | Before | 2011-04-25 14:10 | 2011-04-25 14:46 | 1 | 35.633 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: Serviceman will get another journeyman to help him replace a B/O cutout on pole# 296300. customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 841035 | CPCC | CPCC719768 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_137605_852830235 | 2011 | Before | 2011-08-30 09:46 | 2011-08-30 10:10 | 2 | 48.033 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman located open fuse, investigated for cause, none found, refused, outage restored | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 842305 | CPCC | CPCC716776 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_137601_1560045617 | 2011 | Before | 2011-08-10 10:39 | 2011-08-10 11:04 | 2 | 50.267 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused the tapline fuse at pole# 137601 and it held, the cause was a starling, customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2559 | 45.391
4W8 | 837980 | CPCC | CPCC713419 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_127003_789340132 | 2011 | Before | 2011-07-21 21:08 | 2011-07-21 21:56 | 14 | 669.433 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Blown line fuse. Serviceman patrolled and did not find a cause. Refused and customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -117.2547 | 45.3965
4W8 | 838782 | CPCC | CPCC717684 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_021200_1560040275 | 2011 | Before | 2011-08-18 16:47 | 2011-08-18 18:57 | 1 | 130.117 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: replaced transformer fuse | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
4W8 | 870830 | CPCC | CPCC737645 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_127003_789340132 | 2011 | Before | 2011-12-29 02:46 | 2011-12-29 04:36 | 14 | 1548.633 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: patroling line no cause, refused & holding | DISTRIBUTION | DEVICE | MANUAL | 2011-12-29 07:45 | COMPLETED |  | 2011-12-29 02:46 | 2011-12-29 04:36 | 2011-12-29 04:56 | -117.2547 | 45.3965
4W8 | 874624 | CPCC | CPCC740146 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_299720_304570069 | 2012 | Before | 2012-01-17 12:38 | 2012-01-17 13:31 | 1 | 52.783 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Deteriorated o/h service. Serviceman made repairs. | DISTRIBUTION | CUSTOMER | AUTO | 2012-01-17 15:45 | COMPLETED |  | 2012-01-17 12:38 | 2012-01-17 13:31 | 2012-01-17 13:47 | -117.2099 | 45.2752
4W8 | 872035 | CPCC | CPCC738621 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | Line Cut-55989 | 2012 | Before | 2012-01-03 09:07 | 2012-01-03 13:29 | 9 | 2355.15 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | POLE OH |  |  |  | SOURCE: Crew needed to replace a pole that was broken by a truck. Customers are back in full service. | DISTRIBUTION | DEVICE | MANUAL | 2012-01-03 15:00 | COMPLETED |  | 2012-01-03 09:07 | 2012-01-03 13:29 | 2012-01-03 14:06 | -117.2084 | 45.5209
4W8 | 873302 | CPCC | CPCC739232 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_309309_933390273 | 2012 | Before | 2012-01-09 21:38 | 2012-01-09 23:16 | 5 | 491.833 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: replaced broken cutout | DISTRIBUTION | DEVICE | AUTO | 2012-01-10 00:45 | COMPLETED |  | 2012-01-09 21:38 | 2012-01-09 23:16 | 2012-01-10 06:16 | -117.2311 | 45.3575
4W8 | 871243 | CPCC | CPCC738064 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_301502_933390313 | 2011 | Before | 2011-12-30 10:33 | 2011-12-30 11:42 | 4 | 279.067 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Serviceman needs another journeyman to help change out a B/O cutout. Customers are back in full service. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2011-12-30 13:45 | COMPLETED |  | 2011-12-30 10:33 | 2011-12-30 11:42 | 2011-12-30 14:36 | -117.2466 | 45.3599
4W8 | 883380 | CPCC | CPCC747928 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_237903_852830183 | 2012 | Before | 2012-02-22 06:03 | 2012-02-22 06:50 | 3 | 140.9 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown line fuse, limb on line. Removed tree line and refused. | DISTRIBUTION | DEVICE | AUTO | 2012-02-22 09:15 | COMPLETED |  | 2012-02-22 06:03 | 2012-02-22 06:54 | 2012-02-22 06:55 | -117.2764 | 45.3811
4W8 | 877556 | CPCC | CPCC743958 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_247900_852830189 | 2012 | Before | 2012-01-21 11:38 | 2012-01-21 21:15 | 16 | 9228.533 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | POLE OH |  |  |  | SOURCE: Crew needed to replace a pole that caught fire. | DISTRIBUTION | DEVICE | MANUAL | 2012-01-21 22:15 | COMPLETED |  | 2012-01-21 11:38 | 2012-01-21 21:15 | 2012-01-22 10:50 | -117.2563 | 45.3817
4W8 | 887486 | CPCC | CPCC751904 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_247900_852830189 | 2012 | Before | 2012-03-03 12:28 | 2012-03-03 14:09 | 13 | 1310.617 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: patroled & refused | DISTRIBUTION | DEVICE | AUTO | 2012-03-03 15:30 | COMPLETED |  | 2012-03-03 12:29 | 2012-03-03 14:09 | 2012-03-03 16:30 | -117.2563 | 45.3817
4W8 | 903656 | CPCC | CPCC767999 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_290011_1560038357 | 2012 | Before | 2012-05-03 07:09 | 2012-05-03 07:56 | 2 | 92.767 | 0 | 0 | 1 | Y | N | N | N | N |  | ENVIRONMENT | FIRE/SMOKE (NOT DUE TO FAULTS) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman refused transformer# 290011 and it held, the cause was a house fire. Customers are back in full service. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-05-03 10:15 | COMPLETED |  | 2012-05-03 07:09 | 2012-05-03 07:56 | 2012-05-03 09:01 | -117.2287 | 45.3525
4W8 | 906298 | CPCC | CPCC769639 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_057901_69740153 | 2012 | Before | 2012-05-15 13:00 | 2012-05-15 13:39 | 1 | 39.283 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman refused transformer# 057901 and it held, the cause is unknown, pump is back in full service. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-05-15 16:00 | COMPLETED |  | 2012-05-15 13:00 | 2012-05-15 13:40 | 2012-05-15 14:10 | -117.2145 | 45.4262
4W8 | 897404 | CPCC | CPCC764104 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_298707_304570100 | 2012 | Before | 2012-04-05 07:09 | 2012-04-05 09:54 | 35 | 5735.684 | 0 | 0 | 2 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | SNOW, SLEET AND BLIZZARD | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman needs another journeyman to help make repairs to the overhead primary that was taken down by a snow covered tree limb. | DISTRIBUTION | DEVICE | MANUAL | 2012-04-05 10:45 | COMPLETED |  | 2012-04-05 07:09 | 2012-04-05 10:54 | 2012-04-05 13:22 | -117.2107 | 45.2748
4W8 | 890854 | CPCC | CPCC756563 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_180000_340370060 | 2012 | Before | 2012-03-16 06:24 | 2012-03-16 08:35 | 1 | 130.983 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Broken cutout. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-03-16 09:30 | COMPLETED |  | 2012-03-16 06:24 | 2012-03-16 08:35 | 2012-03-16 08:45 | -117.1252 | 45.2932
4W8 | 905932 | CPCC | CPCC769394 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_121803_69740182 | 2012 | Before | 2012-05-14 07:58 | 2012-05-14 08:55 | 1 | 57.117 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: serviceman re-fused, customers back in service | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-05-14 11:00 | COMPLETED |  | 2012-05-14 07:58 | 2012-05-14 08:55 | 2012-05-14 11:29 | -117.1426 | 45.4095
4W8 | 906402 | CPCC | CPCC769533 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_205004_101040240 | 2012 | Before | 2012-05-15 10:59 | 2012-05-15 17:16 | 10 | 3772.333 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | LIGHTNING ARRESTER OH |  |  |  | SOURCE: Found to be a bad lightning arrestor | DISTRIBUTION | DEVICE | MANUAL | 2012-05-15 19:00 | COMPLETED |  | 2012-05-15 10:59 | 2012-05-15 17:16 | 2012-05-15 18:20 | -117.2201 | 45.3669
4W8 | 902130 | CPCC | CPCC767187 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_296501_304570126 | 2012 | Before | 2012-04-26 17:53 | 2012-04-26 18:51 | 2 | 115.167 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: bad cut out | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-04-26 21:00 | COMPLETED |  | 2012-04-26 17:53 | 2012-04-26 18:51 | 2012-04-26 18:55 | -117.2151 | 45.2712
4W8 | 896841 | CPCC | CPCC763479 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_070003_69740114 | 2012 | Before | 2012-04-02 16:16 | 2012-04-02 18:10 | 3 | 342.45 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: suspected cows rubbing on guy , blown line fuse | DISTRIBUTION | DEVICE | AUTO | 2012-04-02 19:15 | COMPLETED |  | 2012-04-02 16:16 | 2012-04-02 18:10 | 2012-04-02 18:17 | -117.2505 | 45.3965
4W8 | 908737 | CPCC | CPCC770992 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_127003_789340132 | 2012 | Before | 2012-05-24 21:40 | 2012-05-24 22:25 | 17 | 776.617 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman arrived and found open line fuse. replaced it outage restored. | DISTRIBUTION | DEVICE | AUTO | 2012-05-25 00:45 | COMPLETED |  | 2012-05-24 21:40 | 2012-05-24 22:25 | 2012-05-25 01:20 | -117.2547 | 45.3965
4W8 | 889242 | CPCC | CPCC753724 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_199704_101040273 | 2012 | Before | 2012-03-12 15:19 | 2012-03-12 16:39 | 12 | 654.267 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | CROSS ARM OH |  |  |  | SOURCE: Blown tapline fuse due to pole fire. Serviceman isolating pole fire and will get help to make repairs. | DISTRIBUTION | DEVICE | AUTO | 2012-03-12 18:30 | COMPLETED |  | 2012-03-12 15:19 | 2012-03-12 16:39 | 2012-03-12 18:05 | -117.23 | 45.3769
4W8 | 887605 | CPCC | CPCC751980 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_291108_1560078921 | 2012 | Before | 2012-03-04 03:55 | 2012-03-04 16:01 | 22 | 15980.433 | 0 | 0 | 1 | Y | N | N | N | Y | 2012-03-04 to 2012 03-04 OR Northeast | PLANNED | EMERGENCY DAMAGE REPAIR | INTERFERENCE | VEHICLE ACCIDENT | POLE OH |  |  |  | SOURCE: opened for down pole. part of outage # 751977 | DISTRIBUTION | DEVICE | MANUAL | 2012-03-04 17:00 | COMPLETED |  | 2012-03-04 03:55 | 2012-03-08 13:44 | 2012-03-04 16:05 | -117.2268 | 45.3544
4W8 | 897321 | CPCC | CPCC764082 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_210104_1560038602 | 2012 | Before | 2012-04-05 02:55 | 2012-04-05 05:20 | 333 | 48235.05 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: nothing found will test from RC 4W43 | DISTRIBUTION | DEVICE | AUTO | 2012-04-05 07:15 | COMPLETED |  | 2012-04-05 04:15 | 2012-04-05 05:20 | 2012-04-05 05:25 | -117.2064 | 45.28
4W8 | 897322 | CPCC | CPCC764083 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_042000_1560102488 | 2012 | Before | 2012-04-05 04:59 | 2012-04-05 05:20 | 21 | 436.8 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: opened RC to safely close SL's, beyond nothing was found and will test from RC | DISTRIBUTION | DEVICE | AUTO | 2012-04-05 08:00 | COMPLETED |  | 2012-04-05 04:59 | 2012-04-05 05:20 | 2012-04-05 05:25 | -117.2031 | 45.3238
4W8 | 897412 | CPCC | CPCC764124 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_298707_304570100 | 2012 | Before | 2012-04-05 07:41 | 2012-04-05 09:54 | 39 | 5179.85 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | TREES | TREE - NON-PREVENTABLE | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Associate to outage# 764104. Serviceman took outage on the tapline fuses at pole# 298707 to make repairs to the overhead primary that was taken down by a snow covered limbs. | DISTRIBUTION | DEVICE | AUTO | 2012-04-05 10:45 | COMPLETED |  | 2012-04-05 07:41 | 2012-04-05 10:54 | 2012-04-05 13:25 | -117.2107 | 45.2748
4W8 | 907859 | CPCC | CPCC770558 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_177701_101040318 | 2012 | Before | 2012-05-21 13:12 | 2012-05-21 14:07 | 1 | 55.633 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: serviceman found blown fuse on bank, which also blew line fuse at pole 170900, refused both fuses, customers back in service | DISTRIBUTION | CUSTOMER | AUTO | 2012-05-21 16:15 | COMPLETED |  | 2012-05-21 13:12 | 2012-06-06 13:25 | 2012-05-21 18:30 | -117.2149 | 45.3929
4W8 | 915873 | CPCC | CPCC774735 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_057901_69740153 | 2012 | Before | 2012-06-21 19:11 | 2012-06-21 20:15 | 1 | 64.433 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD SUSPECTED, NO MORTALITY |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: bid suspected caused outage | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-06-21 22:15 | COMPLETED |  | 2012-06-21 19:11 | 2012-06-21 20:15 | 2012-06-21 20:27 | -117.2145 | 45.4262
4W8 | 918222 | CPCC | CPCC775938 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_177701_101040318 | 2012 | Before | 2012-06-30 08:58 | 2012-06-30 10:01 | 1 | 63.067 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman reports blown cut out, caused by bird, replace fuse, it held power restored | DISTRIBUTION | CUSTOMER | AUTO | 2012-06-30 12:00 | COMPLETED |  | 2012-06-30 08:58 | 2012-06-30 10:01 | 2012-06-30 16:36 | -117.2149 | 45.3929
4W8 | 927851 | CPCC | CPCC781332 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_127003_789340132 | 2012 | Before | 2012-07-28 12:24 | 2012-07-28 14:41 | 14 | 1909.367 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: refuse line fuse no cause found | DISTRIBUTION | DEVICE | AUTO | 2012-07-28 16:15 | COMPLETED |  | 2012-07-28 13:10 | 2012-08-01 13:41 | 2012-07-28 14:45 | -117.2547 | 45.3965
4W8 | 922997 | CPCC | CPCC778834 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_270101_163440166 | 2012 | Before | 2012-07-13 20:48 | 2012-07-13 21:58 | 1 | 70.15 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: replaced transformer fuse | DISTRIBUTION | CUSTOMER | AUTO | 2012-07-14 | COMPLETED |  | 2012-07-13 20:48 | 2012-07-13 21:58 | 2012-07-13 22:31 | -117.1873 | 45.3547
4W8 | 930468 | CPCC | CPCC783018 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_302502_933390306 | 2012 | Before | 2012-08-06 08:50 | 2012-08-06 10:09 | 14 | 1104.367 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: serviceman ptrolled the line and found no issues, refused the cutouts and customers are back in service | DISTRIBUTION | DEVICE | AUTO | 2012-08-06 12:00 | COMPLETED |  | 2012-08-06 08:50 | 2012-08-06 10:09 | 2012-08-06 10:37 | -117.2458 | 45.3599
4W8 | 910793 | CPCC | CPCC771949 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_170900_101040327 | 2012 | Before | 2012-06-02 19:54 | 2012-06-02 20:42 | 4 | 195 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: blown line fuse no cause found | DISTRIBUTION | DEVICE | AUTO | 2012-06-02 23:00 | COMPLETED |  | 2012-06-02 19:54 | 2012-06-02 20:42 | 2012-06-02 20:45 | -117.2298 | 45.3951
4W8 | 915629 | CPCC | CPCC774586 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_057901_69740153 | 2012 | Before | 2012-06-20 18:06 | 2012-06-20 19:11 | 1 | 64.9 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman enroute will not have service upon arrival will call when finished. replaced transformer fuse | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-06-20 21:15 | COMPLETED |  | 2012-06-20 18:06 | 2012-06-26 13:18 | 2012-06-21 00:21 | -117.2145 | 45.4262
4W8 | 915209 | CPCC | CPCC774371 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_057901_69740153 | 2012 | Before | 2012-06-19 08:22 | 2012-06-19 09:06 | 1 | 44.433 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman refused transformer# 057901 and it held, the cause is unknown, pump is back in full service. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-06-19 11:30 | COMPLETED |  | 2012-06-19 08:22 | 2012-06-19 09:06 | 2012-06-19 10:01 | -117.2145 | 45.4262
4W8 | 925063 | CPCC | CPCC780087 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_248300_852830213 | 2012 | Before | 2012-07-19 10:36 | 2012-07-19 11:08 | 2 | 65.467 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman refused transformer# 248300 and it held, the cause was a starling, customers are back in full service. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-07-19 13:45 | COMPLETED |  | 2012-07-19 10:36 | 2012-07-19 11:08 | 2012-07-19 11:21 | -117.2531 | 45.3726
4W8 | 913068 | CPCC | CPCC773309 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_309504_933390282 | 2012 | Before | 2012-06-10 07:21 | 2012-06-10 08:41 | 6 | 484.8 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | LIGHTNING ARRESTER OH |  |  |  | SOURCE: Serviceman was able to cut arrestor in the clear and restore power. | DISTRIBUTION | DEVICE | AUTO | 2012-06-10 10:30 | COMPLETED |  | 2012-06-10 07:21 | 2012-06-10 08:41 | 2012-06-10 18:05 | -117.2311 | 45.3594
4W8 | 925477 | CPCC | CPCC780405 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_169904_1560029374 | 2012 | Before | 2012-07-20 11:57 | 2012-07-20 12:35 | 2 | 77.867 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman refused the tapline fuse at pole# 169904 and it held, the cause is unknown. | DISTRIBUTION | DEVICE | AUTO | 2012-07-20 15:00 | COMPLETED |  | 2012-07-20 11:57 | 2012-07-20 12:35 | 2012-07-20 13:51 | -117.1886 | 45.3956
4W8 | 930115 | CPCC | CPCC782444 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_172801_101040323 | 2012 | Before | 2012-08-05 13:07 | 2012-08-05 13:28 | 1 | 20.3 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown transformer fuse, cause unknown. Refused and customer is back on. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2012-08-05 13:07 | 2012-08-05 13:28 | 2012-08-05 13:55 | -117.2243 | 45.3935
4W8 | 917771 | CPCC | CPCC775766 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | EPS_CB4W8 | 2012 | Before | 2012-06-28 16:03 | 2012-06-28 16:03 | 0 | 0 | 1447 | 241.167 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: T&R Unknown | DISTRIBUTION | DEVICE | AUTO | 2012-06-28 19:15 | COMPLETED |  | 2012-06-28 16:03 | 2012-06-28 17:17 | 2012-06-28 17:22 | -117.2825 | 45.4181
4W8 | 1092981 | CPCC | CPCC783808 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_110900_69740201 | 2012 | Before | 2012-08-10 11:35 | 2012-08-10 12:56 | 5 | 406.25 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman refused the tapline fuse at pole# 110900 and it held, the cause is unknown, customers are back in full service. | DISTRIBUTION | DEVICE | AUTO | 2012-08-10 14:45 | COMPLETED |  | 2012-08-10 11:35 | 2012-08-10 12:56 | 2012-08-10 13:30 | -117.1672 | 45.4102
4W8 | 1302655 | CPCC | CPCC785002 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_220500_101040204 | 2012 | Before | 2012-08-19 05:32 | 2012-08-19 16:31 | 14 | 5160.057 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | SOURCE: Serviceman arrived, and patrolling line Serviceman found B/O xfrmr and isolated it will need 2 man crew to replace. Restored power to remaining customers. PROSPER: added in reststage from 785026 | DISTRIBUTION | DEVICE | AUTO | 2012-08-19 10:15 | COMPLETED |  | 2012-08-19 07:11 | 2012-08-27 10:45 | 2012-08-19 18:50 | -117.1873 | 45.3744
4W8 | 1307989 | CPCC | CPCC787348 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_011300_633620116 | 2012 | Before | 2012-09-10 11:27 | 2012-09-10 12:28 | 15 | 923 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | OTHER, KNOWN CAUSE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Foreman states that when he remove the elbow from the standoff, the arc jumped across to the dust cover ground wire, will head back to refuse the cutout. | DISTRIBUTION | DEVICE | AUTO | 2012-09-10 14:30 | COMPLETED |  | 2012-09-10 11:27 | 2012-09-10 12:28 | 2012-09-10 13:52 | -117.2684 | 45.4159
4W8 | 1307836 | CPCC | CPCC787296 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_021200_1560040275 | 2012 | Before | 2012-09-09 21:19 | 2012-09-09 21:58 | 1 | 39.233 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman found blown xfmr fuse, but no cause. refused & restored power | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-09-10 00:30 | COMPLETED |  | 2012-09-09 21:19 | 2012-09-09 21:58 | 2012-09-09 23:55 | -117.1647 | 45.4149
4W8 | 1304511 | CPCC | CPCC785926 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_299502_304570153 | 2012 | Before | 2012-08-26 18:48 | 2012-08-26 19:57 | 1 | 68.95 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Swerviceman found blown xfrmr fuse, no cause found, refused and power restored. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-08-26 22:00 | COMPLETED |  | 2012-08-26 18:48 | 2012-08-26 19:57 | 2012-08-27 05:45 | -117.2084 | 45.2716
4W8 | 1304323 | CPCC | CPCC785856 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_010501_69740193 | 2012 | Before | 2012-08-26 10:47 | 2012-08-26 11:41 | 1 | 53.283 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: replaced transformer fuse | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-08-26 14:00 | COMPLETED |  | 2012-08-26 10:47 | 2012-08-26 11:41 | 2012-08-26 11:45 | -117.1426 | 45.42
4W8 | 1329725 | CPCC | CPCC803086 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_290601_933390408 | 2012 | Before | 2012-12-05 10:39 | 2012-12-05 11:26 | 1 | 47.167 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown x-fmr fuse due to sparrow. Serviceman replace fuse. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-12-05 13:45 | COMPLETED |  | 2012-12-05 10:39 | 2012-12-05 11:26 | 2012-12-05 11:41 | -117.2284 | 45.3613
4W8 | 1315754 | CPCC | CPCC792854 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_055001_69740107 | 2012 | Before | 2012-10-16 11:38 | 2012-10-16 12:39 | 161 | 6560.833 | 0 | 0 | 2 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman patrolled the overhead and did not find a cause, customers are back in full service. | DISTRIBUTION | DEVICE | AUTO | 2012-10-16 14:45 | COMPLETED |  | 2012-10-16 11:40 | 2012-10-18 10:54 | 2012-10-16 12:51 | -117.2181 | 45.4112
4W8 | 1328793 | CPCC | CPCC802481 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_054701_69740434 | 2012 | Before | 2012-12-02 08:00 | 2012-12-02 18:01 | 57 | 22327.05 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE | WEATHER | RAIN | POLE OH |  |  |  | SOURCE: Serviceman found pole top burned off at 330600. Serviceman had to open recloser 4W40 to isolate jumpers @ 330500. Repairs complete. See also associated outage 802635 | DISTRIBUTION | DEVICE | MANUAL | 2012-12-02 18:00 | COMPLETED |  | 2012-12-02 08:00 | 2012-12-02 18:01 | 2012-12-02 18:11 | -117.2196 | 45.4226
4W8 | 1329361 | CPCC | CPCC802913 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_042000_1560102488 | 2012 | Before | 2012-12-04 06:35 | 2012-12-04 07:01 | 99 | 2615.25 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | TREES | TREE - NON-PREVENTABLE | PLANNED OUTAGE |  |  |  | SOURCE: Crew took outage to make repairs on outage 802866 | DISTRIBUTION | DEVICE | AUTO | 2012-12-04 09:45 | COMPLETED |  | 2012-12-04 06:35 | 2012-12-06 14:48 | 2012-12-04 07:07 | -117.2031 | 45.3238
4W8 | 1329362 | CPCC | CPCC802866 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_210104_1560038602 | 2012 | Before | 2012-12-04 04:32 | 2012-12-04 07:01 | 255 | 38024.75 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Tree in line, wire down , crew made repairs | DISTRIBUTION | DEVICE | MANUAL | 2012-12-04 09:00 | COMPLETED |  | 2012-12-04 04:32 | 2012-12-04 07:01 | 2012-12-04 07:07 | -117.2064 | 45.28
4W8 | 1329409 | CPCC | CPCC802876 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_110401_69740202 | 2012 | Before | 2012-12-04 05:29 | 2012-12-04 08:01 | 1 | 151.817 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman onsite making repairs to the overhead secondary service that was taken down by a tree. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-12-04 08:30 | COMPLETED |  | 2012-12-04 05:29 | 2012-12-04 08:01 | 2012-12-04 09:36 | -117.166 | 45.404
4W8 | 1330583 | CPCC | CPCC803473 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_298707_304570100 | 2012 | Before | 2012-12-09 10:03 | 2012-12-09 15:40 | 22 | 5637.831 | 0 | 0 | 2 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | SNOW, SLEET AND BLIZZARD | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman reports tree through the line, wire down, crew removed trees repaired down line power restored | DISTRIBUTION | DEVICE | MANUAL | 2012-12-09 17:00 | COMPLETED |  | 2012-12-09 10:03 | 2012-12-12 09:30 | 2012-12-09 15:56 | -117.2107 | 45.2748
4W8 | 1315730 | CPCC | CPCC792797 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_320907_997300258 | 2012 | Before | 2012-10-16 08:37 | 2012-10-16 10:04 | 7 | 609.933 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | SOURCE: Crew needed to change out a B/O transformer on pole# 320907. | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2012-10-16 13:00 | COMPLETED |  | 2012-10-16 08:37 | 2012-10-16 10:45 | 2012-10-16 11:47 | -117.2292 | 45.3519
4W8 | 1316436 | CPCC | CPCC793262 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_172801_101040323 | 2012 | Before | 2012-10-18 08:59 | 2012-10-18 12:39 | 1 | 219.933 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: serviceman refused the cutout, customers are back in service | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-10-18 12:00 | COMPLETED |  | 2012-10-18 08:59 | 2012-10-18 12:39 | 2012-10-18 13:15 | -117.2243 | 45.3935
4W8 | 1317181 | CPCC | CPCC793765 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_200703_101040260 | 2012 | Before | 2012-10-22 08:42 | 2012-10-22 10:33 | 1 | 111.65 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman found open x-fmr fuse. He is investigating cause. No cause found. Serviceman refused cut-out. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-10-22 11:45 | COMPLETED |  | 2012-10-22 08:42 | 2012-10-22 10:33 | 2012-10-22 11:51 | -117.2288 | 45.3768
4W8 | 1328792 | CPCC | CPCC802635 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_054701_69740434 | 2012 | Before | 2012-12-02 17:36 | 2012-12-02 18:01 | 27 | 669.6 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | POLE FIRE | POLE OH |  |  |  | SOURCE: Serviceman had to open recloser 4W40 to land jumpers @ 330500 after pole fire repair from outage #802481. Jumpers landed, recloser closed, power restored | DISTRIBUTION | DEVICE | AUTO | 2012-12-02 20:45 | COMPLETED |  | 2012-12-02 17:36 | 2012-12-02 18:01 | 2012-12-02 18:11 | -117.2196 | 45.4226
4W8 | 1318709 | CPCC | CPCC794685 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_299720_304570069 | 2012 | Before | 2012-10-27 09:19 | 2012-10-27 10:41 | 1 | 82.383 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | OTHER UTILITY/CONTRACTOR | TREES | TREE - NON-PREVENTABLE | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman enroute. Wrong serviceman shown on standby. Serviceman repaired down service & restored power | DISTRIBUTION | CUSTOMER | AUTO | 2012-10-27 12:30 | COMPLETED |  | 2012-10-27 09:19 | 2012-10-27 10:50 | 2012-10-27 11:25 | -117.2099 | 45.2752
4W8 | 1312124 | CPCC | CPCC789673 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_237500_852830222 | 2012 | Before | 2012-09-30 10:16 | 2012-09-30 11:40 | 1 | 84.217 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown fuse, no cause found, re-fused and held, power restored | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-09-30 13:30 | COMPLETED |  | 2012-09-30 10:16 | 2012-10-01 10:55 | 2012-09-30 14:17 | -117.2763 | 45.375
4W8 | 1325942 | CPCC | CPCC799567 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_170900_101040327 | 2012 | Before | 2012-11-20 05:12 | 2012-11-20 12:17 | 13 | 5521.967 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Crew needed to make repairs to the overhead primary that was taken down by a tree. | DISTRIBUTION | DEVICE | AUTO | 2012-11-20 08:15 | COMPLETED |  | 2012-11-20 05:12 | 2012-11-20 12:17 | 2012-11-20 18:37 | -117.2298 | 45.3951
4W8 | 1325978 | CPCC | CPCC799952 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | Line Cut-69230 | 2012 | Before | 2012-11-20 13:17 | 2012-11-20 17:42 | 13 | 3439.15 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | POLE FIRE | POLE OH |  |  |  | SOURCE: Servicemen opened the jumper at pole# 321521 to isolate a pole that caught fire, crew will need to replace the pole. | DISTRIBUTION | DEVICE | AUTO | 2012-11-20 16:30 | COMPLETED |  | 2012-11-20 13:17 | 2012-11-26 14:17 | 2012-11-20 18:52 | -117.2254 | 45.3456
4W8 | 1326342 | CPCC | CPCC800296 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_296901_304570000 | 2012 | Before | 2012-11-21 15:08 | 2012-11-21 17:20 | 7 | 923.883 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: B/O cut-out. Serviceman to get help tp replace cut-out. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-11-21 18:15 | COMPLETED |  | 2012-11-21 15:08 | 2012-11-21 17:20 | 2012-11-21 17:30 | -117.2146 | 45.2774
4W8 | 1325382 | CPCC | CPCC799513 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | Line Cut-69010 | 2012 | Before | 2012-11-19 20:51 | 2012-11-19 23:32 | 1449 | 232975.05 | 0 | 0 | 1 | Y | N | N | N | Y | 11-19-2012 to 11-19-2012 OR Northeast | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Loss of Transmission | DISTRIBUTION | DEVICE | AUTO | 2012-11-20 01:30 | COMPLETED |  | 2012-11-19 22:30 | 2012-11-19 23:58 | 2012-11-20 00:04 | -117.2825 | 45.4181
4W8 | 1313191 | CPCC | CPCC790537 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_240404_163440214 | 2012 | Before | 2012-10-05 08:14 | 2012-10-05 08:51 | 1 | 37.167 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman refused transformer# 240404 and it held, the cause was a starling, customer is back in full service. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-10-05 11:15 | COMPLETED |  | 2012-10-05 08:14 | 2012-10-05 08:51 | 2012-10-05 10:25 | -117.1445 | 45.3736
4W8 | 1325450 | CPCC | CPCC799547 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_118900_750140204 | 2012 | Before | 2012-11-20 01:38 | 2012-11-20 01:41 | 0 | 0 | 14 | 35.05 | 2 | Y | N | N | N | N |  | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman isolated Line down and closed line fuses in. | DISTRIBUTION | DEVICE | AUTO | 2012-11-20 04:45 | COMPLETED |  | 2012-11-20 01:38 | 2012-11-20 01:41 | 2012-11-20 02:51 | -117.2748 | 45.4105
4W8 | 1325467 | CPCC | CPCC799533 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_030004_69740156 | 2012 | Before | 2012-11-20 00:01 | 2012-11-20 03:22 | 21 | 4213.293 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Wire down due to wind popped pin out and broke cross arm. | DISTRIBUTION | DEVICE | AUTO | 2012-11-20 03:00 | COMPLETED |  | 2012-11-20 00:01 | 2012-11-26 13:59 | 2012-11-20 03:30 | -117.1872 | 45.4116
4W8 | 1325691 | CPCC | CPCC799745 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_127003_789340132 | 2012 | Before | 2012-11-20 09:17 | 2012-11-20 10:24 | 14 | 930.767 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | B/O EQUIPMENT | INSULATOR OH |  |  |  | SOURCE: Serviceman took outage on the tapline fuses at pole# 127003 to replace a B/O deadend bell. | DISTRIBUTION | DEVICE | AUTO | 2012-11-20 12:30 | COMPLETED |  | 2012-11-20 09:17 | 2012-11-20 11:24 | 2012-11-20 11:25 | -117.2547 | 45.3965
4W8 | 1325204 | CPCC | CPCC799258 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | Line Cut-68977 | 2012 | Before | 2012-11-19 18:11 | 2012-11-19 20:13 | 37 | 4499.2 | 0 | 0 | 1 | Y | N | N | N | Y | 11-19-2012 to 11-19-2012 OR Northeast | EQUIPMENT FAILURE | B/O EQUIPMENT | WEATHER | WIND | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: Serviceman found broken 'B' phase jumper on load side of recloser. Opened recloser to isolate. Need crew to repair. Crew assigned and on the way | DISTRIBUTION | DEVICE | AUTO | 2012-11-19 21:30 | COMPLETED |  | 2012-11-19 18:17 | 2012-11-19 20:13 | 2012-11-19 22:55 | -117.2196 | 45.4226
4W8 | 1325050 | CPCC | CPCC798305 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_100901_69740172 | 2012 | Before | 2012-11-19 11:05 | 2012-11-19 11:17 | 101 | 1185.067 | 0 | 0 | 1 | Y | N | N | N | Y | 11-19-2012 to 11-19-2012 OR Northeast | PLANNED | INTENTIONAL TO CLEAR TROUBLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: serviceman complete, customers are back in service | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-11-19 11:05 | 2012-11-19 11:17 | 2012-11-19 22:12 | -117.1887 | 45.4107
4W8 | 1325231 | CPCC | CPCC799297 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_054701_69740434 | 2012 | Before | 2012-11-19 18:47 | 2012-11-19 20:13 | 20 | 1708 | 0 | 0 | 1 | Y | N | N | N | Y | 11-19-2012 to 11-19-2012 OR Northeast | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: crew opened the reclosure to repair jumper on ls of reclosure | DISTRIBUTION | DEVICE | AUTO | 2012-11-19 22:00 | COMPLETED |  | 2012-11-19 18:47 | 2012-11-19 20:13 | 2012-11-19 22:59 | -117.2196 | 45.4226
4W8 | 1325929 | CPCC | CPCC799739 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_138101_852830230 | 2012 | Before | 2012-11-20 08:55 | 2012-11-20 13:52 | 1 | 296.967 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: serviceman repaired the secondary conductor, customers are back in service | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-11-20 12:00 | COMPLETED |  | 2012-11-20 08:55 | 2012-11-26 14:11 | 2012-11-20 18:36 | -117.2532 | 45.3847
4W8 | 1325468 | CPCC | CPCC799551 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_030004_69740156 | 2012 | Before | 2012-11-20 02:22 | 2012-11-20 03:22 | 19 | 1132.717 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Associated to outage 799533. Took emergency outage. | DISTRIBUTION | DEVICE | AUTO | 2012-11-20 05:30 | COMPLETED |  | 2012-11-20 02:22 | 2012-11-20 03:22 | 2012-11-20 03:30 | -117.1872 | 45.4116
4W8 | 1340527 | CPCC | CPCC816939 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_307407_933390288 | 2013 | Before | 2013-01-14 18:16 | 2013-01-14 18:50 | 2 | 67.667 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman was already on site, called by enterprise GF. Found blown xfmr fuse , no cause, Refused & restored. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-01-14 21:30 | COMPLETED |  | 2013-01-14 18:17 | 2013-01-14 18:58 | 2013-01-14 20:51 | -117.2345 | 45.3593
4W8 | 1339529 | CPCC | CPCC816291 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_298707_304570100 | 2013 | Before | 2013-01-10 01:09 | 2013-01-10 04:42 | 21 | 3832.45 | 0 | 0 | 2 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman found blown 'A' phase fuse @ 298707 with single phase line down on Wilderness Rd (Tree through line). Called 2 more men (enroute). Repaired line between 295702 & 703 & restored power. | DISTRIBUTION | DEVICE | MANUAL | 2013-01-10 05:15 | COMPLETED |  | 2013-01-10 01:09 | 2013-01-10 04:42 | 2013-01-10 04:45 | -117.2107 | 45.2748
4W8 | 1345990 | CPCC | CPCC819864 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_127003_789340132 | 2013 | Before | 2013-02-14 06:07 | 2013-02-14 06:47 | 14 | 567 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman found blown 'B' phase fuse @ 127003. No cause | DISTRIBUTION | DEVICE | AUTO | 2013-02-14 09:30 | COMPLETED |  | 2013-02-14 06:17 | 2013-02-14 06:47 | 2013-02-14 08:45 | -117.2547 | 45.3965
4W8 | 1333855 | CPCC | CPCC807917 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_298707_304570100 | 2012 | Before | 2012-12-20 03:12 | 2012-12-20 07:25 | 21 | 5312.65 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: crew complete, customers are back in service | DISTRIBUTION | DEVICE | AUTO | 2012-12-20 06:15 | COMPLETED |  | 2012-12-20 03:12 | 2012-12-20 07:25 | 2012-12-20 07:41 | -117.2107 | 45.2748
4W8 | 1345376 | CPCC | CPCC819572 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_220500_101040204 | 2013 | Before | 2013-02-10 05:36 | 2013-02-10 07:21 | 38 | 3971.633 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: broken cut out, crew to make repairs. Cutout replaced power restored. | DISTRIBUTION | DEVICE | AUTO | 2013-02-10 09:15 | COMPLETED |  | 2013-02-10 06:06 | 2013-02-10 07:21 | 2013-02-10 09:55 | -117.1873 | 45.3744
4W8 | 1340024 | CPCC | CPCC816594 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | EPS_CB4W8 | 2013 | Before | 2013-01-12 05:32 | 2013-01-12 06:55 | 1451 | 112133 | 0 | 0 | 3 | Y | N | N | Y | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CIRCUIT BREAKER SUB |  |  |  | SOURCE: CB 4W8 is locked open. CB failed to close, bypassed CB 4W8 to pick up customers. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2013-01-12 05:45 | 2013-01-12 06:58 | 2013-01-12 07:04 | -117.2825 | 45.4181
4W8 | 1351773 | CPCC | CPCC823886 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_118501_789340121 | 2013 | Before | 2013-03-18 14:33 | 2013-03-18 15:06 | 1 | 33.517 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman refused transformer# 118501 and it held, the cause is unknown, customer is back in full service. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-03-18 17:45 | COMPLETED |  | 2013-03-18 14:33 | 2013-03-18 15:06 | 2013-03-18 15:25 | -117.2755 | 45.4037
4W8 | 1348014 | CPCC | CPCC821517 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_127003_789340132 | 2013 | Before | 2013-02-27 04:45 | 2013-02-27 05:30 | 14 | 638.167 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (PROTECTED SPECIES) (BMTS) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman found blown line fuse, no cause PROSPER: crane/heron - bmts 9540 | DISTRIBUTION | DEVICE | AUTO | 2013-02-27 07:45 | COMPLETED |  | 2013-02-27 04:45 | 2013-03-20 11:26 | 2013-02-27 06:15 | -117.2547 | 45.3965
4W8 | 1350288 | CPCC | CPCC823043 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_200701_1560039959 | 2013 | Before | 2013-03-10 16:14 | 2013-03-10 17:07 | 15 | 799.75 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman arrived and found 2 blown line fuses. Patrolled the line anmd found no cause, closed on test and they held. | DISTRIBUTION | DEVICE | AUTO | 2013-03-10 19:15 | COMPLETED |  | 2013-03-10 16:14 | 2013-03-10 17:07 | 2013-03-10 18:45 | -117.2296 | 45.3778
4W8 | 1348639 | CPCC | CPCC822150 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_330600_579890067 | 2013 | Before | 2013-03-03 06:12 | 2013-03-03 13:20 | 26 | 11134.067 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | POLE OH |  |  |  | SOURCE: Serviceman arrived and found open line fuse, will patrol and report. Pole top burnt out on pole 059900, called crew in from out of dist. to make repairs | DISTRIBUTION | DEVICE | MANUAL | 2013-03-03 15:15 | COMPLETED |  | 2013-03-03 06:12 | 2013-03-03 13:20 | 2013-03-03 13:25 | -117.2092 | 45.4353
4W8 | 1348640 | CPCC | CPCC822152 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_330600_579890067 | 2013 | Before | 2013-03-03 07:12 | 2013-03-03 13:20 | 4 | 1473.267 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | POLE FIRE | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: opened other 2 fuses so repairs could be made at pole 059900 | DISTRIBUTION | DEVICE | MANUAL | 2013-03-03 15:15 | COMPLETED |  | 2013-03-03 07:12 | 2013-03-06 15:33 | 2013-03-03 13:26 | -117.2092 | 45.4353
4W8 | 1364865 | CPCC | CPCC832604 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_191508_101040301 | 2013 | Before | 2013-05-13 17:03 | 2013-05-13 19:35 | 18 | 2728.206 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE | WEATHER | LIGHTNING | INSULATOR OH |  |  |  | SOURCE: may be able to reframe pole blown line fuse PROSPER: Added 1 customer from CPCC832615. | DISTRIBUTION | DEVICE | AUTO | 2013-05-13 20:45 | COMPLETED |  | 2013-05-13 17:37 | 2013-05-14 08:48 | 2013-05-13 21:16 | -117.248 | 45.3746
4W8 | 1363981 | CPCC | CPCC831936 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_124401_69740186 | 2013 | Before | 2013-05-10 08:51 | 2013-05-10 09:15 | 1 | 24.467 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman reports open fuse on transformer, re- fused and it held, power restored | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-05-10 12:00 | COMPLETED |  | 2013-05-10 08:51 | 2013-05-10 10:31 | 2013-05-10 10:35 | -117.1359 | 45.4024
4W8 | 1365934 | CPCC | CPCC833034 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_247900_852830189 | 2013 | Before | 2013-05-17 20:28 | 2013-05-17 22:02 | 13 | 1217.233 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: found expired cat at pole | DISTRIBUTION | DEVICE | AUTO | 2013-05-17 23:30 | COMPLETED |  | 2013-05-17 20:28 | 2013-05-17 22:02 | 2013-05-17 22:06 | -117.2563 | 45.3817
4W8 | 1357662 | CPCC | CPCC827155 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_330600_579890067 | 2013 | Before | 2013-04-13 13:28 | 2013-04-13 13:54 | 26 | 676.433 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: serviceman refused the cutot and customers are back in service | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2013-04-13 13:28 | 2013-04-13 13:54 | 2013-04-13 14:20 | -117.2092 | 45.4353
4W8 | 1355506 | CPCC | CPCC826094 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_020204_69740113 | 2013 | Before | 2013-04-04 20:51 | 2013-04-05 00:30 | 6 | 1312.3 | 0 | 0 | 1 | Y | N | N | N | Y | 2013-04-04 to 2013-04-04 OR Northeast | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: Broken jumper on line fuse. Also found broken jumper on dip fuse. Crew on site to repair. | DISTRIBUTION | DEVICE | MANUAL | 2013-04-05 03:00 | COMPLETED |  | 2013-04-04 20:51 | 2013-04-05 00:34 | 2013-04-05 03:10 | -117.1671 | 45.4156
4W8 | 1364867 | CPCC | CPCC832607 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_219800_101040178 | 2013 | Before | 2013-05-13 17:44 | 2013-05-13 20:26 | 3 | 485.267 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | INSULATOR OH |  |  |  | SOURCE: broken pin insulator, wire laying on the ground, will make repairs and re-energize the line. Repairs made. | DISTRIBUTION | DEVICE | AUTO | 2013-05-13 20:45 | COMPLETED |  | 2013-05-13 17:44 | 2013-05-13 20:26 | 2013-05-13 21:16 | -117.1882 | 45.3791
4W8 | 1364448 | CPCC | CPCC832406 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_203900_101040722 | 2013 | Before | 2013-05-12 15:41 | 2013-05-12 17:35 | 1 | 113.817 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Bad order cutout and connectors. Replaced and customer is back on | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-05-12 18:45 | COMPLETED |  | 2013-05-12 15:41 | 2013-05-12 17:35 | 2013-05-12 17:45 | -117.2222 | 45.3812
4W8 | 1357160 | CPCC | CPCC826896 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_297802_1560098189 | 2013 | Before | 2013-04-10 13:16 | 2013-04-10 17:47 | 3 | 812.05 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Per GF the district is in training and will not be able to head to this call till 1630. | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2013-04-10 17:30 | COMPLETED |  | 2013-04-10 13:16 | 2013-04-10 17:47 | 2013-04-10 17:50 | -117.2125 | 45.2765
4W8 | 1364864 | CPCC | CPCC832614 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_191508_101040301 | 2013 | Before | 2013-05-13 18:25 | 2013-05-13 19:35 | 74 | 5181.233 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: crew needed to open the last two cutouts to make repairs to primary conductor wire | DISTRIBUTION | DEVICE | AUTO | 2013-05-13 21:30 | COMPLETED |  | 2013-05-13 18:25 | 2013-05-13 19:35 | 2013-05-13 21:16 | -117.248 | 45.3746
4W8 | 1358116 | CPCC | CPCC827633 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_197800_101040299 | 2013 | Before | 2013-04-15 14:25 | 2013-04-15 16:18 | 1 | 112.767 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Broken xfmr cut-out. Crew to replace. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-04-15 17:30 | COMPLETED |  | 2013-04-15 14:25 | 2013-04-15 16:18 | 2013-04-15 18:10 | -117.2349 | 45.3784
4W8 | 1355429 | CPCC | CPCC825946 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_210104_1560038602 | 2013 | Before | 2013-04-04 12:02 | 2013-04-04 16:54 | 334 | 44875.067 | 0 | 0 | 3 | Y | N | N | N | Y | 2013-04-04 to 2013-04-04 OR Northeast | TREES | TREE - NON-PREVENTABLE |  |  | POLE OH |  |  |  | SOURCE: Crew needed to replace a pole that was damaged by a tree that fell thru the overhead primary. Pole ok, broken xarm | DISTRIBUTION | DEVICE | MANUAL | 2013-04-04 19:00 | COMPLETED |  | 2013-04-04 12:07 | 2013-04-04 16:54 | 2013-04-04 17:05 | -117.2064 | 45.28
4W8 | 1375138 | CPCC | CPCC838449 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | Line Cut-75949 | 2013 | Before | 2013-06-24 21:01 | 2013-06-24 22:15 | 1457 | 107648.017 | 0 | 0 | 1 | Y | N | N | N | Y | 06/24/2013 to 06/24/2013 OR Northeast | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | OTHER SUB (EXPLAIN IN COMMENTS) |  |  |  | SOURCE: Loss of Transmission (3W86 open to lockout at Hurricane). Broken High side insulator to T-999 at Enterprise the cause. | DISTRIBUTION | DEVICE | AUTO | 2013-06-25 00:30 | COMPLETED |  | 2013-06-24 21:18 | 2013-06-26 09:06 | 2013-06-25 02:25 | -117.2825 | 45.4181
4W8 | 1371280 | CPCC | CPCC836386 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_071000_69740144 | 2013 | Before | 2013-06-10 06:57 | 2013-06-10 07:38 | 3 | 123.2 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD SUSPECTED, NO MORTALITY |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman reports open c/o on pole 071000, no cause found , suspect starling, re-fused and it held, power restored | DISTRIBUTION | DEVICE | AUTO | 2013-06-10 10:00 | COMPLETED |  | 2013-06-10 06:57 | 2013-06-11 11:04 | 2013-06-10 10:20 | -117.248 | 45.3965
4W8 | 1374666 | CPCC | CPCC838173 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_197800_101040299 | 2013 | Before | 2013-06-23 07:27 | 2013-06-23 08:39 | 1 | 72.033 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (PROTECTED SPECIES) (BMTS) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman found magpie on xfrmr caused blown fuse, refused and it held. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-06-23 10:30 | COMPLETED |  | 2013-06-23 07:27 | 2013-06-23 08:39 | 2013-06-23 08:55 | -117.2349 | 45.3784
4W8 | 1364641 | CPCC | CPCC832474 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_219504_101040192 | 2013 | Before | 2013-05-13 10:03 | 2013-05-13 10:55 | 1 | 52.35 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | DEAD END B/O OH |  |  |  | SOURCE: Fuse blown due to porimary wire down (cause was b/o deadend). Crew made repairs. | DISTRIBUTION | DEVICE | MANUAL | 2013-05-13 13:00 | COMPLETED |  | 2013-05-13 10:03 | 2013-05-13 10:55 | 2013-05-13 13:21 | -117.1885 | 45.3744
4W8 | 1355177 | CPCC | CPCC825829 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_054900_69740133 | 2013 | Before | 2013-04-03 14:25 | 2013-04-03 18:28 | 3 | 729 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | SOURCE: Serviceman reports a B/O transformer. He will call for crew. Correct FP 054603, completed & restored | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2013-04-03 18:30 | COMPLETED |  | 2013-04-03 14:25 | 2013-04-03 18:28 | 2013-04-03 18:35 | -117.2205 | 45.4259
4W8 | 1359204 | CPCC | CPCC828385 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_200701_1560039959 | 2013 | Before | 2013-04-21 07:18 | 2013-04-21 08:20 | 15 | 937.5 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman found center & south phase fuses blown @ 200701, no cause. Refused & restored. | DISTRIBUTION | DEVICE | AUTO | 2013-04-21 10:30 | COMPLETED |  | 2013-04-21 07:18 | 2013-04-21 08:31 | 2013-04-21 10:35 | -117.2296 | 45.3778
4W8 | 1374439 | CPCC | CPCC837903 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_029304_1560033467 | 2013 | Before | 2013-06-21 12:55 | 2013-06-21 14:25 | 1 | 89.733 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (PROTECTED SPECIES) (BMTS) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman refused transformer# 029304 and it held, the cause was a magpie, customer is back in full service. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-06-21 16:00 | COMPLETED |  | 2013-06-21 12:55 | 2013-06-21 14:25 | 2013-06-21 15:45 | -117.2744 | 45.414
4W8 | 1353139 | CPCC | CPCC824727 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_302502_933390306 | 2013 | Before | 2013-03-25 07:11 | 2013-03-25 08:23 | 5 | 360.167 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: B/O cutout, crew to made repairs, power restored | DISTRIBUTION | DEVICE | AUTO | 2013-03-25 10:15 | COMPLETED |  | 2013-03-25 07:11 | 2013-03-25 08:23 | 2013-03-25 08:31 | -117.2458 | 45.3599
4W8 | 1360592 | CPCC | CPCC829165 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_319902_1560048102 | 2013 | Before | 2013-04-28 08:34 | 2013-04-28 09:30 | 1 | 55.833 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman found Car-v-pole. Hit guy wire (no damage to pole or guy) & pulled service apart. Serviceman to make repairs. Serviceman made repairs to service & restored power. | DISTRIBUTION | CUSTOMER | AUTO | 2013-04-28 11:45 | COMPLETED |  | 2013-04-28 08:34 | 2013-04-28 09:43 | 2013-04-28 11:35 | -117.2305 | 45.3516
4W8 | 1388728 | CPCC | CPCC844935 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_010000_633620106 | 2013 | Before | 2013-08-05 20:11 | 2013-08-05 21:17 | 2 | 133 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown transformer fuse, cause unknown. Refused and customers are back on. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-08-05 23:15 | COMPLETED |  | 2013-08-05 20:11 | 2013-08-05 21:17 | 2013-08-06 06:02 | -117.27 | 45.4116
4W8 | 1382887 | CPCC | CPCC842301 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_198100_101040290 | 2013 | Before | 2013-07-17 07:41 | 2013-07-17 08:26 | 1 | 44.833 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman reports blown fuse on transformer, tested good, re-fused and it held power restored, no cause found | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-07-17 10:45 | COMPLETED |  | 2013-07-17 07:41 | 2013-07-17 08:26 | 2013-07-17 10:05 | -117.2313 | 45.3688
4W8 | 1388788 | CPCC | CPCC845051 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_186700_101040165 | 2013 | Before | 2013-08-06 08:21 | 2013-08-06 10:23 | 1 | 122.017 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Servicemen will replace the B/O cutout on pole# 186700 at a later time, customer will need to provide better access across irrigation ditches before we can change out the cutout. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-08-06 11:30 | COMPLETED |  | 2013-08-06 08:21 | 2013-08-06 10:23 | 2013-08-06 10:32 | -117.2377 | 45.3926
4W8 | 1383088 | CPCC | CPCC842309 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_028500_673650162 | 2013 | Before | 2013-07-17 08:21 | 2013-07-17 08:23 | 0 | 0 | 321 | 642 | 1 | Y | N | N | N | N |  | OPERATIONAL | PACIFICORP EMPLOYEE - FIELD |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman setting up a hold inadvertently opened recloser, closed it and it held, power restored | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2013-07-17 08:21 | 2013-07-17 08:37 | 2013-07-17 16:25 | -117.2749 | 45.4191
4W8 | 1393119 | CPCC | CPCC846328 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_297606_304570118 | 2013 | Before | 2013-08-12 10:16 | 2013-08-12 11:34 | 1 | 77.517 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown x-fmr fuse, no cause found, Serviceman replaced fuse and it held. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-08-12 13:30 | COMPLETED |  | 2013-08-12 10:16 | 2013-08-12 11:34 | 2013-08-12 11:42 | -117.2137 | 45.2742
4W8 | 1393769 | CPCC | CPCC846599 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_123001_789340134 | 2013 | Before | 2013-08-14 12:56 | 2013-08-14 14:02 | 2 | 133.233 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman found an open transformer fuse, he will investigate. Serviceman found no cause, he has replaced fuse and power is restored. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2013-08-14 12:56 | 2013-08-14 14:02 | 2013-08-14 14:11 | -117.2636 | 45.3963
4W8 | 1383411 | CPCC | CPCC842440 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_210104_1560038602 | 2013 | Before | 2013-07-18 11:32 | 2013-07-18 13:40 | 178 | 22775.1 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Fed Ex Truck Snagged Overhead Telephone line that was low and attached to PPL Pole, causing Over head Primary conductor to break, no Perp. Information, crew to make repairs, also see outage 842446 for emergency repairs PROSPER: Added 1 customer from CPCC842442. | DISTRIBUTION | DEVICE | MANUAL | 2013-07-18 16:00 | COMPLETED |  | 2013-07-18 11:46 | 2013-07-19 10:35 | 2013-07-18 15:05 | -117.2064 | 45.28
4W8 | 1386107 | CPCC | CPCC843830 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_039600_1560030181 | 2013 | Before | 2013-07-27 23:23 | 2013-07-28 04:46 | 5 | 1614.667 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman helping with transmission outage. Will go after serviceman found ug dip pole fuse blown. animal remain on arrestor / cutout (could not tell what though) refused and holding. | DISTRIBUTION | DEVICE | AUTO | 2013-07-28 02:30 | COMPLETED |  | 2013-07-27 23:23 | 2013-07-28 04:46 | 2013-07-28 05:01 | -117.1672 | 45.4206
4W8 | 1400156 | CPCC | CPCC851653 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_137601_1560045617 | 2013 | Before | 2013-09-05 07:36 | 2013-09-05 08:26 | 2 | 99.9 | 0 | 0 | 1 | Y | N | N | N | Y | 2013-09-05 to 2013-09-05 OR Northeast | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman refused the tapline fuse at pole# 137601 and it held, the cause is unknown, customers are back in full service. | DISTRIBUTION | DEVICE | AUTO | 2013-09-05 10:45 | COMPLETED |  | 2013-09-05 07:36 | 2013-09-05 08:26 | 2013-09-05 11:19 | -117.2559 | 45.391
4W8 | 1400160 | CPCC | CPCC851673 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_118600_69740185 | 2013 | Before | 2013-09-05 09:41 | 2013-09-05 10:31 | 1 | 49.317 | 0 | 0 | 1 | Y | N | N | N | Y | 2013-09-05 to 2013-09-05 OR Northeast | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman refused the dip fuse at pole# 118600 and it held, the cause was lightning, customer is back in full service. | DISTRIBUTION | DEVICE | AUTO | 2013-09-05 12:45 | COMPLETED |  | 2013-09-05 09:41 | 2013-09-05 10:31 | 2013-09-05 11:19 | -117.15 | 45.406
4W8 | 1385971 | CPCC | CPCC843749 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_140701_163440206 | 2013 | Before | 2013-07-27 12:39 | 2013-07-27 13:17 | 1 | 37.833 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: serviceman found no cause, refused the cutout and customers are back in service | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-07-27 15:45 | COMPLETED |  | 2013-07-27 12:39 | 2013-07-29 13:56 | 2013-07-27 13:46 | -117.1654 | 45.3924
4W8 | 1383410 | CPCC | CPCC842446 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_210104_1560038602 | 2013 | Before | 2013-07-18 12:58 | 2013-07-18 13:40 | 157 | 6575.683 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | INTERFERENCE | VEHICLE ACCIDENT | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Crew took emergency outage to make repairs, do to damage caused by Vehichle accident, see outage 842447 for accident outage | DISTRIBUTION | DEVICE | MANUAL | 2013-07-18 16:00 | COMPLETED |  | 2013-07-18 12:58 | 2013-07-19 10:54 | 2013-07-18 15:05 | -117.2064 | 45.28
4W8 | 1384430 | CPCC | CPCC843012 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_172801_101040323 | 2013 | Before | 2013-07-22 11:56 | 2013-07-22 12:24 | 1 | 28.617 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman reports blown fuse on transformer, tested good, re-fused and it held power restored, no cause found | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-07-22 15:00 | COMPLETED |  | 2013-07-22 11:56 | 2013-07-22 12:24 | 2013-07-22 12:30 | -117.2243 | 45.3935
4W8 | 1384997 | CPCC | CPCC843238 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_200701_1560039959 | 2013 | Before | 2013-07-23 21:14 | 2013-07-23 23:55 | 15 | 2426.5 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD SUSPECTED, NO MORTALITY |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: 2 blown line fuses, serviceman is patrolling. Patrolled and found a bunch of geese at the end of the line. Refused andcustomers are back on. | DISTRIBUTION | DEVICE | MANUAL | 2013-07-24 01:30 | COMPLETED |  | 2013-07-23 21:14 | 2013-07-23 23:55 | 2013-07-24 00:41 | -117.2296 | 45.3778
4W8 | 1387622 | CPCC | CPCC844421 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_047701_69740163 | 2013 | Before | 2013-08-01 15:25 | 2013-08-01 16:09 | 1 | 43.533 | 0 | 0 | 1 | Y | N | N | N | Y | 2013-08-01 to 2013-08-01 OR Northeast | TREES | TREE - NON-PREVENTABLE |  |  | CONNECTOR OH |  |  |  | SOURCE: Tree on service caused connectors to fail, repairs made . power restored | DISTRIBUTION | CUSTOMER | AUTO | 2013-08-01 18:30 | COMPLETED |  | 2013-08-01 15:25 | 2013-08-01 16:09 | 2013-08-01 16:12 | -117.1923 | 45.4221
4W8 | 1404274 | CPCC | CPCC855436 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_330900_353200013 | 2013 | Before | 2013-09-16 18:50 | 2013-09-16 20:08 | 1 | 78.233 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: serviceman found a blown fuse, will investigate for cause no cause found, replaced fuse | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-09-16 22:00 | COMPLETED |  | 2013-09-16 18:50 | 2013-09-16 20:08 | 2013-09-16 20:22 | -117.2067 | 45.5284
4W8 | 1405785 | CPCC | CPCC856090 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_138100_852830231 | 2013 | Before | 2013-09-20 19:27 | 2013-09-20 20:01 | 1 | 33.917 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown transformer fuse. Refused and customer is back on. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-09-20 22:30 | COMPLETED |  | 2013-09-20 19:27 | 2013-09-20 20:01 | 2013-09-20 21:07 | -117.2545 | 45.3847
4W8 | 1408339 | CPCC | CPCC857469 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_106900_69740175 | 2013 | Before | 2013-09-28 16:50 | 2013-09-28 18:11 | 8 | 652.667 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Wind slapped phases together. Power back on. | DISTRIBUTION | DEVICE | AUTO | 2013-09-28 20:00 | COMPLETED |  | 2013-09-28 16:50 | 2013-09-28 18:11 | 2013-09-28 21:56 | -117.1738 | 45.4113
4W8 | 1408669 | CPCC | CPCC858365 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_220500_101040204 | 2013 | Before | 2013-09-29 03:40 | 2013-09-29 05:48 | 17 | 2177.7 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: serviceman on site patrolling, no cause found replaced line fuse | DISTRIBUTION | DEVICE | AUTO | 2013-09-29 06:45 | COMPLETED |  | 2013-09-29 03:40 | 2013-09-29 05:48 | 2013-09-29 06:50 | -117.1873 | 45.3744
4W8 | 1408679 | CPCC | CPCC858407 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_320911_997300261 | 2013 | Before | 2013-09-29 06:20 | 2013-09-29 07:23 | 1 | 62.75 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Removed tree from service, customer left off for repairs. | DISTRIBUTION | CUSTOMER | AUTO | 2013-09-29 09:30 | COMPLETED |  | 2013-09-29 06:20 | 2013-09-29 07:23 | 2013-09-29 07:50 | -117.2291 | 45.3506
4W8 | 1410417 | CPCC | CPCC860388 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_200703_101040260 | 2013 | Before | 2013-10-02 09:00 | 2013-10-02 09:48 | 1 | 47.833 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown x-fmr fuse due to starling. Serviceman replaced fuse and it held. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-10-02 12:00 | COMPLETED |  | 2013-10-02 09:00 | 2013-10-02 09:48 | 2013-10-02 12:31 | -117.2288 | 45.3768
4W8 | 1410810 | CPCC | CPCC860602 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_070003_69740114 | 2013 | Before | 2013-10-03 12:48 | 2013-10-03 13:39 | 3 | 152.9 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown tapline fuse, no cause found. Serviceman replaced fuse and it held. | DISTRIBUTION | DEVICE | AUTO | 2013-10-03 16:00 | COMPLETED |  | 2013-10-03 12:48 | 2013-10-03 13:39 | 2013-10-03 16:26 | -117.2505 | 45.3965
4W8 | 1403944 | CPCC | CPCC855269 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_199101_101040170 | 2013 | Before | 2013-09-16 05:20 | 2013-09-16 06:39 | 1 | 78.783 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: replaced transformer fuse | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2013-09-16 05:20 | 2013-09-16 06:39 | 2013-09-16 06:47 | -117.2301 | 45.3696
4W8 | 1408788 | CPCC | CPCC858563 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_201704_101040261 | 2013 | Before | 2013-09-29 11:28 | 2013-09-29 12:38 | 1 | 69.333 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman onsite making repairs to the overhead secondary service that is down due to a tree, primary neutral is also down and will need a crew to make repairs. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-09-29 14:30 | COMPLETED |  | 2013-09-29 11:28 | 2013-09-29 12:38 | 2013-09-29 14:06 | -117.2273 | 45.3768
4W8 | 1408832 | CPCC | CPCC858327 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_170900_101040327 | 2013 | Before | 2013-09-29 01:52 | 2013-09-29 15:35 | 13 | 10704.85 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Crew needed to make repairs to the overhead primary that was taken down by a tree. | DISTRIBUTION | DEVICE | MANUAL | 2013-09-29 17:00 | COMPLETED |  | 2013-09-29 01:52 | 2013-09-29 15:35 | 2013-09-29 15:56 | -117.2298 | 45.3951
4W8 | 1431615 | CPCC | CPCC872096 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_070003_69740114 | 2013 | Before | 2013-12-23 14:57 | 2013-12-23 19:31 | 3 | 821.05 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: patroled no cause found | DISTRIBUTION | DEVICE | MANUAL | 2013-12-23 20:00 | COMPLETED |  | 2013-12-23 14:57 | 2013-12-23 19:31 | 2013-12-23 19:34 | -117.2505 | 45.3965
4W8 | 1430408 | CPCC | CPCC871804 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_169701_1560029376 | 2013 | Before | 2013-12-19 15:02 | 2013-12-19 16:16 | 6 | 444.8 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: found B/O fuse, no cause found. refused and restored power | DISTRIBUTION | DEVICE | AUTO | 2013-12-19 18:15 | COMPLETED |  | 2013-12-19 15:02 | 2013-12-19 16:16 | 2013-12-19 16:39 | -117.1886 | 45.3928
4W8 | 1440457 | CPCC | CPCC878720 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_307407_933390288 | 2014 | Before | 2014-02-07 12:07 | 2014-02-07 12:32 | 2 | 50.767 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman refused transformer# 307407 and it held, the cause is unknown. Customers are back in full service. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-02-07 15:15 | COMPLETED |  | 2014-02-07 12:07 | 2014-02-07 12:32 | 2014-02-07 13:38 | -117.2345 | 45.3593
4W8 | 1429140 | CPCC | CPCC871344 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_210200_579890079 | 2013 | Before | 2013-12-15 17:11 | 2013-12-15 18:48 | 2 | 193.933 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Serviceman found open fuse will patrol and close on test. Found broken cutout need 2nd man replaced cutout and restored power | DISTRIBUTION | DEVICE | AUTO | 2013-12-15 20:15 | COMPLETED |  | 2013-12-15 17:11 | 2013-12-15 18:48 | 2013-12-15 18:53 | -117.2083 | 45.4601
4W8 | 1446233 | CPCC | CPCC886628 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_170900_101040327 | 2014 | Before | 2014-02-24 09:32 | 2014-02-24 10:05 | 7 | 229.95 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman reports blown fuse on Pole 170900, patrolled Line, found no cause, refused and it | DISTRIBUTION | DEVICE | AUTO | 2014-02-24 12:45 | COMPLETED |  | 2014-02-24 09:32 | 2014-02-24 10:05 | 2014-02-24 10:33 | -117.2298 | 45.3951
4W8 | 1432865 | CPCC | CPCC872654 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_240404_163440214 | 2013 | Before | 2013-12-31 15:44 | 2013-12-31 16:28 | 1 | 43.9 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Found open xfmr fuse due to starling. Serviceman replaced fuse and it held. PROSPER: Changed Direct Cause from Animals. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-12-31 18:45 | COMPLETED |  | 2013-12-31 15:44 | 2014-01-06 15:12 | 2013-12-31 16:34 | -117.1445 | 45.3736
4W8 | 1445919 | CPCC | CPCC886482 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_169701_1560029376 | 2014 | Before | 2014-02-21 17:38 | 2014-02-21 18:37 | 9 | 537.3 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: 2 blown line fuses responder patrolling | DISTRIBUTION | DEVICE | AUTO | 2014-02-21 20:45 | COMPLETED |  | 2014-02-21 17:38 | 2014-02-21 18:38 | 2014-02-21 18:39 | -117.1886 | 45.3928
4W8 | 1453351 | CPCC | CPCC891151 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_048200_69740166 | 2014 | Before | 2014-03-26 14:32 | 2014-03-26 19:06 | 1 | 274.183 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | SOURCE: Serviceman is enroute, about an hour and a half away. Blown line fuse, serviceman check all wire is up. Refused and fuse blew again. Customer said we could come back tomorrow to check. | DISTRIBUTION | CUSTOMER | MANUAL | 2014-03-26 20:15 | COMPLETED |  | 2014-03-26 14:32 | 2014-03-26 19:06 | 2014-03-26 21:49 | -117.1909 | 45.4151
4W8 | 1464673 | CPCC | CPCC896651 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | Line Cut-85436 | 2014 | Before | 2014-05-08 11:04 | 2014-05-08 14:51 | 363 | 82449.4 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | POLE FIRE | POLE OH |  |  |  | SOURCE: Crew took outage to replace a pole that caught fire. | DISTRIBUTION | DEVICE | MANUAL | 2014-05-08 17:00 | COMPLETED |  | 2014-05-08 11:04 | 2014-05-08 14:52 | 2014-05-08 15:08 | -117.2219 | 45.3368
4W8 | 1455686 | CPCC | CPCC892222 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_290011_1560038357 | 2014 | Before | 2014-04-06 14:22 | 2014-04-06 14:55 | 1 | 33.35 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: Serviceman found bad order connector at weatherhead. Will replace & restore | DISTRIBUTION | CUSTOMER | AUTO | 2014-04-06 17:30 | COMPLETED |  | 2014-04-06 14:22 | 2014-04-06 14:55 | 2014-04-06 15:18 | -117.2287 | 45.3525
4W8 | 1451192 | CPCC | CPCC889995 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | Line Cut-84113 | 2014 | Before | 2014-03-17 13:34 | 2014-03-17 15:03 | 2 | 178.433 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Tree fell through primary. Crew to make repairs. | DISTRIBUTION | DEVICE | MANUAL | 2014-03-17 15:30 | COMPLETED |  | 2014-03-17 13:34 | 2014-03-17 15:03 | 2014-03-17 15:34 | -117.2152 | 45.2711
4W8 | 1452371 | CPCC | CPCC890455 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_309204_933390249 | 2014 | Before | 2014-03-22 09:46 | 2014-03-22 12:06 | 14 | 1959.3 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Bad order line fuse cutout. Replaced cutout and customers are back on. | DISTRIBUTION | DEVICE | AUTO | 2014-03-22 14:00 | COMPLETED |  | 2014-03-22 10:54 | 2014-03-22 12:06 | 2014-03-22 13:16 | -117.2317 | 45.3563
4W8 | 1450210 | CPCC | CPCC889174 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_118900_750140204 | 2014 | Before | 2014-03-13 07:57 | 2014-03-13 08:26 | 9 | 263.85 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD SUSPECTED, NO MORTALITY |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman found open tapline fuses at pole# 118900, patrolled , found no vause, Closed for test it held, power restored, suspect bird | DISTRIBUTION | DEVICE | MANUAL | 2014-03-13 09:57 | COMPLETED |  | 2014-03-13 07:57 | 2014-03-13 08:26 | 2014-03-13 09:29 | -117.2748 | 45.4105
4W8 | 1453534 | CPCC | CPCC891248 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_362000_1560148398 | 2014 | Before | 2014-03-27 11:59 | 2014-03-27 13:03 | 1 | 63.733 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman refused transformer# 362000 and it held, the cause was a rotted fuse, pump is back in full service. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-03-27 15:00 | COMPLETED |  | 2014-03-27 11:59 | 2014-03-27 13:03 | 2014-03-27 14:24 | -117.1401 | 45.3374
4W8 | 1465682 | CPCC | CPCC897194 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_124401_69740186 | 2014 | Before | 2014-05-12 08:51 | 2014-05-12 10:09 | 1 | 78.083 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Open x-fmr fuse, no cause found. Serviceman replaced fuse and it held. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-05-12 12:00 | COMPLETED |  | 2014-05-12 08:51 | 2014-05-12 10:09 | 2014-05-12 12:43 | -117.1359 | 45.4024
4W8 | 1465253 | CPCC | CPCC897142 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_117701_789340116 | 2014 | Before | 2014-05-11 09:56 | 2014-05-11 10:48 | 1 | 52.117 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Serviceman found burned up cutout. Serviceman to apply temp repair. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-05-11 13:00 | COMPLETED |  | 2014-05-11 09:56 | 2014-05-11 10:48 | 2014-05-11 12:08 | -117.2766 | 45.4075
4W8 | 1464997 | CPCC | CPCC896833 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | Line Cut-85468 | 2014 | Before | 2014-05-09 15:03 | 2014-05-09 15:09 | 1432 | 9689.867 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE | INTERFERENCE | OTHER INTERFERING OBJECT | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Loss of x-mission. Switched back in service at 15:09:20, cause under investigationpatroled line, found bird nest at structure 4/20 | DISTRIBUTION | DEVICE | AUTO | 2014-05-09 18:15 | COMPLETED |  | 2014-05-09 15:05 | 2014-05-13 09:38 | 2014-05-09 21:28 | -117.2825 | 45.4181
4W8 | 1461360 | CPCC | CPCC894710 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_330502_579890068 | 2014 | Before | 2014-04-25 08:47 | 2014-04-25 09:43 | 15 | 841.75 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | POLE FIRE | POLE OH |  |  |  | SOURCE: Serviceman took outage on the tapline fuses at pole# 332500 to make temp repairs to a pole that caught fire. | DISTRIBUTION | DEVICE | MANUAL | 2014-04-25 12:17 | COMPLETED |  | 2014-04-25 08:47 | 2014-04-25 09:43 | 2014-04-25 13:53 | -117.2076 | 45.4338
4W8 | 1467051 | CPCC | CPCC897852 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_274901_163440176 | 2014 | Before | 2014-05-17 10:36 | 2014-05-17 11:12 | 2 | 72.567 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: service man received call direct from customer. arrived @ 10:56 complete @ 11:00 - replaced transformer fuse | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-05-17 13:45 | COMPLETED |  | 2014-05-17 10:36 | 2014-05-17 11:18 | 2014-05-17 11:23 | -117.1776 | 45.3669
4W8 | 1462519 | CPCC | CPCC895616 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_041300_1560121840 | 2014 | Before | 2014-04-29 16:02 | 2014-04-29 17:02 | 1 | 60.083 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman found open line fuse @ 041300, no cause. Refused & restored | DISTRIBUTION | DEVICE | AUTO | 2014-04-29 19:15 | COMPLETED |  | 2014-04-29 16:02 | 2014-04-29 17:17 | 2014-04-29 18:03 | -117.2042 | 45.5049
4W8 | 1450651 | CPCC | CPCC889426 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_295402_304570079 | 2014 | Before | 2014-03-15 09:22 | 2014-03-15 09:45 | 1 | 23.183 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: serviceman states that there was a tree that fell through the line yesterday, he cut the wire down and made it safe, will repair the primary on monday, customer does not need power at this time, Ok to wait to make repairs at a later date | DISTRIBUTION | CUSTOMER | AUTO | 2014-03-15 12:30 | COMPLETED |  | 2014-03-15 09:22 | 2014-03-15 09:45 | 2014-03-15 10:08 | -117.2175 | 45.2698
4W8 | 1450608 | CPCC | CPCC889395 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_297420_304570078 | 2014 | Before | 2014-03-14 17:46 | 2014-03-14 19:10 | 22 | 1845.433 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman found blown 40T 'B' phase fuse open at 297420, 2 spans of primary down at 296501 that heat up to disconnected xfmr and feed no load at this time. Serviceman cut down & wrapped up down line, refused & restored. | DISTRIBUTION | DEVICE | AUTO | 2014-03-14 21:00 | COMPLETED |  | 2014-03-14 17:46 | 2014-03-14 19:17 | 2014-03-14 22:14 | -117.2122 | 45.271
4W8 | 1451191 | CPCC | CPCC889997 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_297420_304570078 | 2014 | Before | 2014-03-17 13:36 | 2014-03-17 15:03 | 26 | 2272.4 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | TREES | TREE - NON-PREVENTABLE | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman opened fuses to make repairs to primary that was taken down by a tree. | DISTRIBUTION | DEVICE | MANUAL | 2014-03-17 15:30 | COMPLETED |  | 2014-03-17 13:36 | 2014-03-17 15:03 | 2014-03-17 15:34 | -117.2122 | 45.271
4W8 | 1463546 | CPCC | CPCC896156 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_330502_579890068 | 2014 | Before | 2014-05-04 02:06 | 2014-05-04 03:15 | 14 | 965.767 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - TRIMMABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman found open line fuse at 330502, brush into phase. Cleared brush, refused & restored. | DISTRIBUTION | DEVICE | AUTO | 2014-05-04 05:15 | COMPLETED |  | 2014-05-04 02:06 | 2014-05-04 03:20 | 2014-05-04 04:08 | -117.2076 | 45.4338
4W8 | 1452370 | CPCC | CPCC890456 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_106900_69740175 | 2014 | Before | 2014-03-22 10:58 | 2014-03-22 12:36 | 8 | 788.4 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown line fuse, no cause found. Refused and customers are back on. | DISTRIBUTION | DEVICE | AUTO | 2014-03-22 14:00 | COMPLETED |  | 2014-03-22 10:58 | 2014-03-22 12:36 | 2014-03-22 13:16 | -117.1738 | 45.4113
4W8 | 1482537 | CPCC | CPCC906306 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_191901_101040303 | 2014 | Before | 2014-07-13 09:01 | 2014-07-13 09:52 | 1 | 50.967 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: No cause found replaced fuse and restored power. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-07-13 12:15 | COMPLETED |  | 2014-07-13 09:01 | 2014-07-13 09:52 | 2014-07-13 12:08 | -117.2472 | 45.3804
4W8 | 1480035 | CPCC | CPCC905038 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_247700_852830214 | 2014 | Before | 2014-07-05 08:22 | 2014-07-05 09:09 | 1 | 47 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: blown transformer fuses- refuse | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-07-05 11:30 | COMPLETED |  | 2014-07-05 08:22 | 2014-07-05 09:09 | 2014-07-05 09:10 | -117.2559 | 45.3782
4W8 | 1486922 | CPCC | CPCC909030 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_030004_69740156 | 2014 | Before | 2014-07-25 04:13 | 2014-07-25 04:26 | 23 | 302.45 | 0 | 0 | 1 | Y | N | N | N | N |  | OPERATIONAL | UNSAFE SITUATION |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: crew had to open the cuouts to safely install some jumpers on pole 039200 that had to be opened up to isolate a car hit pole, will install jumpers and close the cutouts back in | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2014-07-25 04:13 | 2014-07-25 04:26 | 2014-07-25 09:23 | -117.1872 | 45.4116
4W8 | 1486923 | CPCC | CPCC909015 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_030004_69740156 | 2014 | Before | 2014-07-24 21:45 | 2014-07-25 04:26 | 38 | 8750.4 | 0 | 0 | 2 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | INTERFERENCE | VEHICLE ACCIDENT | POLE OH |  |  |  | SOURCE: serviceman isolated a section of the line at pole 020203, closed the fuses and picked up a section of the outage | DISTRIBUTION | DEVICE | MANUAL | 2014-07-25 05:45 | COMPLETED |  | 2014-07-24 21:45 | 2014-07-25 04:26 | 2014-07-25 09:23 | -117.1872 | 45.4116
4W8 | 1491399 | CPCC | CPCC911663 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_169900_101040190 | 2014 | Before | 2014-08-07 12:07 | 2014-08-07 13:43 | 1 | 96 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (PROTECTED SPECIES) (BMTS) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman reports fuse blown on transformer, caused by Hawk, refused and it held, power restored | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-08-07 15:15 | COMPLETED |  | 2014-08-07 12:07 | 2014-08-07 13:43 | 2014-08-07 14:43 | -117.1894 | 45.3958
4W8 | 1494097 | CPCC | CPCC914286 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_118600_69740185 | 2014 | Before | 2014-08-15 11:50 | 2014-08-15 12:57 | 1 | 67.133 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman refused the dip pole# 118600 and it held, the cause was lightning, customer is back in full service. | DISTRIBUTION | DEVICE | AUTO | 2014-08-15 15:00 | COMPLETED |  | 2014-08-15 11:50 | 2014-08-15 12:57 | 2014-08-15 13:03 | -117.15 | 45.406
4W8 | 1486182 | CPCC | CPCC908589 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_054500_69740127 | 2014 | Before | 2014-07-23 05:43 | 2014-07-23 06:13 | 2 | 59 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman reports that the fuse was blown to the transformer on pole 054500 due to lighning. Tested and refused the cutout and customers are back in service | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-07-23 08:45 | COMPLETED |  | 2014-07-23 05:43 | 2014-07-23 06:13 | 2014-07-23 15:41 | -117.2202 | 45.4193
4W8 | 1489854 | CPCC | CPCC910972 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_027305_750140175 | 2014 | Before | 2014-08-03 02:31 | 2014-08-03 02:57 | 1081 | 28466.333 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | B/O EQUIPMENT | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: Crew opened a field recloser to make repairs to a borken jumper on pole 027408 | DISTRIBUTION | DEVICE | AUTO | 2014-08-03 05:30 | COMPLETED |  | 2014-08-03 02:31 | 2014-08-03 02:57 | 2014-08-03 03:04 | -117.2771 | 45.4161
4W8 | 1485217 | CPCC | CPCC908035 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_011501_633620113 | 2014 | Before | 2014-07-20 08:10 | 2014-07-20 09:00 | 1 | 49.75 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | OTHER UTILITY/CONTRACTOR |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Meter pole and guy pole broken with broken neutral. will make a safe condition and repair neutral and report. Temp repairs made. | DISTRIBUTION | CUSTOMER | AUTO | 2014-07-20 11:15 | COMPLETED |  | 2014-07-20 08:10 | 2014-07-20 09:00 | 2014-07-20 17:30 | -117.2695 | 45.4183
4W8 | 1492045 | CPCC | CPCC912218 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_028402_750140219 | 2014 | Before | 2014-08-10 10:34 | 2014-08-10 10:50 | 1 | 15.983 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown xfmr fuse. No cause found. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-08-10 13:45 | COMPLETED |  | 2014-08-10 10:34 | 2014-08-10 10:50 | 2014-08-10 11:08 | -117.2743 | 45.4171
4W8 | 1503202 | CPCC | CPCC919173 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_320722_997300299 | 2014 | Before | 2014-09-18 04:54 | 2014-09-18 05:27 | 1 | 33.717 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Tree came down on secondary service. It damaged the service and pulled customer's weatherhead off of the house. Serviceman to cut service in the clear so customer can make repairs. | DISTRIBUTION | CUSTOMER | AUTO | 2014-09-18 08:00 | COMPLETED |  | 2014-09-18 04:54 | 2014-09-18 05:27 | 2014-09-18 05:48 | -117.2276 | 45.3486
4W8 | 1514362 | CPCC | CPCC929171 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_201600_101040262 | 2014 | Before | 2014-11-01 10:19 | 2014-11-01 11:01 | 1 | 42.317 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: serviceman reports cause unknown, refused the cutout and customers are back in service | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-11-01 13:30 | COMPLETED |  | 2014-11-01 10:19 | 2014-11-01 11:01 | 2014-11-01 15:28 | -117.2261 | 45.3761
4W8 | 1514363 | CPCC | CPCC929176 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_028500_673650162 | 2014 | Before | 2014-11-01 11:15 | 2014-11-01 12:39 | 316 | 26570.333 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: serviceman reports the field recloser is open, patrolling for cause. serviceman reports that a tree had fallen hitting the center phase jumper causing it to lay on the arm. Was not broken just touching the cross arm, all customers are back in service | DISTRIBUTION | DEVICE | AUTO | 2014-11-01 14:15 | COMPLETED |  | 2014-11-01 11:15 | 2014-11-01 12:48 | 2014-11-01 15:28 | -117.2749 | 45.4191
4W8 | 1502282 | CPCC | CPCC918707 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_028402_750140219 | 2014 | Before | 2014-09-14 13:00 | 2014-09-14 14:51 | 1 | 110.3 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: serviceman reports that there was a blown fuse, cause unknown, refused the cutout and customers are back in service | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-09-14 16:00 | COMPLETED |  | 2014-09-14 13:00 | 2014-09-14 14:51 | 2014-09-14 17:53 | -117.2743 | 45.4171
4W8 | 1505299 | CPCC | CPCC920790 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_028500_673650162 | 2014 | Before | 2014-09-25 16:13 | 2014-09-25 16:50 | 316 | 11570.867 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (PROTECTED SPECIES) (BMTS) |  |  | LIGHTNING ARRESTER OH |  |  |  | SOURCE: Serviceman isolated the B/O lighting arrestor that was damaged by a Redtail Hawk, customers are back in full service. | DISTRIBUTION | DEVICE | AUTO | 2014-09-25 19:15 | COMPLETED |  | 2014-09-25 16:16 | 2014-09-25 16:59 | 2014-09-25 17:03 | -117.2749 | 45.4191
4W8 | 1505328 | CPCC | CPCC920800 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_200701_1560039959 | 2014 | Before | 2014-09-25 17:47 | 2014-09-25 18:33 | 17 | 782.567 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD SUSPECTED, NO MORTALITY |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman found N. Fuse on FP# 200701 Open , Patrolling line no cause found, hundreds of starlings on lines. suspect cause. | DISTRIBUTION | DEVICE | AUTO | 2014-09-25 21:00 | COMPLETED |  | 2014-09-25 17:47 | 2014-09-25 18:33 | 2014-09-25 19:38 | -117.2296 | 45.3778
4W8 | 1512274 | CPCC | CPCC926649 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_280300_353200011 | 2014 | Before | 2014-10-25 14:49 | 2014-10-25 17:11 | 1 | 142.067 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Associated with Outage ID # 926097 | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-10-25 17:45 | COMPLETED |  | 2014-10-25 14:44 | 2014-11-05 10:56 | 2014-10-26 07:34 | -117.2075 | 45.534
4W8 | 1513608 | CPCC | CPCC928691 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_169701_1560029376 | 2014 | Before | 2014-10-29 01:56 | 2014-10-29 03:44 | 8 | 857.333 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman arrived and found a fuse open, patrolled line and found bird on center phase renmoved bird and closed in fuse 0309. Line remained out do to other line outage starting after this one. | DISTRIBUTION | DEVICE | AUTO | 2014-10-29 05:00 | COMPLETED |  | 2014-10-29 01:56 | 2014-10-29 03:44 | 2014-10-29 04:53 | -117.1886 | 45.3928
4W8 | 1504616 | CPCC | CPCC919969 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_308208_933390260 | 2014 | Before | 2014-09-23 12:47 | 2014-09-23 13:06 | 24 | 456.8 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | B/O EQUIPMENT | CUT-OUT B/O OH |  |  |  | SOURCE: Crew found a bad cutout, making repairs. | DISTRIBUTION | DEVICE | MANUAL | 2014-09-23 13:30 | COMPLETED |  | 2014-09-23 12:47 | 2014-09-23 13:06 | 2014-09-23 16:23 | -117.2326 | 45.3553
4W8 | 1497149 | CPCC | CPCC915978 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_200701_1560039959 | 2014 | Before | 2014-08-26 01:33 | 2014-08-26 03:00 | 17 | 1475.033 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: patroled, no cause found | DISTRIBUTION | DEVICE | AUTO | 2014-08-26 04:45 | COMPLETED |  | 2014-08-26 01:33 | 2014-08-26 03:00 | 2014-08-26 03:04 | -117.2296 | 45.3778
4W8 | 1507497 | CPCC | CPCC921720 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_202700_101040255 | 2014 | Before | 2014-10-03 17:41 | 2014-10-04 00:50 | 8 | 3426.267 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: blown ug primary calling crew to make repairs, crew has made repairs and the customers are back in service | DISTRIBUTION | DEVICE | MANUAL | 2014-10-04 01:45 | COMPLETED |  | 2014-10-03 17:41 | 2014-10-04 00:50 | 2014-10-04 07:59 | -117.2245 | 45.3778
4W8 | 1516835 | CPCC | CPCC931272 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_170900_101040327 | 2014 | Before | 2014-11-12 04:20 | 2014-11-12 06:07 | 12 | 1287.4 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman re-fused and it held, cause unknown | DISTRIBUTION | DEVICE | AUTO | 2014-11-12 07:45 | COMPLETED |  | 2014-11-12 04:35 | 2014-11-12 06:07 | 2014-11-12 06:08 | -117.2298 | 45.3951
4W8 | 1509293 | CPCC | CPCC922907 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_100901_69740172 | 2014 | Before | 2014-10-14 03:41 | 2014-10-14 04:53 | 86 | 6146.133 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown line fuses due to tree branches. | DISTRIBUTION | DEVICE | AUTO | 2014-10-14 06:45 | COMPLETED |  | 2014-10-14 03:41 | 2014-10-14 04:53 | 2014-10-14 04:58 | -117.1887 | 45.4107
4W8 | 1496325 | CPCC | CPCC915621 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_118900_750140204 | 2014 | Before | 2014-08-23 02:14 | 2014-08-23 03:54 | 7 | 702.683 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: replaced B/O cut out | DISTRIBUTION | DEVICE | AUTO | 2014-08-23 05:15 | COMPLETED |  | 2014-08-23 02:14 | 2014-08-23 03:54 | 2014-08-23 04:03 | -117.2748 | 45.4105
4W8 | 1513583 | CPCC | CPCC928681 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_169701_1560029376 | 2014 | Before | 2014-10-28 22:10 | 2014-10-28 22:42 | 9 | 289.5 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman arrived and found open line fuse and patrolled line. Found no cause. Refused and restored power. | DISTRIBUTION | DEVICE | AUTO | 2014-10-29 01:15 | COMPLETED |  | 2014-10-28 22:10 | 2014-10-28 22:42 | 2014-10-29 00:23 | -117.1886 | 45.3928
4W8 | 1513611 | CPCC | CPCC928692 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_028500_673650162 | 2014 | Before | 2014-10-29 02:55 | 2014-10-29 03:44 | 308 | 15025.267 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman patrolling for cause. No cause found closed on test and restored power. | DISTRIBUTION | DEVICE | AUTO | 2014-10-29 06:00 | COMPLETED |  | 2014-10-29 02:55 | 2014-10-29 03:44 | 2014-10-29 06:33 | -117.2749 | 45.4191
4W8 | 1512268 | CPCC | CPCC926458 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_028500_673650162 | 2014 | Before | 2014-10-25 14:10 | 2014-10-25 14:49 | 312 | 12147.2 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman arrived and found recloser open. patrolling for cause. Serviceman found Tree on single phase, removed and restored, | DISTRIBUTION | DEVICE | AUTO | 2014-10-25 17:15 | COMPLETED |  | 2014-10-25 14:12 | 2014-10-25 14:49 | 2014-10-26 07:04 | -117.2749 | 45.4191
4W8 | 1514365 | CPCC | CPCC929197 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_055001_69740107 | 2014 | Before | 2014-11-01 12:56 | 2014-11-01 13:10 | 157 | 2245.1 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: this was a continuation of outage 929176. serviceman reported that the recloser was opened with aoriginal outage, closed the reclosure and all customers are now back in service | DISTRIBUTION | DEVICE | AUTO | 2014-11-01 16:00 | COMPLETED |  | 2014-11-01 12:56 | 2014-11-01 13:18 | 2014-11-01 15:28 | -117.2181 | 45.4112
4W8 | 1503203 | CPCC | CPCC919174 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_264600_163440184 | 2014 | Before | 2014-09-18 05:01 | 2014-09-18 06:03 | 1 | 61.567 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Tree branch fell on xfmr and blew fuse. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-09-18 08:15 | COMPLETED |  | 2014-09-18 05:01 | 2014-09-18 06:03 | 2014-09-18 06:23 | -117.1566 | 45.3619
4W8 | 1508582 | CPCC | CPCC922376 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_237500_852830222 | 2014 | Before | 2014-10-10 06:30 | 2014-10-10 07:06 | 1 | 35.567 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman found open cutout on pole # 237500; re-fused and it held. Unknown cause. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-10-10 09:30 | COMPLETED |  | 2014-10-10 06:30 | 2014-10-10 07:06 | 2014-10-10 08:13 | -117.2763 | 45.375
4W8 | 1511249 | CPCC | CPCC924150 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_210104_1560038602 | 2014 | Before | 2014-10-22 14:42 | 2014-10-22 20:28 | 87 | 4463.75 | 0 | 0 | 2 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Crew needed to make repairs to the overhead primary that was taken down by a tree. Crew enroute from Pendleton. Repairs made. | DISTRIBUTION | DEVICE | MANUAL | 2014-10-22 22:45 | COMPLETED |  | 2014-10-22 14:45 | 2014-10-22 20:29 | 2014-10-23 04:33 | -117.2064 | 45.28
4W8 | 1512303 | CPCC | CPCC926097 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_028500_673650162 | 2014 | Before | 2014-10-25 12:57 | 2014-10-25 17:56 | 316 | 11046.4 | 0 | 0 | 2 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Isolated down conductor closed in to isolated point and it held. | DISTRIBUTION | DEVICE | AUTO | 2014-10-25 16:15 | COMPLETED |  | 2014-10-25 13:02 | 2014-10-25 17:56 | 2014-10-26 07:36 | -117.2749 | 45.4191
4W8 | 1536424 | CPCC | CPCC947542 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_309300_933390198 | 2015 | Before | 2015-02-06 06:03 | 2015-02-06 16:18 | 77 | 47415.317 | 0 | 0 | 1 | Y | N | N | N | Y | 2015/02/05 OR Northeast | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | NO DISTRIBUTION DAMAGE |  |  |  |  | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2015-02-06 10:06 | 2015-02-07 07:32 | 2015-02-07 07:33 | -117.2301 | 45.3573
4W8 | 1523617 | CPCC | CPCC936718 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_042000_1560102488 | 2014 | Before | 2014-12-11 01:00 | 2014-12-11 04:00 | 349 | 62750.2 | 0 | 0 | 1 | Y | N | N | N | Y | 2014-12-11 OR Northeast | EQUIPMENT FAILURE | POLE FIRE |  |  | POLE OH |  |  |  |  | DISTRIBUTION | DEVICE | MANUAL | 2014-12-11 05:00 | COMPLETED |  | 2014-12-11 01:00 | 2014-12-11 04:02 | 2014-12-11 04:08 | -117.2031 | 45.3238
4W8 | 1537168 | CPCC | CPCC949285 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_299608_304570148 | 2015 | Before | 2015-02-08 16:47 | 2015-02-08 18:07 | 1 | 79.983 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  |  | DISTRIBUTION | CUSTOMER | AUTO |  | COMPLETED |  | 2015-02-08 16:47 | 2015-02-08 18:07 | 2015-02-08 18:09 | -117.2097 | 45.2732
4W8 | 1520853 | CPCC | CPCC934372 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_116680_69740183 | 2014 | Before | 2014-11-27 04:34 | 2014-11-27 05:28 | 1 | 53.633 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman found open fuse refused and restored power. Unknown cause. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-11-27 07:45 | COMPLETED |  | 2014-11-27 04:34 | 2014-11-27 05:28 | 2014-11-27 06:48 | -117.1538 | 45.4061
4W8 | 1522783 | CPCC | CPCC935906 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_100901_69740172 | 2014 | Before | 2014-12-07 04:34 | 2014-12-07 07:10 | 100 | 15541.667 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | POLE OH |  |  |  | SOURCE: Serviceman reports Burned out pole top at FP 219601 | DISTRIBUTION | DEVICE | AUTO | 2014-12-07 08:00 | COMPLETED |  | 2014-12-07 04:48 | 2014-12-07 07:10 | 2014-12-07 13:18 | -117.1887 | 45.4107
4W8 | 1536397 | CPCC | CPCC947908 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_010000_633620106 | 2015 | Before | 2015-02-06 15:53 | 2015-02-07 05:21 | 2 | 1615.667 | 0 | 0 | 1 | Y | N | N | N | Y | 2015/02/05 OR Northeast | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  |  | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2015-02-06 15:53 | 2015-02-07 07:19 | 2015-02-07 07:23 | -117.27 | 45.4116
4W8 | 1536426 | CPCC | CPCC947427 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_199901_101040293 | 2015 | Before | 2015-02-06 09:23 | 2015-02-06 13:02 | 1 | 219.433 | 0 | 0 | 1 | Y | N | N | N | Y | 2015/02/05 OR Northeast | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | NO DISTRIBUTION DAMAGE |  |  |  |  | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2015-02-06 09:23 | 2015-02-07 07:33 | 2015-02-07 07:38 | -117.2309 | 45.3806
4W8 | 1536896 | CPCC | CPCC948830 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_309243_933390270 | 2015 | Before | 2015-02-07 09:04 | 2015-02-07 20:12 | 2 | 1335.633 | 0 | 0 | 1 | Y | N | N | N | Y | 2015/02/05 OR Northeast | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  |  | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2015-02-07 09:04 | 2015-02-08 01:36 | 2015-02-08 01:38 | -117.2307 | 45.3561
4W8 | 1536470 | CPCC | CPCC946831 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_171905_101040326 | 2015 | Before | 2015-02-06 02:34 | 2015-02-06 05:09 | 1 | 154.367 | 0 | 0 | 1 | Y | N | N | N | Y | 2015/02/05 OR Northeast | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: unknown | DISTRIBUTION | CUSTOMER | AUTO |  | COMPLETED |  | 2015-02-06 02:35 | 2015-02-07 07:59 | 2015-02-07 08:03 | -117.227 | 45.3956
4W8 | 1536539 | CPCC | CPCC947932 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_299921_304570089 | 2015 | Before | 2015-02-06 16:28 | 2015-02-07 07:40 | 1 | 911.85 | 0 | 0 | 1 | Y | N | N | N | Y | 2015/02/05 OR Northeast | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  |  | DISTRIBUTION | CUSTOMER | AUTO |  | COMPLETED |  | 2015-02-06 16:28 | 2015-02-07 08:44 | 2015-02-07 08:48 | -117.2084 | 45.2775
4W8 | 1527748 | CPCC | CPCC941713 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_299920_304570087 | 2014 | Before | 2014-12-25 00:56 | 2014-12-25 02:19 | 12 | 991.2 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: serviceman patrolled the line and found no cause for a blown fuse on the tap line. Refused the cutout and customers are back in service | DISTRIBUTION | DEVICE | AUTO | 2014-12-25 04:00 | COMPLETED |  | 2014-12-25 00:57 | 2014-12-25 05:36 | 2014-12-25 05:38 | -117.208 | 45.2782
4W8 | 1524890 | CPCC | CPCC939529 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_298707_304570100 | 2014 | Before | 2014-12-12 19:35 | 2014-12-12 21:57 | 40 | 5670.667 | 0 | 0 | 1 | Y | N | N | N | Y | 2014-12-11 OR Northeast | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Removed tree limbs from line, re-fused and holding | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2014-12-12 19:35 | 2014-12-12 22:01 | 2014-12-12 22:03 | -117.2107 | 45.2748
4W8 | 1525633 | CPCC | CPCC939798 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_298522_304570131 | 2014 | Before | 2014-12-15 12:46 | 2014-12-15 16:29 | 1 | 222.933 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  |  | DISTRIBUTION | CUSTOMER | AUTO |  | COMPLETED |  | 2014-12-15 12:47 | 2014-12-15 16:32 | 2014-12-15 16:33 | -117.2104 | 45.2711
4W8 | 1536895 | CPCC | CPCC948954 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_290001_933390362 | 2015 | Before | 2015-02-07 13:00 | 2015-02-07 20:23 | 1 | 443.767 | 0 | 0 | 1 | Y | N | N | N | Y | 2015/02/05 OR Northeast | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  |  | DISTRIBUTION | CUSTOMER | AUTO |  | COMPLETED |  | 2015-02-07 13:00 | 2015-02-08 01:36 | 2015-02-08 01:38 | -117.2277 | 45.3529
4W8 | 1536441 | CPCC | CPCC947212 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | Line Cut-94045 | 2015 | Before | 2015-02-06 07:38 | 2015-02-07 05:00 | 1 | 1282.217 | 0 | 0 | 1 | Y | N | N | N | Y | 2015/02/05 OR Northeast | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  |  | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2015-02-06 07:38 | 2015-02-07 07:36 | 2015-02-07 07:39 | -117.2533 | 45.3745
4W8 | 1536443 | CPCC | CPCC947153 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | Line Cut-94024 | 2015 | Before | 2015-02-06 07:02 | 2015-02-07 04:58 | 4 | 5265.667 | 0 | 0 | 1 | Y | N | N | N | Y | 2015/02/05 OR Northeast | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  |  | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2015-02-06 07:02 | 2015-02-07 07:37 | 2015-02-07 07:39 | -117.2719 | 45.4174
4W8 | 1536483 | CPCC | CPCC946849 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_202680_101040257 | 2015 | Before | 2015-02-06 02:43 | 2015-02-06 05:09 | 1 | 145.8 | 0 | 0 | 1 | Y | N | N | N | Y | 2015/02/05 OR Northeast | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: unknown | DISTRIBUTION | CUSTOMER | AUTO |  | COMPLETED |  | 2015-02-06 02:43 | 2015-02-07 08:13 | 2015-02-07 08:18 | -117.2247 | 45.3761
4W8 | 1536508 | CPCC | CPCC946934 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_295600_304570113 | 2015 | Before | 2015-02-06 04:16 | 2015-02-06 05:09 | 1 | 53.3 | 0 | 0 | 1 | Y | N | N | N | Y | 2015/02/05 OR Northeast | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: unknown | DISTRIBUTION | CUSTOMER | AUTO |  | COMPLETED |  | 2015-02-06 04:16 | 2015-02-07 08:21 | 2015-02-07 08:23 | -117.2159 | 45.2738
4W8 | 1536538 | CPCC | CPCC947054 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_210104_1560029690 | 2015 | Before | 2015-02-06 05:48 | 2015-02-06 11:59 | 3 | 1111.05 | 0 | 0 | 1 | Y | N | N | N | Y | 2015/02/05 OR Northeast | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: unknown | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2015-02-06 05:48 | 2015-02-07 08:44 | 2015-02-07 08:48 | -117.2064 | 45.28
4W8 | 1528047 | CPCC | CPCC941865 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_125601_789340151 | 2014 | Before | 2014-12-27 13:04 | 2014-12-27 13:51 | 1 | 46.633 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  |  | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-12-27 16:15 | COMPLETED |  | 2014-12-27 13:05 | 2014-12-27 13:52 | 2014-12-27 13:53 | -117.2612 | 45.4063
4W8 | 1536390 | CPCC | CPCC947969 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_126480_1560030059 | 2015 | Before | 2015-02-06 17:36 | 2015-02-07 05:23 | 1 | 707.183 | 0 | 0 | 1 | Y | N | N | N | Y | 2015/02/05 OR Northeast | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  |  | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2015-02-06 17:36 | 2015-02-07 07:16 | 2015-02-07 07:18 | -117.2572 | 45.4029
4W8 | 1536531 | CPCC | CPCC947002 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_027305_750140175 | 2015 | Before | 2015-02-06 01:08 | 2015-02-07 01:37 | 1082 | 288848.5 | 0 | 0 | 2 | Y | N | N | N | Y | 2015/02/05 OR Northeast | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  |  | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2015-02-06 05:10 | 2015-02-07 08:42 | 2015-02-07 08:44 | -117.2771 | 45.4161
4W8 | 1536540 | CPCC | CPCC947947 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_299720_304570069 | 2015 | Before | 2015-02-06 16:56 | 2015-02-07 07:41 | 10 | 8855.333 | 0 | 0 | 1 | Y | N | N | N | Y | 2015/02/05 OR Northeast | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  |  | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2015-02-06 16:56 | 2015-02-07 08:44 | 2015-02-07 08:48 | -117.2099 | 45.2752
4W8 | 1521403 | CPCC | CPCC934879 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_115280_789340089 | 2014 | Before | 2014-11-30 06:08 | 2014-11-30 09:12 | 1 | 183.85 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTORS UG |  |  |  | SOURCE: servicerman reports a bad UG neutral will make repairs bad ug connector made repairs and customer back in full service | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2014-11-30 10:45 | COMPLETED |  | 2014-11-30 06:08 | 2014-11-30 09:12 | 2014-11-30 17:28 | -117.28 | 45.3996
4W8 | 1517863 | CPCC | CPCC932380 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_186380_101040311 | 2014 | Before | 2014-11-15 03:37 | 2014-11-15 05:42 | 1 | 125.083 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Bayonet fuse, deteriorated. Replaced it and restored power. | DISTRIBUTION | CUSTOMER | AUTO | 2014-11-15 06:45 | COMPLETED |  | 2014-11-15 03:37 | 2014-11-15 05:42 | 2014-11-15 06:10 | -117.2364 | 45.3865
4W8 | 1522539 | CPCC | CPCC935576 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_106900_69740175 | 2014 | Before | 2014-12-05 13:10 | 2014-12-05 15:03 | 8 | 907.333 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman reports two fuses blown, will patrol for cause (has to walk this out to patrol line). Didn't find anything. Re-fused and it held. | DISTRIBUTION | DEVICE | AUTO | 2014-12-05 16:15 | COMPLETED |  | 2014-12-05 13:10 | 2014-12-05 15:04 | 2014-12-05 15:54 | -117.1738 | 45.4113
4W8 | 1535780 | CPCC | CPCC946181 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_319806_997300390 | 2015 | Before | 2015-02-05 10:59 | 2015-02-05 13:09 | 3 | 391.4 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Serviceman replaced the B/O cutout on pole# 319806, customers are back in full service | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-02-05 14:00 | COMPLETED |  | 2015-02-05 10:59 | 2015-02-05 14:18 | 2015-02-05 14:23 | -117.2304 | 45.3502
4W8 | 1540251 | CPCC | CPCC952258 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_302502_933390306 | 2015 | Before | 2015-02-21 14:25 | 2015-02-21 16:39 | 14 | 1042.217 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | POLE OH |  |  |  | SOURCE: crew to make repairs | DISTRIBUTION | DEVICE | AUTO | 2015-02-21 17:30 | COMPLETED |  | 2015-02-21 14:26 | 2015-02-21 16:42 | 2015-02-21 16:43 | -117.2458 | 45.3599
4W8 | 1532918 | CPCC | CPCC944399 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_309204_933390249 | 2015 | Before | 2015-01-19 06:42 | 2015-01-19 07:59 | 5 | 386.167 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  |  | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2015-01-19 06:42 | 2015-01-19 08:52 | 2015-01-19 08:53 | -117.2317 | 45.3563
4W8 | 1536541 | CPCC | CPCC947998 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_280903_304570156 | 2015 | Before | 2015-02-06 21:10 | 2015-02-07 07:45 | 1 | 635.467 | 0 | 0 | 1 | Y | N | N | N | Y | 2015/02/05 OR Northeast | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  |  | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2015-02-06 21:10 | 2015-02-07 08:45 | 2015-02-07 08:48 | -117.2076 | 45.277
4W8 | 1536435 | CPCC | CPCC947306 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_248500_852830175 | 2015 | Before | 2015-02-06 08:08 | 2015-02-07 05:00 | 5 | 6261.417 | 0 | 0 | 1 | Y | N | N | N | Y | 2015/02/05 OR Northeast | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  |  | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2015-02-06 08:08 | 2015-02-07 07:35 | 2015-02-07 07:38 | -117.2533 | 45.3745
4W8 | 1536464 | CPCC | CPCC946821 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_309009_933390244 | 2015 | Before | 2015-02-06 02:30 | 2015-02-06 05:09 | 1 | 158.9 | 0 | 0 | 1 | Y | N | N | N | Y | 2015/02/05 OR Northeast | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: unknown | DISTRIBUTION | CUSTOMER | AUTO |  | COMPLETED |  | 2015-02-06 02:30 | 2015-02-07 07:57 | 2015-02-07 07:58 | -117.231 | 45.353
4W8 | 1536398 | CPCC | CPCC947903 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_027200_750140213 | 2015 | Before | 2015-02-06 15:43 | 2015-02-07 04:15 | 1 | 751.75 | 0 | 0 | 1 | Y | N | N | N | Y | 2015/02/05 OR Northeast | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  |  | DISTRIBUTION | CUSTOMER | AUTO |  | COMPLETED |  | 2015-02-06 15:43 | 2015-02-07 07:19 | 2015-02-07 07:23 | -117.277 | 45.4145
4W8 | 1536526 | CPCC | CPCC946970 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_206180_101040236 | 2015 | Before | 2015-02-06 04:48 | 2015-02-06 05:09 | 1 | 21.45 | 0 | 0 | 1 | Y | N | N | N | Y | 2015/02/05 OR Northeast | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: unknown | DISTRIBUTION | CUSTOMER | AUTO |  | COMPLETED |  | 2015-02-06 04:48 | 2015-02-07 08:38 | 2015-02-07 08:43 | -117.2179 | 45.3691
4W8 | 1536721 | CPCC | CPCC948736 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_027201_750140212 | 2015 | Before | 2015-02-07 07:38 | 2015-02-07 16:20 | 3 | 1566.25 | 0 | 0 | 1 | Y | N | N | N | Y | 2015/02/05 OR Northeast | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  |  | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2015-02-07 07:38 | 2015-02-07 16:54 | 2015-02-07 16:58 | -117.2769 | 45.4139
4W8 | 1539005 | CPCC | CPCC951513 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_186400_101040310 | 2015 | Before | 2015-02-14 06:23 | 2015-02-14 07:32 | 2 | 137.733 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  |  | DISTRIBUTION | DEVICE | AUTO | 2015-02-14 09:30 | COMPLETED |  | 2015-02-14 06:23 | 2015-02-14 07:33 | 2015-02-14 07:38 | -117.2363 | 45.3882
4W8 | 1524902 | CPCC | CPCC939332 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | Line Cut-93122 | 2014 | Before | 2014-12-12 10:44 | 2014-12-12 14:16 | 830 | 175503.5 | 0 | 0 | 1 | Y | N | N | N | Y | 2014-12-11 OR Northeast | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  |  | DISTRIBUTION | DEVICE | AUTO | 2014-12-12 13:45 | COMPLETED |  | 2014-12-12 10:44 | 2014-12-12 22:26 | 2014-12-12 22:33 | -117.2458 | 45.3608
4W8 | 1536388 | CPCC | CPCC947984 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_118900_750140204 | 2015 | Before | 2015-02-06 19:15 | 2015-02-07 05:20 | 7 | 4236.867 | 0 | 0 | 1 | Y | N | N | N | Y | 2015/02/05 OR Northeast | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: unknown | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2015-02-06 19:15 | 2015-02-07 07:16 | 2015-02-07 07:18 | -117.2748 | 45.4105
4W8 | 1536436 | CPCC | CPCC947310 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_199704_101040273 | 2015 | Before | 2015-02-06 06:20 | 2015-02-06 21:33 | 13 | 5020.65 | 0 | 0 | 2 | Y | N | N | N | Y | 2015/02/05 OR Northeast | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | NO DISTRIBUTION DAMAGE |  |  |  |  | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2015-02-06 08:09 | 2015-02-07 07:35 | 2015-02-07 07:38 | -117.23 | 45.3769
4W8 | 1536447 | CPCC | CPCC947061 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_319805_997300389 | 2015 | Before | 2015-02-06 05:51 | 2015-02-06 20:05 | 18 | 15363.3 | 0 | 0 | 1 | Y | N | N | N | Y | 2015/02/05 OR Northeast | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | NO DISTRIBUTION DAMAGE |  |  |  |  | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2015-02-06 05:52 | 2015-02-07 07:39 | 2015-02-07 07:43 | -117.2313 | 45.3506
4W8 | 1536530 | CPCC | CPCC946995 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_204680_101040252 | 2015 | Before | 2015-02-06 05:08 | 2015-02-06 05:09 | 0 | 0 | 1 | 0.833 | 1 | Y | N | N | N | Y | 2015/02/05 OR Northeast | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: unknown | DISTRIBUTION | CUSTOMER | AUTO |  | COMPLETED |  | 2015-02-06 05:09 | 2015-02-07 08:42 | 2015-02-07 08:44 | -117.2207 | 45.3761
4W8 | 1526755 | CPCC | CPCC940705 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_027305_750140175 | 2014 | Before | 2014-12-21 04:55 | 2014-12-21 06:04 | 1082 | 74135.033 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | NO DISTRIBUTION DAMAGE |  |  |  |  | DISTRIBUTION | DEVICE | AUTO | 2014-12-21 08:15 | COMPLETED |  | 2014-12-21 04:57 | 2014-12-22 10:58 | 2014-12-21 10:58 | -117.2771 | 45.4161
4W8 | 1536391 | CPCC | CPCC947963 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_264800_163440183 | 2015 | Before | 2015-02-06 17:28 | 2015-02-07 01:49 | 1 | 500.733 | 0 | 0 | 1 | Y | N | N | N | Y | 2015/02/05 OR Northeast | WEATHER | WIND |  |  | JUMPER WIRE/STIRRUP OH |  |  |  |  | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2015-02-06 17:29 | 2015-02-07 07:17 | 2015-02-07 07:18 | -117.1567 | 45.3651
4W8 | 1536407 | CPCC | CPCC947810 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_127003_789340132 | 2015 | Before | 2015-02-06 13:45 | 2015-02-06 20:04 | 14 | 5305.067 | 0 | 0 | 1 | Y | N | N | N | Y | 2015/02/05 OR Northeast | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: unknown | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2015-02-06 13:45 | 2015-02-07 07:23 | 2015-02-07 07:28 | -117.2547 | 45.3965
4W8 | 1536706 | CPCC | CPCC947055 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_210104_1560038602 | 2015 | Before | 2015-02-06 05:48 | 2015-02-07 16:16 | 325 | 161063.033 | 0 | 0 | 2 | Y | N | N | N | Y | 2015/02/05 OR Northeast | TREES | TREE - NON-PREVENTABLE |  |  | POLE OH |  |  |  |  | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2015-02-06 05:48 | 2015-02-07 16:17 | 2015-02-07 16:18 | -117.2064 | 45.28
4W8 | 1537076 | CPCC | CPCC949177 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_320600_997300312 | 2015 | Before | 2015-02-08 08:38 | 2015-02-08 09:26 | 1 | 47.833 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  |  | DISTRIBUTION | CUSTOMER | AUTO |  | COMPLETED |  | 2015-02-08 08:38 | 2015-02-08 10:39 | 2015-02-08 10:43 | -117.2285 | 45.3476
4W8 | 1548469 | CPCC | CPCC957260 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | Line Cut-95085 | 2015 | Before | 2015-03-31 11:07 | 2015-03-31 12:27 | 145 | 11513 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: Crew needed to make repairs to the B/O overhead primary jumper on FR# 4W13 | DISTRIBUTION | DEVICE | AUTO | 2015-03-31 14:15 | COMPLETED |  | 2015-03-31 11:08 | 2015-03-31 12:53 | 2015-03-31 12:53 | -117.2749 | 45.4191
4W8 | 1544987 | CPCC | CPCC954825 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_247900_852830189 | 2015 | Before | 2015-03-15 15:41 | 2015-03-15 16:46 | 13 | 851.283 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: | DISTRIBUTION | DEVICE | AUTO | 2015-03-15 19:15 | COMPLETED |  | 2015-03-15 16:11 | 2015-03-15 17:01 | 2015-03-15 17:04 | -117.2563 | 45.3817
4W8 | 1561451 | CPCC | CPCC964939 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_330600_579890067 | 2015 | Before | 2015-05-19 12:45 | 2015-05-19 14:29 | 27 | 2819.7 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (PROTECTED SPECIES) (BMTS) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman refused the tapline fuse at pole# 330600 and it held, the cause was a redtailed hawk. | DISTRIBUTION | DEVICE | AUTO | 2015-05-19 16:00 | COMPLETED |  | 2015-05-19 12:55 | 2015-05-19 16:53 | 2015-05-19 16:58 | -117.2092 | 45.4353
4W8 | 1557497 | CPCC | CPCC962922 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_121803_69740182 | 2015 | Before | 2015-05-04 08:43 | 2015-05-04 10:20 | 1 | 96.55 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman refused transformer# 121803 and it held, the cause is unknown | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2015-05-04 08:43 | 2015-05-04 14:29 | 2015-05-04 14:33 | -117.1426 | 45.4095
4W8 | 1562531 | CPCC | CPCC965692 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_220500_101040204 | 2015 | Before | 2015-05-23 19:40 | 2015-05-23 21:01 | 32 | 2585.6 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman removed tree branches from Pole # 240500 replaced fuses at Pole 220500 | DISTRIBUTION | DEVICE | AUTO | 2015-05-23 23:45 | COMPLETED |  | 2015-05-23 19:48 | 2015-05-23 21:09 | 2015-05-23 21:13 | -117.1873 | 45.3744
4W8 | 1545466 | CPCC | CPCC955148 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_306005_1080105704 | 2015 | Before | 2015-03-16 21:10 | 2015-03-16 22:56 | 1 | 105.933 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: B/O xfmr cut-out | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-03-17 00:15 | COMPLETED |  | 2015-03-16 21:10 | 2015-03-17 02:04 | 2015-03-17 02:08 | -117.2376 | 45.3529
4W8 | 1562469 | CPCC | CPCC965642 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_119081_594930027 | 2015 | Before | 2015-05-23 10:43 | 2015-05-23 13:21 | 1 | 157.883 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: serviceman found fuse open on undergroud transformer due to lightning, re- fuse and holding, customer restored | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-05-23 13:45 | COMPLETED |  | 2015-05-23 10:43 | 2015-05-23 13:22 | 2015-05-23 13:28 | -117.0224 | 45.483
4W8 | 1544909 | CPCC | CPCC954504 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_170900_101040327 | 2015 | Before | 2015-03-15 08:53 | 2015-03-15 09:32 | 12 | 469.2 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman found field side fuse open on FP 170900, Patrolled, found no cause, re-fused and holding | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2015-03-15 08:54 | 2015-03-15 09:33 | 2015-03-15 09:38 | -117.2298 | 45.3951
4W8 | 1560800 | CPCC | CPCC964619 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_297500_304570075 | 2015 | Before | 2015-05-17 07:30 | 2015-05-17 10:16 | 5 | 833.417 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: B/O cut-out on dip pole | DISTRIBUTION | DEVICE | AUTO | 2015-05-17 10:30 | COMPLETED |  | 2015-05-17 07:30 | 2015-05-17 12:41 | 2015-05-17 12:43 | -117.2137 | 45.2712
4W8 | 1544772 | CPCC | CPCC954418 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_127003_789340132 | 2015 | Before | 2015-03-14 06:25 | 2015-03-14 07:21 | 14 | 774.433 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman arrived, found blown line fuse at FP 127003, patrolling now to investigate.No cause found, replaced fuse and holding | DISTRIBUTION | DEVICE | AUTO | 2015-03-14 09:30 | COMPLETED |  | 2015-03-14 06:25 | 2015-03-14 08:34 | 2015-03-14 08:39 | -117.2547 | 45.3965
4W8 | 1559514 | CPCC | CPCC964081 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_290303_933391128 | 2015 | Before | 2015-05-12 10:28 | 2015-05-12 12:00 | 2 | 183.3 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: broken cutout | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-05-12 13:30 | COMPLETED |  | 2015-05-12 10:28 | 2015-05-12 12:56 | 2015-05-12 12:58 | -117.2293 | 45.3573
4W8 | 1545067 | CPCC | CPCC954981 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_110900_69740201 | 2015 | Before | 2015-03-15 19:49 | 2015-03-15 20:16 | 6 | 161.1 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: open fuses to repair jumper outage # 954940 | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2015-03-15 19:49 | 2015-03-15 20:18 | 2015-03-15 20:23 | -117.1672 | 45.4102
4W8 | 1546014 | CPCC | CPCC955450 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_332500_579890073 | 2015 | Before | 2015-03-19 12:55 | 2015-03-19 14:12 | 1 | 76.833 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VANDALISM OR THEFT |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman reported a stick was removed from the line. The fuses were replaced and held. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-03-19 16:00 | COMPLETED |  | 2015-03-19 12:55 | 2015-03-19 15:00 | 2015-03-19 15:03 | -117.2044 | 45.4337
4W8 | 1562442 | CPCC | CPCC965633 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_198500_101040292 | 2015 | Before | 2015-05-23 09:09 | 2015-05-23 10:05 | 1 | 56.317 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | SOURCE: Serviceman found service on ground, found 2 B/O Connectors, repaired and replaced, Customer Restored | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2015-05-23 09:09 | 2015-05-23 10:08 | 2015-05-23 10:08 | -117.2325 | 45.3743
4W8 | 1560579 | CPCC | CPCC964542 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_100901_69740172 | 2015 | Before | 2015-05-16 01:41 | 2015-05-16 05:20 | 53 | 11618.483 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman having issues with Service Truck , called out second journeyman with truck to assist. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2015-05-16 01:42 | 2015-05-16 05:23 | 2015-05-16 05:23 | -117.1887 | 45.4107
4W8 | 1545066 | CPCC | CPCC954940 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_105200_69740173 | 2015 | Before | 2015-03-15 18:04 | 2015-03-15 20:16 | 1 | 132.767 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: broken jumper with crew help will repair, Broken jumper repaired. Power Restored | DISTRIBUTION | CUSTOMER | AUTO | 2015-03-15 21:15 | COMPLETED |  | 2015-03-15 18:04 | 2015-03-15 20:18 | 2015-03-15 20:18 | -117.1779 | 45.4009
4W8 | 1548468 | CPCC | CPCC957262 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_028500_673650162 | 2015 | Before | 2015-03-31 11:24 | 2015-03-31 12:27 | 174 | 10909.8 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | B/O EQUIPMENT | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: Serviceman took outage on FR# 4W13 to make repairs to the overhead primary jumper | DISTRIBUTION | DEVICE | AUTO | 2015-03-31 14:30 | COMPLETED |  | 2015-03-31 11:24 | 2015-03-31 12:52 | 2015-03-31 12:53 | -117.2749 | 45.4191
4W8 | 1561229 | CPCC | CPCC964889 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_170900_101040327 | 2015 | Before | 2015-05-18 23:53 | 2015-05-19 01:38 | 12 | 1250.8 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman found 40T open at FP 170900, Patrolled and found no cause, Re-fused and Holding, all customers restored | DISTRIBUTION | DEVICE | AUTO | 2015-05-19 03:00 | COMPLETED |  | 2015-05-18 23:54 | 2015-05-19 01:41 | 2015-05-19 01:43 | -117.2298 | 45.3951
4W8 | 1562434 | CPCC | CPCC965621 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_174903_594930036 | 2015 | Before | 2015-05-23 06:46 | 2015-05-23 08:36 | 2 | 220.833 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman found blown fuse on FP 174803, No Cause found, Re-Fused and Holding, all customers restored | DISTRIBUTION | DEVICE | AUTO | 2015-05-23 10:00 | COMPLETED |  | 2015-05-23 06:47 | 2015-05-23 08:37 | 2015-05-23 08:38 | -117.0938 | 45.4853
4W8 | 1565515 | CPCC | CPCC967556 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_053102_69740120 | 2015 | Before | 2015-06-03 15:13 | 2015-06-03 16:51 | 1 | 98.133 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Cutout | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-06-03 18:15 | COMPLETED |  | 2015-06-03 15:13 | 2015-06-03 17:00 | 2015-06-03 17:03 | -117.2238 | 45.4123
4W8 | 1575929 | CPCC | CPCC973628 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_124401_69740186 | 2015 | Before | 2015-07-04 06:58 | 2015-07-04 07:53 | 1 | 54.233 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman replaced a blown fuse | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-07-04 10:00 | COMPLETED |  | 2015-07-04 06:59 | 2015-07-04 14:56 | 2015-07-04 14:58 | -117.136 | 45.4024
4W8 | 1581727 | CPCC | CPCC978731 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_290605_933390406 | 2015 | Before | 2015-07-20 16:49 | 2015-07-20 17:56 | 1 | 66.517 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: removed bird, replaced transformer fuse | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-07-20 20:00 | COMPLETED |  | 2015-07-20 16:50 | 2015-07-20 17:56 | 2015-07-20 17:58 | -117.2292 | 45.362
4W8 | 1578932 | CPCC | CPCC976300 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | Line Cut-96829 | 2015 | Before | 2015-07-11 13:06 | 2015-07-11 14:12 | 1452 | 95686.8 | 0 | 0 | 1 | Y | N | N | N | Y | 2015-07-11 OR Northeast | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: loss of walla walla- hells cyn 230 kv line | DISTRIBUTION | DEVICE | AUTO | 2015-07-11 16:15 | COMPLETED |  | 2015-07-11 13:07 | 2015-07-11 14:15 | 2015-07-11 14:18 | -117.2825 | 45.4181
4W8 | 1584358 | CPCC | CPCC980326 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_186700_101040165 | 2015 | Before | 2015-07-29 16:20 | 2015-07-29 17:04 | 1 | 44.217 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: serviceman reports a blown fuse, investigating for cause, serviceman reports that the outage was due to a starling, refused the cutout and customers are back in service | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-07-29 19:30 | COMPLETED |  | 2015-07-29 16:20 | 2015-07-29 17:26 | 2015-07-29 17:29 | -117.2377 | 45.3926
4W8 | 1576686 | CPCC | CPCC974031 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_247900_852830189 | 2015 | Before | 2015-07-06 06:04 | 2015-07-06 06:55 | 13 | 655.85 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: patroled, no cause found | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2015-07-06 06:04 | 2015-07-06 17:38 | 2015-07-06 17:43 | -117.2563 | 45.3817
4W8 | 1573768 | CPCC | CPCC971991 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_248300_852830213 | 2015 | Before | 2015-06-29 08:45 | 2015-06-29 09:33 | 2 | 95.467 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman refused transformer# 248300 and it held, the cause is unknown | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-06-29 11:45 | COMPLETED |  | 2015-06-29 08:46 | 2015-06-29 16:40 | 2015-06-29 16:43 | -117.2531 | 45.3726
4W8 | 1566761 | CPCC | CPCC968032 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_205004_101040240 | 2015 | Before | 2015-06-07 22:38 | 2015-06-08 02:18 | 10 | 2203.167 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Fuse blown @ term pole -- serviceman investigating -- fault indicators showed fault -- did callout for a crew -- cable tested good -- re-fused & it held | DISTRIBUTION | DEVICE | MANUAL | 2015-06-08 04:45 | COMPLETED |  | 2015-06-07 22:38 | 2015-06-08 03:49 | 2015-06-08 03:53 | -117.2201 | 45.3669
4W8 | 1583642 | CPCC | CPCC979979 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_186700_101040165 | 2015 | Before | 2015-07-27 08:31 | 2015-07-27 09:16 | 1 | 45.117 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2015-07-27 08:31 | 2015-07-27 17:05 | 2015-07-27 17:09 | -117.2377 | 45.3926
4W8 | 1580691 | CPCC | CPCC977346 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_297420_304570078 | 2015 | Before | 2015-07-16 16:04 | 2015-07-16 17:41 | 28 | 2711.333 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman replaced blown fuses due to a tree branch in the line that burnt off. | DISTRIBUTION | DEVICE | AUTO | 2015-07-16 19:15 | COMPLETED |  | 2015-07-16 16:05 | 2015-07-16 20:03 | 2015-07-16 20:04 | -117.2123 | 45.271
4W8 | 1577108 | CPCC | CPCC974498 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_127003_789340132 | 2015 | Before | 2015-07-07 10:28 | 2015-07-07 11:14 | 22 | 1007.6 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: refused and it held, no cause found | DISTRIBUTION | DEVICE | AUTO | 2015-07-07 13:30 | COMPLETED |  | 2015-07-07 10:31 | 2015-07-07 17:53 | 2015-07-07 17:53 | -117.2547 | 45.3965
4W8 | 1574244 | CPCC | CPCC972560 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_240501_163440212 | 2015 | Before | 2015-06-30 07:46 | 2015-06-30 09:50 | 1 | 124.033 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Serviceman found a broken line cutout; crew to repair | DISTRIBUTION | DEVICE | AUTO | 2015-06-30 11:00 | COMPLETED |  | 2015-06-30 07:46 | 2015-06-30 10:09 | 2015-06-30 10:13 | -117.1445 | 45.3742
4W8 | 1588218 | CPCC | CPCC983055 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_186700_101040165 | 2015 | Before | 2015-08-10 10:01 | 2015-08-10 10:45 | 1 | 44.117 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: transformer fuse | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-08-10 13:15 | COMPLETED |  | 2015-08-10 10:01 | 2015-08-10 15:22 | 2015-08-10 15:24 | -117.2377 | 45.3926
4W8 | 1572563 | CPCC | CPCC971292 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_200701_1560039959 | 2015 | Before | 2015-06-26 12:32 | 2015-06-26 13:59 | 13 | 1125.15 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD NEST (BMTS) |  |  | LIGHTNING ARRESTER OH |  |  |  | SOURCE: Serviceman removed grass and sticks from the overhead primary, refused and it held, customers are back in full service | DISTRIBUTION | DEVICE | AUTO | 2015-06-26 15:45 | COMPLETED |  | 2015-06-26 12:33 | 2015-06-26 14:01 | 2015-06-26 14:03 | -117.2296 | 45.3778
4W8 | 1601943 | CPCC | CPCC991448 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_117900_69740191 | 2015 | Before | 2015-09-30 14:01 | 2015-09-30 15:13 | 1 | 72.233 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE ONLY -UG ( NO CAUSE FOUND) |  |  |  | SOURCE: Serviceman found open dip fuse; no cause found; re-fused and it held. (meter was on wrong FP, should have been on FP 118600) | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-09-30 17:15 | COMPLETED |  | 2015-09-30 14:03 | 2015-09-30 15:16 | 2015-09-30 15:18 | -117.1513 | 45.4106
4W8 | 1611138 | CPCC | CPCC998014 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_298707_304570100 | 2015 | Before | 2015-11-09 16:01 | 2015-11-09 19:33 | 32 | 6760.7 | 0 | 0 | 2 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | SNOW, SLEET AND BLIZZARD | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: crew to make repairs, Repairs completed, all customers restored | DISTRIBUTION | DEVICE | AUTO | 2015-11-09 19:30 | COMPLETED |  | 2015-11-09 16:27 | 2015-11-17 14:29 | 2015-11-10 00:34 | -117.2107 | 45.2748
4W8 | 1602938 | CPCC | CPCC992501 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_138000_852830229 | 2015 | Before | 2015-10-04 09:48 | 2015-10-04 10:37 | 2 | 99.067 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Re-fused transformer -- no cause | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-10-04 13:00 | COMPLETED |  | 2015-10-04 09:48 | 2015-10-04 18:01 | 2015-10-04 18:03 | -117.2541 | 45.382
4W8 | 1611137 | CPCC | CPCC998025 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_298707_304570100 | 2015 | Before | 2015-11-09 18:10 | 2015-11-09 19:33 | 37 | 3075.317 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: crew deenergized to make repairs, repairs complete | DISTRIBUTION | DEVICE | AUTO | 2015-11-09 21:15 | COMPLETED |  | 2015-11-09 18:10 | 2015-11-10 00:33 | 2015-11-10 00:34 | -117.2107 | 45.2748
4W8 | 1606909 | CPCC | CPCC995568 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_202003_101040246 | 2015 | Before | 2015-10-22 05:33 | 2015-10-22 06:34 | 1 | 60.567 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman replaced a blown fuse. Unknown cause. | DISTRIBUTION | CUSTOMER | AUTO | 2015-10-22 08:45 | COMPLETED |  | 2015-10-22 05:33 | 2015-10-22 15:19 | 2015-10-22 15:24 | -117.224 | 45.3674
4W8 | 1596178 | CPCC | CPCC988108 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_330600_579890067 | 2015 | Before | 2015-09-05 18:47 | 2015-09-06 03:50 | 31 | 16834.55 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | POLE OH |  |  |  | SOURCE: Crew repaired burnt Pole# 210200 | DISTRIBUTION | DEVICE | MANUAL | 2015-09-06 06:00 | COMPLETED |  | 2015-09-05 19:20 | 2015-09-06 06:41 | 2015-09-06 06:43 | -117.2092 | 45.4353
4W8 | 1591917 | CPCC | CPCC985125 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_199000_101040275 | 2015 | Before | 2015-08-23 11:52 | 2015-08-23 12:29 | 18 | 681.6 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: serviceman reports a blown fuse, will patrol for cause,serviceman reports that he has patrolled the line and found no cause, refused the cutout and customers are back in service | DISTRIBUTION | DEVICE | AUTO | 2015-08-23 15:00 | COMPLETED |  | 2015-08-23 11:53 | 2015-08-23 14:24 | 2015-08-23 14:28 | -117.2305 | 45.3668
4W8 | 1601837 | CPCC | CPCC991402 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_200703_101040260 | 2015 | Before | 2015-09-30 07:54 | 2015-09-30 08:25 | 1 | 30.967 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman found transformer fuse blown due to a small bird (unrecognizable as it was scorched); re-fused and it held. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-09-30 11:00 | COMPLETED |  | 2015-09-30 07:54 | 2015-09-30 08:52 | 2015-09-30 08:53 | -117.2288 | 45.3768
4W8 | 1589115 | CPCC | CPCC983447 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_186700_101040165 | 2015 | Before | 2015-08-13 07:38 | 2015-08-13 08:08 | 1 | 30.333 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Re-fused transformer -- bird | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-08-13 10:45 | COMPLETED |  | 2015-08-13 07:38 | 2015-08-13 11:01 | 2015-08-13 11:03 | -117.2377 | 45.3926
4W8 | 1606173 | CPCC | CPCC995239 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_191901_101040303 | 2015 | Before | 2015-10-19 05:45 | 2015-10-19 06:36 | 1 | 51.267 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Replaced transformer fuse | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-10-19 08:45 | COMPLETED |  | 2015-10-19 05:45 | 2015-10-19 13:48 | 2015-10-19 13:49 | -117.2472 | 45.3804
4W8 | 1592488 | CPCC | CPCC985372 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_240404_163440214 | 2015 | Before | 2015-08-25 07:50 | 2015-08-25 08:35 | 1 | 44.95 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: starling | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-08-25 11:00 | COMPLETED |  | 2015-08-25 07:53 | 2015-08-25 15:22 | 2015-08-25 15:24 | -117.1445 | 45.3736
4W8 | 1618563 | CPCC | CPCC1004664 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | Line Cut-99173 | 2015 | Before | 2015-12-07 09:48 | 2015-12-07 17:07 | 13 | 5698.767 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | POLE FIRE | POLE OH |  |  |  | SOURCE: Serviceman took outage so a crew can replace a pole that caught fire | DISTRIBUTION | DEVICE | AUTO | 2015-12-07 13:00 | COMPLETED |  | 2015-12-07 09:48 | 2015-12-08 07:16 | 2015-12-08 07:19 | -117.2064 | 45.28
4W8 | 1618038 | CPCC | CPCC1004015 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_290207_933390385 | 2015 | Before | 2015-12-06 14:23 | 2015-12-06 15:59 | 1 | 96.583 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Crew repaired broken cutout and restored customers | DISTRIBUTION | CUSTOMER | AUTO |  | COMPLETED |  | 2015-12-06 14:23 | 2015-12-06 16:51 | 2015-12-06 16:54 | -117.2292 | 45.3564
4W8 | 1612080 | CPCC | CPCC998595 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_175900_101040321 | 2015 | Before | 2015-11-14 09:32 | 2015-11-14 11:29 | 2 | 233.933 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | LIGHTNING ARRESTER OH |  |  |  | SOURCE: Serviceman had two bad lightning arrestors, repaired and restored | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-11-14 14:15 | COMPLETED |  | 2015-11-14 11:14 | 2015-11-14 12:47 | 2015-11-14 12:49 | -117.2197 | 45.3952
4W8 | 1614331 | CPCC | CPCC1001155 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_202700_101040255 | 2015 | Before | 2015-11-20 07:52 | 2015-11-20 11:50 | 8 | 1904.8 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Crew needed to make repairs to the B/O underground primary | DISTRIBUTION | DEVICE | MANUAL | 2015-11-20 14:00 | COMPLETED |  | 2015-11-20 07:56 | 2015-11-20 13:27 | 2015-11-20 13:29 | -117.2245 | 45.3778
4W8 | 1618562 | CPCC | CPCC1004484 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | Line Cut-99170 | 2015 | Before | 2015-12-07 09:00 | 2015-12-07 17:07 | 11 | 5351.317 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | POLE OH |  |  |  | SOURCE: Crew needed to replace a pole that caught fire | DISTRIBUTION | DEVICE | AUTO | 2015-12-07 12:00 | COMPLETED |  | 2015-12-07 09:01 | 2015-12-08 07:16 | 2015-12-08 07:19 | -117.2064 | 45.28
4W8 | 1613776 | CPCC | CPCC1000914 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_027101_750140211 | 2015 | Before | 2015-11-18 18:28 | 2015-11-18 19:37 | 1 | 69.067 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman repaired downed service and replaced transformer fuse, all customers restored | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2015-11-18 21:45 | COMPLETED |  | 2015-11-18 18:28 | 2015-11-19 03:25 | 2015-11-19 03:28 | -117.2769 | 45.4134
4W8 | 1618254 | CPCC | CPCC1004483 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_210104_1560038602 | 2015 | Before | 2015-12-07 08:59 | 2015-12-07 11:40 | 64 | 10299.733 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | POLE OH |  |  |  | SOURCE: Serviceman refused the dip fuse at pole# 210104 and it held, the cause was fault current from a pole fire near by | DISTRIBUTION | DEVICE | AUTO | 2015-12-07 14:00 | COMPLETED |  | 2015-12-07 08:59 | 2015-12-07 12:56 | 2015-12-07 12:58 | -117.2064 | 45.28
4W8 | 1634382 | CPCC | CPCC1021883 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_100901_69740172 | 2016 | Before | 2016-01-28 11:43 | 2016-01-28 12:43 | 79 | 4791.35 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman removed a tree limb, customers are back in full service | DISTRIBUTION | DEVICE | AUTO | 2016-01-28 15:30 | COMPLETED |  | 2016-01-28 12:23 | 2016-01-28 14:27 | 2016-01-28 14:29 | -117.1887 | 45.4107
4W8 | 1614908 | CPCC | CPCC1001495 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_047701_69740163 | 2015 | Before | 2015-11-23 14:06 | 2015-11-23 15:29 | 1 | 82.983 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: B/O secondary connectors | DISTRIBUTION | CUSTOMER | AUTO | 2015-11-23 17:15 | COMPLETED |  | 2015-11-23 14:07 | 2015-11-23 16:50 | 2015-11-23 16:55 | -117.1923 | 45.4221
4W8 | 1618542 | CPCC | CPCC1005065 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | Line Cut-99189 | 2015 | Before | 2015-12-07 21:49 | 2015-12-07 23:18 | 7 | 622.3 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | INSULATOR OH |  |  |  | SOURCE: Service man de-energized line @ FP# 320721 -- need crew assist to relace insulator -- pole fire out & pole OK | DISTRIBUTION | DEVICE | AUTO | 2015-12-08 01:00 | COMPLETED |  | 2015-12-07 21:50 | 2015-12-08 07:06 | 2015-12-08 07:09 | -117.2285 | 45.3486
4W8 | 1652469 | CPCC | CPCC1036508 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_030004_69740156 | 2016 | Before | 2016-04-10 12:43 | 2016-04-10 14:54 | 21 | 2760.45 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Crew repaired broken cut out at F/P 030004 | DISTRIBUTION | DEVICE | AUTO | 2016-04-10 17:15 | COMPLETED |  | 2016-04-10 12:43 | 2016-04-10 19:15 | 2016-04-10 19:17 | -117.1872 | 45.4116
4W8 | 1644748 | CPCC | CPCC1030514 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_309010_933390220 | 2016 | Before | 2016-03-10 00:26 | 2016-03-10 08:14 | 13 | 6090.5 | 54 | 229.5 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | POLE OH |  |  |  | SOURCE: Blown line fuse due to a pole fire. Serviceman to issolate pole and refuse line. | DISTRIBUTION | DEVICE | AUTO | 2016-03-10 03:30 | COMPLETED |  | 2016-03-10 00:26 | 2016-03-10 09:07 | 2016-03-10 09:12 | -117.231 | 45.3524
4W8 | 1644522 | CPCC | CPCC1029542 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_299921_304570089 | 2016 | Before | 2016-03-09 12:06 | 2016-03-09 13:01 | 3 | 164.85 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: B/O cutout | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2016-03-09 12:37 | 2016-03-09 16:14 | 2016-03-09 16:16 | -117.2084 | 45.2775
4W8 | 1646924 | CPCC | CPCC1033064 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_264600_163440184 | 2016 | Before | 2016-03-18 05:43 | 2016-03-18 06:35 | 1 | 51.55 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: Serviceman found blown lightning arrestor at FP# 264600. Serviceman found burnt open jumper on transformer. Replaced and customer is back on. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2016-03-18 06:34 | 2016-03-18 07:05 | 2016-03-18 07:08 | -117.1567 | 45.3619
4W8 | 1656365 | CPCC | CPCC1042100 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_309300_933390198 | 2016 | Before | 2016-04-23 14:32 | 2016-04-23 16:17 | 103 | 10876.8 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | INSULATOR OH |  |  |  | SOURCE: glass tracked across | DISTRIBUTION | DEVICE | AUTO | 2016-04-23 17:45 | COMPLETED |  | 2016-04-23 14:45 | 2016-04-23 17:27 | 2016-04-23 17:28 | -117.2301 | 45.3573
4W8 | 1644229 | CPCC | CPCC1029396 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_200701_1560039959 | 2016 | Before | 2016-03-08 12:03 | 2016-03-08 12:59 | 16 | 881.067 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman refused the tapline fuses and they held, the cause is unknown | DISTRIBUTION | DEVICE | AUTO | 2016-03-08 15:15 | COMPLETED |  | 2016-03-08 12:08 | 2016-03-08 13:41 | 2016-03-08 13:42 | -117.2296 | 45.3778
4W8 | 1655259 | CPCC | CPCC1041317 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_340500_579890071 | 2016 | Before | 2016-04-19 17:34 | 2016-04-19 18:48 | 1 | 74.033 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | LIGHTNING ARRESTER OH |  |  |  | SOURCE: Serviceman disconnected the bad lightening arrestor and replaced blown fuse on the transformer | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2016-04-19 20:45 | COMPLETED |  | 2016-04-19 17:34 | 2016-04-19 20:37 | 2016-04-19 20:38 | -117.1872 | 45.4335
4W8 | 1672041 | CPCC | CPCC1049843 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_027305_750140175 | 2016 | Before | 2016-06-08 17:00 | 2016-06-08 17:40 | 1079 | 43142.017 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | RECLOSER-NORMAL OPERATION OH (NO CAUSE FOUND) |  |  |  | SOURCE: patrolled; no cause found; tried on test; hot and holding; | DISTRIBUTION | DEVICE | AUTO | 2016-06-08 20:15 | COMPLETED |  | 2016-06-08 17:04 | 2016-06-08 20:38 | 2016-06-08 20:43 | -117.2771 | 45.4161
4W8 | 1670313 | CPCC | CPCC1048167 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_304601_933390317 | 2016 | Before | 2016-06-04 12:15 | 2016-06-04 12:56 | 1 | 40.45 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Re-fused transformer -- no cause | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2016-06-04 15:15 | COMPLETED |  | 2016-06-04 12:16 | 2016-06-04 12:57 | 2016-06-04 12:57 | -117.2403 | 45.3609
4W8 | 1675363 | CPCC | CPCC1052025 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_295600_304570113 | 2016 | Before | 2016-06-19 13:21 | 2016-06-19 14:08 | 1 | 46.933 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman replaced a blown transformer fuse | DISTRIBUTION | CUSTOMER | AUTO | 2016-06-19 16:30 | COMPLETED |  | 2016-06-19 13:21 | 2016-06-19 23:57 | 2016-06-19 23:57 | -117.2159 | 45.2738
4W8 | 1661498 | CPCC | CPCC1043795 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_227802_101040209 | 2016 | Before | 2016-05-05 20:59 | 2016-05-05 22:11 | 2 | 143.433 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: refused transformer, lightning caused. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2016-05-06 | COMPLETED |  | 2016-05-05 20:59 | 2016-05-06 01:14 | 2016-05-06 01:18 | -117.1734 | 45.3793
4W8 | 1661500 | CPCC | CPCC1043794 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_264600_163440184 | 2016 | Before | 2016-05-05 20:56 | 2016-05-05 22:50 | 1 | 114.483 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: tap line fuse blown, lightning. refused and holding. no damages | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2016-05-06 | COMPLETED |  | 2016-05-05 20:56 | 2016-05-06 01:14 | 2016-05-06 01:18 | -117.1567 | 45.3619
4W8 | 1661506 | CPCC | CPCC1043799 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_191600_101040166 | 2016 | Before | 2016-05-05 22:47 | 2016-05-06 00:37 | 1 | 109.35 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | WEATHER | LIGHTNING | CUT-OUT B/O OH |  |  |  | SOURCE: | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2016-05-06 02:00 | COMPLETED |  | 2016-05-05 22:50 | 2016-05-06 01:16 | 2016-05-06 01:18 | -117.2468 | 45.3772
4W8 | 1664944 | CPCC | CPCC1045440 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_308242_933390255 | 2016 | Before | 2016-05-15 08:55 | 2016-05-15 09:41 | 1 | 45.633 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: serviceman found squirrel below open fuse at FP 308242 - refused and back in service | DISTRIBUTION | CUSTOMER | AUTO | 2016-05-15 12:00 | COMPLETED |  | 2016-05-15 08:55 | 2016-05-15 18:41 | 2016-05-15 18:43 | -117.2324 | 45.3561
4W8 | 1661503 | CPCC | CPCC1043801 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_191508_101040301 | 2016 | Before | 2016-05-05 23:23 | 2016-05-06 00:36 | 15 | 1085.817 | 0 | 0 | 3 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: center phase cutout broken. hit by lightning. crew will open other cutouts to allow safe replacment of cutout. | DISTRIBUTION | DEVICE | AUTO | 2016-05-06 02:30 | COMPLETED |  | 2016-05-05 23:24 | 2016-05-06 01:15 | 2016-05-06 01:18 | -117.248 | 45.3746
4W8 | 1673986 | CPCC | CPCC1051045 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_162200_101040182 | 2016 | Before | 2016-06-14 20:32 | 2016-06-14 21:02 | 1 | 29.717 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | LIGHTNING ARRESTER OH |  |  |  | SOURCE: Serviceman replaced transformer fuse blown due to lightning arrestor failure, restored all customers | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2016-06-14 20:33 | 2016-06-15 02:08 | 2016-06-15 02:08 | -117.2043 | 45.3851
4W8 | 1659322 | CPCC | CPCC1043017 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_118900_750140204 | 2016 | Before | 2016-05-02 08:30 | 2016-05-02 08:56 | 3 | 77.95 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (PROTECTED SPECIES) (BMTS) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: serviceman reports found dead goose, refused at FP118900 same outage as 1043012 | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2016-05-02 08:30 | 2016-05-02 09:40 | 2016-05-02 09:42 | -117.2749 | 45.4105
4W8 | 1662732 | CPCC | CPCC1044448 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_210104_1560038602 | 2016 | Before | 2016-05-09 12:52 | 2016-05-09 14:50 | 321 | 37979.65 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Junctions blown -- serviceman investigating report of line down Serviceman reports tree limb at FP 299821 brought down lines down | DISTRIBUTION | DEVICE | AUTO | 2016-05-09 16:15 | COMPLETED |  | 2016-05-09 12:52 | 2016-05-09 14:55 | 2016-05-09 14:58 | -117.2064 | 45.28
4W8 | 1659321 | CPCC | CPCC1043012 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_125601_789340151 | 2016 | Before | 2016-05-02 08:14 | 2016-05-02 08:57 | 1 | 43 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (PROTECTED SPECIES) (BMTS) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: serviceman reports found dead goose, refused at FP118900 same outage as 1043017 | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2016-05-02 11:15 | COMPLETED |  | 2016-05-02 08:14 | 2016-05-02 09:40 | 2016-05-02 09:42 | -117.2612 | 45.4063
4W8 | 1680726 | CPCC | CPCC1055055 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_127003_789340132 | 2016 | Before | 2016-07-07 05:28 | 2016-07-07 06:12 | 13 | 575.9 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman found open fuse, patrolled and found no cause, refused and holding, all customers restored | DISTRIBUTION | DEVICE | AUTO | 2016-07-07 08:30 | COMPLETED |  | 2016-07-07 05:28 | 2016-07-07 06:16 | 2016-07-07 06:18 | -117.2547 | 45.3965
4W8 | 1679841 | CPCC | CPCC1054515 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_111202_69740204 | 2016 | Before | 2016-07-04 09:22 | 2016-07-04 10:28 | 1 | 66.083 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman replaced a blown transformer fuse | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2016-07-04 12:30 | COMPLETED |  | 2016-07-04 09:22 | 2016-07-04 17:18 | 2016-07-04 17:23 | -117.1641 | 45.3999
4W8 | 1661502 | CPCC | CPCC1043805 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_199704_101040273 | 2016 | Before | 2016-05-05 23:52 | 2016-05-06 00:36 | 47 | 2043.717 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | WEATHER | LIGHTNING | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: crew opened line cutouts to drop load to allow safe opening of another set of cutout. associated to initial call # 1043799 | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2016-05-05 23:52 | 2016-05-06 01:15 | 2016-05-06 01:18 | -117.23 | 45.3769
4W8 | 1661499 | CPCC | CPCC1043798 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_220500_101040204 | 2016 | Before | 2016-05-05 22:49 | 2016-05-05 22:49 | 0 | 0 | 11 | 7.7 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: center phase blown on tap line fuse. refused. lightning caused | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2016-05-05 22:49 | 2016-05-06 01:14 | 2016-05-06 01:18 | -117.1874 | 45.3744
4W8 | 1661501 | CPCC | CPCC1043804 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_200701_1560039959 | 2016 | Before | 2016-05-05 23:51 | 2016-05-06 00:35 | 13 | 575.25 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | WEATHER | LIGHTNING | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: crew opened line cutouts to drop load to allow safe opening of another set of cutout. associated to initial call # 1043799 | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2016-05-05 23:51 | 2016-05-06 01:15 | 2016-05-06 01:18 | -117.2296 | 45.3778
4W8 | 1664318 | CPCC | CPCC1044926 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_120100_69740181 | 2016 | Before | 2016-05-13 08:34 | 2016-05-13 10:58 | 1 | 144.633 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: blow fuse FP120100 | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2016-05-13 11:45 | COMPLETED |  | 2016-05-13 08:34 | 2016-05-13 13:19 | 2016-05-13 13:23 | -117.1446 | 45.3989
4W8 | 1681264 | CPCC | CPCC1055404 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_247900_852830189 | 2016 | Before | 2016-07-08 15:34 | 2016-07-08 15:41 | 16 | 122.667 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | INTENTIONAL TO CLEAR TROUBLE | TREES | TREE - NON-PREVENTABLE | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Crew opened fuse on pole 247900 so they could safely remove tree from our line | DISTRIBUTION | DEVICE | MANUAL | 2016-07-08 17:45 | COMPLETED |  | 2016-07-08 15:34 | 2016-07-08 15:48 | 2016-07-08 15:53 | -117.2563 | 45.3817
4W8 | 1681379 | CPCC | CPCC1055406 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_030004_69740156 | 2016 | Before | 2016-07-08 16:15 | 2016-07-08 18:36 | 22 | 3099.8 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Tap fuse blown -- patrolled line & found tree fell on the line -- called for assist & cleared tree's | DISTRIBUTION | DEVICE | AUTO | 2016-07-08 19:15 | COMPLETED |  | 2016-07-08 16:15 | 2016-07-08 18:36 | 2016-07-08 18:38 | -117.1872 | 45.4116
4W8 | 1682280 | CPCC | CPCC1055990 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_130002_163440207 | 2016 | Before | 2016-07-11 10:52 | 2016-07-11 12:15 | 1 | 83.267 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (PROTECTED SPECIES) (BMTS) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: blue Herron | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2016-07-11 14:00 | COMPLETED |  | 2016-07-11 10:52 | 2016-07-11 15:42 | 2016-07-11 15:43 | -117.1453 | 45.3821
4W8 | 1682019 | CPCC | CPCC1055902 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_198003_101040289 | 2016 | Before | 2016-07-10 17:36 | 2016-07-10 18:54 | 1 | 78.4 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman replaced transformer fuse and restored all customers, No Cause found | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2016-07-10 20:45 | COMPLETED |  | 2016-07-10 17:36 | 2016-07-11 04:28 | 2016-07-11 04:33 | -117.2336 | 45.367
4W8 | 1683128 | CPCC | CPCC1056405 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_011601_633620135 | 2016 | Before | 2016-07-14 05:44 | 2016-07-14 06:59 | 10 | 751.333 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Tap fuse blown -- patrolling line -- | DISTRIBUTION | DEVICE | AUTO | 2016-07-14 08:45 | COMPLETED |  | 2016-07-14 05:44 | 2016-07-14 15:49 | 2016-07-14 15:53 | -117.2697 | 45.4198
4W8 | 1692295 | CPCC | CPCC1062612 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_294100_579890063 | 2016 | Before | 2016-08-11 17:39 | 2016-08-11 20:21 | 1 | 162.267 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: bird - replaced transformer fuse | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2016-08-11 20:45 | COMPLETED |  | 2016-08-11 17:39 | 2016-08-11 20:22 | 2016-08-11 20:23 | -117.2215 | 45.4429
4W8 | 1702201 | CPCC | CPCC1070267 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_199000_101040275 | 2016 | Before | 2016-09-17 23:47 | 2016-09-18 02:07 | 18 | 2153.7 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: crew changed B/O Cutout and restored all customers | DISTRIBUTION | DEVICE | AUTO | 2016-09-18 03:15 | COMPLETED |  | 2016-09-17 23:47 | 2016-09-18 05:30 | 2016-09-18 05:33 | -117.2305 | 45.3668
4W8 | 1706068 | CPCC | CPCC1072086 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_207201_267850154 | 2016 | Before | 2016-09-29 08:00 | 2016-09-29 08:46 | 5 | 230.167 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Crew replaced a broken cut out F/ P 207201 | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2016-09-29 08:00 | 2016-09-29 08:56 | 2016-09-29 08:58 | -117.2125 | 45.2816
4W8 | 1691100 | CPCC | CPCC1062036 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_137601_1560045617 | 2016 | Before | 2016-08-08 07:18 | 2016-08-08 08:10 | 2 | 102.1 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: response on site, found blown tap line fuse on pole 137601. patrolled, didn't find anything, closed on test and it held. | DISTRIBUTION | DEVICE | AUTO | 2016-08-08 10:30 | COMPLETED |  | 2016-08-08 07:19 | 2016-08-08 11:49 | 2016-08-08 11:53 | -117.2559 | 45.391
4W8 | 1695089 | CPCC | CPCC1065381 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_054701_69740434 | 2016 | Before | 2016-08-22 04:53 | 2016-08-22 05:06 | 32 | 391.467 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | SOURCE: opened reclosure FR 4W40 at FP 054701 to make repairs on bad jumper on 'A' phase. Associate this outage with 1065376 | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2016-08-22 04:53 | 2016-08-22 05:07 | 2016-08-22 05:08 | -117.2197 | 45.4226
4W8 | 1692233 | CPCC | CPCC1062600 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_138101_852830230 | 2016 | Before | 2016-08-11 15:01 | 2016-08-11 16:39 | 1 | 97.833 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Crew replaced broken cut out | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2016-08-11 18:00 | COMPLETED |  | 2016-08-11 15:01 | 2016-08-11 16:39 | 2016-08-11 16:43 | -117.2532 | 45.3847
4W8 | 1695090 | CPCC | CPCC1065376 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | Line Cut-102915 | 2016 | Before | 2016-08-22 03:17 | 2016-08-22 05:06 | 27 | 2934.9 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: Open Jumper at Field Recloser 4W40 ' A' Phase at FP 054701 | DISTRIBUTION | DEVICE | AUTO | 2016-08-22 06:30 | COMPLETED |  | 2016-08-22 03:18 | 2016-08-22 05:07 | 2016-08-22 05:08 | -117.2197 | 45.4226
4W8 | 1714466 | CPCC | CPCC1080206 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_027407_750140225 | 2016 | Before | 2016-10-27 10:29 | 2016-10-27 11:30 | 1 | 61.017 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman reported that the transformer fuse was blown and the cut out was cracked. Serviceman replaced the cut out and the blown transformer fuse | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2016-10-27 13:30 | COMPLETED |  | 2016-10-27 10:29 | 2016-10-27 15:54 | 2016-10-27 15:58 | -117.2772 | 45.417
4W8 | 1721944 | CPCC | CPCC1085463 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_027405_750140218 | 2016 | Before | 2016-12-01 10:08 | 2016-12-01 10:56 | 7 | 334.6 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown transformer fuse replaced transformer fuse | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2016-12-01 13:15 | COMPLETED |  | 2016-12-01 10:09 | 2016-12-01 11:10 | 2016-12-01 11:14 | -117.2758 | 45.4162
4W8 | 1724156 | CPCC | CPCC1087095 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_028500_673650162 | 2016 | Before | 2016-12-09 14:50 | 2016-12-09 20:42 | 307 | 93806.717 | 0 | 0 | 3 | Y | N | N | N | Y | OR Consolidated 12-09-2016 | WEATHER | WIND |  |  | POLE OH |  |  |  | SOURCE: Broken Pole, isolated, broken pole at FP 017400 - temp up - more repairs needed - all customer back in service | DISTRIBUTION | DEVICE | AUTO | 2016-12-09 18:15 | COMPLETED |  | 2016-12-09 14:56 | 2016-12-09 20:43 | 2016-12-09 20:45 | -117.275 | 45.4191
4W8 | 1710225 | CPCC | CPCC1075731 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_170900_101040327 | 2016 | Before | 2016-10-14 05:31 | 2016-10-14 07:03 | 11 | 1012.733 | 0 | 0 | 1 | Y | N | N | N | Y | OR Northeast 10-13-2016 | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown line fuses, serviceman is patrolling. Tree limb was on primary, cleared and refused. Customers are back on. | DISTRIBUTION | DEVICE | AUTO | 2016-10-14 09:15 | COMPLETED |  | 2016-10-14 06:10 | 2016-10-14 11:03 | 2016-10-14 11:08 | -117.2299 | 45.3951
4W8 | 1710467 | CPCC | CPCC1076178 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_309009_933390244 | 2016 | Before | 2016-10-14 13:03 | 2016-10-14 13:42 | 1 | 39.033 | 0 | 0 | 1 | Y | N | N | N | Y | OR Northeast 10-13-2016 | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: broken sec nust, service man made repairs | DISTRIBUTION | CUSTOMER | AUTO | 2016-10-14 16:15 | COMPLETED |  | 2016-10-14 13:03 | 2016-10-14 15:45 | 2016-10-14 15:48 | -117.2311 | 45.353
4W8 | 1713424 | CPCC | CPCC1079550 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_248300_852830213 | 2016 | Before | 2016-10-23 16:24 | 2016-10-23 17:15 | 2 | 103.033 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Re-fused transformer -- no cause | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2016-10-23 19:30 | COMPLETED |  | 2016-10-23 16:24 | 2016-10-23 18:21 | 2016-10-23 18:23 | -117.2531 | 45.3726
4W8 | 1710226 | CPCC | CPCC1075822 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_210104_1560038602 | 2016 | Before | 2016-10-14 07:36 | 2016-10-14 08:49 | 324 | 23619.6 | 0 | 0 | 1 | Y | N | N | N | Y | OR Northeast 10-13-2016 | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Tree on line caused blown fuse | DISTRIBUTION | DEVICE | AUTO | 2016-10-14 11:45 | COMPLETED |  | 2016-10-14 07:46 | 2016-10-14 11:03 | 2016-10-14 11:08 | -117.2064 | 45.28
4W8 | 1728130 | CPCC | CPCC1092612 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_191508_101040301 | 2016 | Before | 2016-12-18 03:03 | 2016-12-18 04:55 | 78 | 8738.6 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: crew to replace broken cut out | DISTRIBUTION | DEVICE | AUTO | 2016-12-18 06:30 | COMPLETED |  | 2016-12-18 03:10 | 2016-12-18 06:06 | 2016-12-18 06:08 | -117.248 | 45.3746
4W8 | 1728330 | CPCC | CPCC1092729 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_207100_267850161 | 2016 | Before | 2016-12-19 07:19 | 2016-12-19 08:40 | 1 | 80.267 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman found line fuse open, patrolled, no cause found, refused and holding | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2016-12-19 11:45 | COMPLETED |  | 2016-12-19 08:38 | 2016-12-20 08:39 | 2016-12-19 08:43 | -117.2117 | 45.2807
4W8 | 1724154 | CPCC | CPCC1087272 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_028500_673650162 | 2016 | Before | 2016-12-09 20:18 | 2016-12-09 20:41 | 61 | 1374.533 | 0 | 0 | 1 | Y | N | N | N | Y | OR Consolidated 12-09-2016 | WEATHER | WIND |  |  | POLE OH |  |  |  | SOURCE: broken pole at FP 017400 - temp up - more repairs needed - all customer back in service | DISTRIBUTION | DEVICE | AUTO | 2016-12-09 23:30 | COMPLETED |  | 2016-12-09 20:18 | 2016-12-09 20:43 | 2016-12-09 20:45 | -117.275 | 45.4191
4W8 | 1711753 | CPCC | CPCC1078230 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_308301_933390257 | 2016 | Before | 2016-10-17 06:40 | 2016-10-17 08:44 | 2 | 247.633 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | LIGHTNING ARRESTER OH |  |  |  | SOURCE: lightning arrestor found b/o | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2016-10-17 09:45 | COMPLETED |  | 2016-10-17 06:41 | 2016-10-17 10:44 | 2016-10-17 10:48 | -117.2327 | 45.3566
4W8 | 1719092 | CPCC | CPCC1082780 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_170900_101040327 | 2016 | Before | 2016-11-18 04:53 | 2016-11-18 06:43 | 12 | 1324.4 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Tap fuse blown -- serviceman patrolling line -- no trouble found -- re-fused | DISTRIBUTION | DEVICE | AUTO | 2016-11-18 08:00 | COMPLETED |  | 2016-11-18 04:53 | 2016-11-18 06:43 | 2016-11-18 06:48 | -117.2299 | 45.3951
4W8 | 1712936 | CPCC | CPCC1079209 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_100901_69740172 | 2016 | Before | 2016-10-21 05:45 | 2016-10-21 06:59 | 80 | 5881.333 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (PROTECTED SPECIES) (BMTS) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: REMOVED HAWK & REFUSED | DISTRIBUTION | DEVICE | AUTO | 2016-10-21 09:30 | COMPLETED |  | 2016-10-21 06:21 | 2016-10-21 07:47 | 2016-10-21 07:53 | -117.1887 | 45.4107
4W8 | 1712508 | CPCC | CPCC1078934 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_123001_789340134 | 2016 | Before | 2016-10-19 09:56 | 2016-10-19 11:59 | 4 | 492.933 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Found fuse open on pole 123001; unknown cause; re-fused and it held. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2016-10-19 13:00 | COMPLETED |  | 2016-10-19 09:56 | 2016-10-19 12:35 | 2016-10-19 12:38 | -117.2633 | 45.3963
4W8 | 1713189 | CPCC | CPCC1079363 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_290605_933390406 | 2016 | Before | 2016-10-22 08:22 | 2016-10-22 09:17 | 1 | 54.55 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Re-fused transformer -- starling | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2016-10-22 11:30 | COMPLETED |  | 2016-10-22 08:22 | 2016-10-22 09:55 | 2016-10-22 09:58 | -117.2292 | 45.362
4W8 | 1709870 | CPCC | CPCC1075076 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_042000_1560102488 | 2016 | Before | 2016-10-13 19:23 | 2016-10-13 20:19 | 344 | 19218.133 | 0 | 0 | 1 | Y | N | N | N | Y | OR Northeast 10-13-2016 | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: recloser 4W43 open; patrolling. Tree limb on line, cleared and closed field recloser in. Customers are back on. | DISTRIBUTION | DEVICE | AUTO | 2016-10-13 22:45 | COMPLETED |  | 2016-10-13 19:34 | 2016-10-13 20:19 | 2016-10-13 20:23 | -117.2031 | 45.3238
4W8 | 1710022 | CPCC | CPCC1075507 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_028500_673650162 | 2016 | Before | 2016-10-14 00:42 | 2016-10-14 01:16 | 307 | 10223.1 | 0 | 0 | 1 | Y | N | N | N | Y | OR Northeast 10-13-2016 | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Recloser locked open, patrolling for cause. Crew cleared tree limbs from line and restored all customers | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2016-10-14 00:42 | 2016-10-14 03:22 | 2016-10-14 03:23 | -117.275 | 45.4191
4W8 | 1710468 | CPCC | CPCC1075933 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_309009_933390244 | 2016 | Before | 2016-10-14 09:21 | 2016-10-14 12:59 | 1 | 217.567 | 0 | 0 | 1 | Y | N | N | N | Y | OR Northeast 10-13-2016 | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Tree through service, repairs made PROSPER: power out | DISTRIBUTION | CUSTOMER | AUTO | 2016-10-14 12:30 | COMPLETED |  | 2016-10-14 09:22 | 2016-10-14 16:08 | 2016-10-14 15:48 | -117.2311 | 45.353
4W8 | 1711325 | CPCC | CPCC1076919 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_207001_101040231 | 2016 | Before | 2016-10-15 13:30 | 2016-10-15 17:22 | 10 | 2311.5 | 0 | 0 | 1 | Y | N | N | N | Y | OR Northeast 10-13-2016 | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: serviceman reports bad order cutout at this pole, FP 207001 | DISTRIBUTION | DEVICE | AUTO | 2016-10-15 16:30 | COMPLETED |  | 2016-10-15 13:31 | 2016-10-16 00:15 | 2016-10-16 00:19 | -117.2128 | 45.3678
4W8 | 1730041 | CPCC | CPCC1093743 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_201704_101040261 | 2016 | Before | 2016-12-24 17:26 | 2016-12-24 19:05 | 1 | 99.167 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | SOURCE: Replaced connector at the transformer -- customer advised | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2016-12-24 20:30 | COMPLETED |  | 2016-12-24 17:26 | 2016-12-25 07:10 | 2016-12-25 07:13 | -117.2274 | 45.3768
4W8 | 1722792 | CPCC | CPCC1085980 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_290601_933390408 | 2016 | Before | 2016-12-05 11:26 | 2016-12-05 12:05 | 1 | 38.85 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Re-fused transormer -- no cause | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2016-12-05 14:30 | COMPLETED |  | 2016-12-05 11:26 | 2016-12-05 12:57 | 2016-12-05 12:58 | -117.2285 | 45.3613
4W8 | 1709936 | CPCC | CPCC1075204 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_030004_69740156 | 2016 | Before | 2016-10-13 20:20 | 2016-10-13 21:37 | 29 | 2218.983 | 0 | 0 | 1 | Y | N | N | N | Y | OR Northeast 10-13-2016 | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: 2 blown line fuses, serviceman is patrolling for cause. Removed tree limbs from line, refused and customers are back on. | DISTRIBUTION | DEVICE | AUTO | 2016-10-13 23:45 | COMPLETED |  | 2016-10-13 20:20 | 2016-10-13 22:11 | 2016-10-13 22:13 | -117.1872 | 45.4116
4W8 | 1728329 | CPCC | CPCC1092724 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_299920_304570087 | 2016 | Before | 2016-12-19 08:38 | 2016-12-19 08:40 | 0 | 0 | 9 | 12.15 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman found line fuse open, patrolled, no cause found, refused and holding | DISTRIBUTION | DEVICE | AUTO | 2016-12-19 10:30 | COMPLETED |  | 2016-12-19 07:20 | 2016-12-19 08:40 | 2016-12-19 08:43 | -117.208 | 45.2782
4W8 | 1729849 | CPCC | CPCC1093677 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_240200_1560098377 | 2016 | Before | 2016-12-23 18:20 | 2016-12-23 19:22 | 2 | 124.333 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Re-fused transformer -- cat | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2016-12-23 21:30 | COMPLETED |  | 2016-12-23 18:20 | 2016-12-24 01:35 | 2016-12-24 01:38 | -117.1461 | 45.3704
4W8 | 1711532 | CPCC | CPCC1078089 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_297704_304570102 | 2016 | Before | 2016-10-16 14:27 | 2016-10-16 15:33 | 1 | 66.25 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Crew repaired B/O Cutout and restored all customers | DISTRIBUTION | CUSTOMER | AUTO | 2016-10-16 17:30 | COMPLETED |  | 2016-10-16 14:27 | 2016-10-16 16:01 | 2016-10-16 16:03 | -117.2119 | 45.2748
4W8 | 1747615 | CPCC | CPCC1114910 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_298707_304570100 | 2017 | Before | 2017-02-16 04:57 | 2017-02-16 11:45 | 21 | 7621.15 | 0 | 0 | 2 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: found tree thru line -- primary & secondary down | DISTRIBUTION | DEVICE | MANUAL | 2017-02-16 13:00 | COMPLETED |  | 2017-02-16 04:57 | 2017-02-16 12:06 | 2017-02-16 12:08 | -117.2107 | 45.2748
4W8 | 1738912 | CPCC | CPCC1105595 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_170900_101040327 | 2017 | Before | 2017-01-18 06:21 | 2017-01-18 09:07 | 11 | 1825.633 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (PROTECTED SPECIES) (BMTS) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown line fuse at FP# 170900, serviceman is patrolling. Found 2 owls at FP081100 Crew is bird guarding the pole | DISTRIBUTION | DEVICE | AUTO | 2017-01-18 09:30 | COMPLETED |  | 2017-01-18 06:21 | 2017-01-18 09:49 | 2017-01-18 09:53 | -117.2299 | 45.3951
4W8 | 1746644 | CPCC | CPCC1114382 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_330000_353200014 | 2017 | Before | 2017-02-12 14:28 | 2017-02-12 15:59 | 10 | 907.833 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (PROTECTED SPECIES) (BMTS) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman found open line fuse, patrolling for cause, Serviceman found dead hawk at FP 163200, removed and refused, restored all customers | DISTRIBUTION | DEVICE | AUTO | 2017-02-12 17:30 | COMPLETED |  | 2017-02-12 14:28 | 2017-02-12 16:39 | 2017-02-12 16:43 | -117.2087 | 45.5149
4W8 | 1744362 | CPCC | CPCC1111295 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_205004_101040240 | 2017 | Before | 2017-02-05 20:30 | 2017-02-05 21:26 | 10 | 561 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman found Dip Fuse Open, no Cause Found, refused and restored all customers | DISTRIBUTION | DEVICE | AUTO | 2017-02-05 23:45 | COMPLETED |  | 2017-02-05 20:31 | 2017-02-06 03:11 | 2017-02-06 03:13 | -117.2201 | 45.3669
4W8 | 1751904 | CPCC | CPCC1118181 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_169701_1560029376 | 2017 | Before | 2017-03-04 21:08 | 2017-03-04 21:56 | 7 | 337.283 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Tap fuse blown - patrolled line -- no trouble found -- re-fused | DISTRIBUTION | DEVICE | AUTO | 2017-03-05 00:15 | COMPLETED |  | 2017-03-04 21:08 | 2017-03-05 06:25 | 2017-03-05 06:29 | -117.1886 | 45.3928
4W8 | 1744136 | CPCC | CPCC1111031 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_028300_750140221 | 2017 | Before | 2017-02-04 21:02 | 2017-02-04 22:07 | 1 | 64.817 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | SNOW, SLEET AND BLIZZARD |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Snow caused service drop to break, serviceman to make repairs and put service back up, all repairs completed and customers restored PROSPER: power out | DISTRIBUTION | CUSTOMER | AUTO | 2017-02-05 00:15 | COMPLETED |  | 2017-02-04 21:02 | 2017-02-06 10:38 | 2017-02-05 01:43 | -117.2743 | 45.4159
4W8 | 1744363 | CPCC | CPCC1111294 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_201000_101040247 | 2017 | Before | 2017-02-05 20:29 | 2017-02-05 20:42 | 3 | 37.55 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman found open Transformer fuse, No Cuase found, refused and restored all customers | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2017-02-05 20:29 | 2017-02-06 03:12 | 2017-02-06 03:14 | -117.2275 | 45.3668
4W8 | 1740808 | CPCC | CPCC1108468 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_200703_101040260 | 2017 | Before | 2017-01-23 08:10 | 2017-01-23 09:12 | 1 | 62.45 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: fuse unknown | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2017-01-23 11:15 | COMPLETED |  | 2017-01-23 08:10 | 2017-01-23 09:14 | 2017-01-23 09:18 | -117.2288 | 45.3768
4W8 | 1744400 | CPCC | CPCC1111441 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_320900_997300256 | 2017 | Before | 2017-02-06 04:36 | 2017-02-06 06:14 | 2 | 197.433 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | POLE OH |  |  |  | SOURCE: Crew added pole top extension and restored all customers | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2017-02-06 04:36 | 2017-02-06 06:30 | 2017-02-06 06:33 | -117.2277 | 45.3518
4W8 | 1744381 | CPCC | CPCC1111440 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_309300_933390198 | 2017 | Before | 2017-02-06 03:24 | 2017-02-06 04:36 | 104 | 7328.25 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Fuses at FP 309300 blown due to Pole Fire at FP 320900, serviceman isolated and refused, restored all customers | DISTRIBUTION | DEVICE | AUTO | 2017-02-06 07:15 | COMPLETED |  | 2017-02-06 04:12 | 2017-02-06 04:39 | 2017-02-06 04:43 | -117.2301 | 45.3573
4W8 | 1747470 | CPCC | CPCC1114801 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_291108_1560078921 | 2017 | Before | 2017-02-15 23:16 | 2017-02-16 01:17 | 27 | 3272.85 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: field recloser 4W11 tripped open. tree across primary lines. associated outage 1114799. tree cleared and field recloser closed PROSPER: This outage needs an arrive time on 2345 please CPCC1114801 OR ENTERPRISE ENTERPRISE (OR) 4W8 27 27 02/15/17 23:15 02/16/17 01:17 Mike Lanegan Pendleton/Enterprise Ops 541-278-2936 office 541-303-3238 cell | DISTRIBUTION | DEVICE | AUTO | 2017-02-16 02:30 | COMPLETED |  | 2017-02-15 23:19 | 2017-02-16 07:39 | 2017-02-16 02:53 | -117.2268 | 45.3544
4W8 | 1751476 | CPCC | CPCC1117933 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_030004_69740156 | 2017 | Before | 2017-03-02 15:38 | 2017-03-02 17:21 | 35 | 3627.167 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: two fuses found open, on patrol. no cause found, refused and holding | DISTRIBUTION | DEVICE | AUTO | 2017-03-02 19:15 | COMPLETED |  | 2017-03-02 16:22 | 2017-03-02 21:12 | 2017-03-02 21:14 | -117.1872 | 45.4116
4W8 | 1744401 | CPCC | CPCC1111453 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | Line Cut-105497 | 2017 | Before | 2017-02-06 05:09 | 2017-02-06 06:14 | 3 | 194.65 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | PLANNED OUTAGE |  |  |  | SOURCE: Serviceman lifted Hot taps at this FP to make repairs to Pole at FP 320900 | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2017-02-06 05:09 | 2017-02-06 06:30 | 2017-02-06 06:33 | -117.2277 | 45.3522
4W8 | 1742051 | CPCC | CPCC1109208 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_259602_899040118 | 2017 | Before | 2017-01-26 11:56 | 2017-01-26 13:11 | 1 | 74.767 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: Serviceman replaced B/O Connector and restored all customers PROSPER: power out | DISTRIBUTION | CUSTOMER | AUTO | 2017-01-26 15:00 | COMPLETED |  | 2017-01-26 11:56 | 2017-01-26 15:43 | 2017-01-26 13:38 | -117.2518 | 45.3623
4W8 | 1745605 | CPCC | CPCC1113520 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_020204_69740113 | 2017 | Before | 2017-02-09 07:43 | 2017-02-09 08:30 | 1 | 46.833 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Open line fuses at FP# 020204, serviceman is patrolling. nothing found, refused | DISTRIBUTION | DEVICE | AUTO | 2017-02-09 10:45 | COMPLETED |  | 2017-02-09 07:43 | 2017-02-09 09:25 | 2017-02-09 09:28 | -117.1672 | 45.4157
4W8 | 1743149 | CPCC | CPCC1109720 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_117180_789340090 | 2017 | Before | 2017-01-31 16:13 | 2017-01-31 17:18 | 1 | 65.65 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE ONLY -UG ( NO CAUSE FOUND) |  |  |  | SOURCE: Serviceman replaced a blown padmount transformer fuse | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2017-01-31 19:15 | COMPLETED |  | 2017-01-31 16:13 | 2017-01-31 18:39 | 2017-01-31 18:43 | -117.2771 | 45.3989
4W8 | 1739068 | CPCC | CPCC1106232 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | EPS_CB4W8 | 2017 | Before | 2017-01-18 11:33 | 2017-01-18 11:47 | 1436 | 20510.867 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: CB 1W6 & 1W48 liocked open | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2017-01-18 11:38 | 2017-01-19 16:12 | 2017-01-18 13:28 | -117.2824 | 45.418
4W8 | 1744360 | CPCC | CPCC1111308 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_202003_101040246 | 2017 | Before | 2017-02-05 20:57 | 2017-02-05 21:27 | 2 | 60.367 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman found Transformer Fuse Open, no Cause Found, refused and restored all customers | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2017-02-06 | COMPLETED |  | 2017-02-05 20:57 | 2017-02-06 03:11 | 2017-02-06 03:13 | -117.224 | 45.3674
4W8 | 1744364 | CPCC | CPCC1111281 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_200001_1560001075 | 2017 | Before | 2017-02-05 19:52 | 2017-02-05 20:28 | 19 | 684 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: Serviceman repaired b/o Jumper at FP 200001, restored all customers | DISTRIBUTION | DEVICE | AUTO | 2017-02-05 23:00 | COMPLETED |  | 2017-02-05 19:52 | 2017-02-06 03:12 | 2017-02-06 03:14 | -117.2295 | 45.3668
4W8 | 1776670 | CPCC | CPCC1141728 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_309402_933390281 | 2017 | Before | 2017-05-22 10:04 | 2017-05-22 11:10 | 9 | 590.1 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | LIGHTNING ARRESTER OH |  |  |  | SOURCE: bad lightning arrester | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2017-05-22 10:05 | 2017-05-22 12:21 | 2017-05-22 12:23 | -117.2312 | 45.3586
4W8 | 1776671 | CPCC | CPCC1141705 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_055922_221510259 | 2017 | Before | 2017-05-22 08:19 | 2017-05-22 09:19 | 1 | 59.15 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: b/o secondary connector. | DISTRIBUTION | CUSTOMER | AUTO | 2017-05-22 11:30 | COMPLETED |  | 2017-05-22 08:20 | 2017-05-22 12:22 | 2017-05-22 12:23 | -117.2153 | 45.3355
4W8 | 1775583 | CPCC | CPCC1140512 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_030004_69740156 | 2017 | Before | 2017-05-17 17:25 | 2017-05-17 18:34 | 22 | 1507.367 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown line fuse patrolling for cause, no cause found, refused and holding | DISTRIBUTION | DEVICE | AUTO | 2017-05-17 20:45 | COMPLETED |  | 2017-05-17 17:40 | 2017-05-17 19:32 | 2017-05-17 19:33 | -117.1872 | 45.4116
4W8 | 1775683 | CPCC | CPCC1140547 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_309300_933390198 | 2017 | Before | 2017-05-18 07:36 | 2017-05-18 08:15 | 27 | 1047.6 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | INSULATOR OH |  |  |  | SOURCE: Blown dip fuse, Arcing due to failed insulator. Replaced and customers are back on. Outage was restored at 08:15:00 PROSPER: add 1 from CPCC1140550, Associated to outage 1140547. Bad connectivity in Cadops. | DISTRIBUTION | DEVICE | AUTO | 2017-05-18 11:00 | COMPLETED |  | 2017-05-18 07:36 | 2017-05-25 15:05 | 2017-05-18 08:54 | -117.2301 | 45.3573
4W8 | 1760820 | CPCC | CPCC1125461 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_220500_101040204 | 2017 | Before | 2017-04-04 19:04 | 2017-04-04 23:49 | 19 | 5421.65 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Serviceman arrived, Found B/O Cutout, requested 2nd Lineman, ARCOS Callout started, Lineman enroute from Pendleton to assist, Crew onsite, repairs in Progress, Repairs complete and all customers restored | DISTRIBUTION | DEVICE | MANUAL | 2017-04-05 01:00 | COMPLETED |  | 2017-04-04 19:04 | 2017-04-05 05:59 | 2017-04-05 06:03 | -117.1874 | 45.3744
4W8 | 1779615 | CPCC | CPCC1143561 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_120100_69740181 | 2017 | Before | 2017-05-31 13:39 | 2017-05-31 15:05 | 1 | 85.933 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: refused | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2017-05-31 16:45 | COMPLETED |  | 2017-05-31 13:39 | 2017-05-31 16:05 | 2017-05-31 16:08 | -117.1446 | 45.3989
4W8 | 1781193 | CPCC | CPCC1144474 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_116680_69740183 | 2017 | Before | 2017-06-05 16:13 | 2017-06-05 23:08 | 1 | 415.083 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: tree removed near FP 117500 transformer re-energized and customers power has been restored | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2017-06-06 | COMPLETED |  | 2017-06-05 16:13 | 2017-06-06 06:27 | 2017-06-06 06:29 | -117.1538 | 45.4061
4W8 | 1781391 | CPCC | CPCC1144648 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_120100_69740181 | 2017 | Before | 2017-06-06 15:45 | 2017-06-06 17:29 | 1 | 104.117 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: b/o cut out | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2017-06-06 18:45 | COMPLETED |  | 2017-06-06 15:45 | 2017-06-06 17:54 | 2017-06-06 17:58 | -117.1446 | 45.3989
4W8 | 1788016 | CPCC | CPCC1147891 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_162200_101040182 | 2017 | Before | 2017-06-25 09:05 | 2017-06-25 18:02 | 1 | 536.533 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: Bad jumper & cutouts -- ran Arcos for a crew | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2017-06-25 21:15 | COMPLETED |  | 2017-06-25 09:05 | 2017-06-26 00:55 | 2017-06-26 00:58 | -117.2043 | 45.3851
4W8 | 1790875 | CPCC | CPCC1150396 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_214700__4308881 | 2017 | Before | 2017-07-03 15:01 | 2017-07-03 15:47 | 1 | 45.85 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Re-fused transformer -- no cause | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2017-07-03 18:15 | COMPLETED |  | 2017-07-03 15:02 | 2017-07-03 17:04 | 2017-07-03 17:08 | -117.1983 | 45.3777
4W8 | 1791383 | CPCC | CPCC1150643 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_140701_163440206 | 2017 | Before | 2017-07-05 11:26 | 2017-07-05 12:20 | 1 | 54.633 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Re-fused tronsformer -- no cause | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2017-07-05 14:30 | COMPLETED |  | 2017-07-05 11:26 | 2017-07-05 13:31 | 2017-07-05 13:33 | -117.1654 | 45.3924
4W8 | 1793174 | CPCC | CPCC1152056 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_127003_789340132 | 2017 | Before | 2017-07-10 09:29 | 2017-07-10 10:09 | 22 | 889.9 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman refused Line Fuses at FP 127003, No Cause Found, Restored all customers | DISTRIBUTION | DEVICE | AUTO | 2017-07-10 13:00 | COMPLETED |  | 2017-07-10 09:47 | 2017-07-10 11:00 | 2017-07-10 11:03 | -117.2547 | 45.3965
4W8 | 1794888 | CPCC | CPCC1152789 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | RC_028500_673650162 | 2017 | Before | 2017-07-15 04:21 | 2017-07-15 05:50 | 311 | 27751.567 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: patroled no cause | DISTRIBUTION | DEVICE | AUTO | 2017-07-15 07:30 | COMPLETED |  | 2017-07-15 04:28 | 2017-07-15 05:51 | 2017-07-15 05:53 | -117.275 | 45.4191
4W8 | 1796606 | CPCC | CPCC1153774 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_136000_852830228 | 2017 | Before | 2017-07-19 20:11 | 2017-07-19 21:16 | 1 | 65.267 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | SOURCE: non protected bird caused transformer fuse to open, tested and refused, customer has been restored | DISTRIBUTION | CUSTOMER | AUTO | 2017-07-19 23:15 | COMPLETED |  | 2017-07-19 20:11 | 2017-07-19 21:48 | 2017-07-19 21:53 | -117.2575 | 45.3819
4W8 | 1797041 | CPCC | CPCC1153933 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_290601_933390408 | 2017 | Before | 2017-07-21 07:58 | 2017-07-21 08:38 | 1 | 39.75 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown xfmr fuse due to a starling | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2017-07-21 11:00 | COMPLETED |  | 2017-07-21 07:58 | 2017-07-21 08:38 | 2017-07-21 08:43 | -117.2285 | 45.3613
4W8 | 1798198 | CPCC | CPCC1154732 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_161100_1560045418 | 2017 | Before | 2017-07-24 20:54 | 2017-07-24 21:50 | 1 | 55.633 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: refused | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2017-07-24 20:54 | 2017-07-25 06:21 | 2017-07-25 06:23 | -117.2043 | 45.4732
4W8 | 1804841 | CPCC | CPCC1158834 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | Line Cut-108422 | 2017 | Before | 2017-08-13 09:03 | 2017-08-13 10:39 | 5 | 477.25 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman replaced a blown fuse at F/P 121004 that is NOT modelled on cad ops | DISTRIBUTION | DEVICE | AUTO | 2017-08-13 12:30 | COMPLETED |  | 2017-08-13 09:03 | 2017-08-13 19:14 | 2017-08-13 19:18 | -117.2684 | 45.3962
4W8 | 1804844 | CPCC | CPCC1158819 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_240501_163440212 | 2017 | Before | 2017-08-13 07:54 | 2017-08-13 10:13 | 1 | 138.517 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman replaced a blown fuse at F/P 240501. Cause Unknown | DISTRIBUTION | DEVICE | AUTO | 2017-08-13 11:00 | COMPLETED |  | 2017-08-13 07:54 | 2017-08-13 19:14 | 2017-08-13 19:18 | -117.1445 | 45.3742
4W8 | 1805288 | CPCC | CPCC1159082 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_200701_1560039959 | 2017 | Before | 2017-08-14 20:50 | 2017-08-14 23:25 | 21 | 3258.85 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: serviceman reports 2 fuses open at FP 200701, patrolled line, no cause found, refused and customers have been restored | DISTRIBUTION | DEVICE | MANUAL | 2017-08-15 02:00 | COMPLETED |  | 2017-08-14 20:50 | 2017-08-15 00:20 | 2017-08-15 00:23 | -117.2296 | 45.3778
4W8 | 1805937 | CPCC | CPCC1159249 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_240501_163440212 | 2017 | Before | 2017-08-16 10:26 | 2017-08-16 11:28 | 1 | 62.733 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Crew changed B/O Cutout, restored all customers | DISTRIBUTION | DEVICE | AUTO | 2017-08-16 13:30 | COMPLETED |  | 2017-08-16 10:26 | 2017-08-17 06:33 | 2017-08-17 06:38 | -117.1445 | 45.3742
4W8 | 1808654 | CPCC | CPCC1160776 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_270702_1560045404 | 2017 | Before | 2017-08-27 11:37 | 2017-08-27 15:51 | 4 | 1016.067 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: serviceman enroute from pendleton replaced tap fuse | DISTRIBUTION | DEVICE | MANUAL | 2017-08-27 16:45 | COMPLETED |  | 2017-08-27 11:37 | 2017-08-27 15:53 | 2017-08-27 15:58 | -117.1872 | 45.3631
4W8 | 1810371 | CPCC | CPCC1161693 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_214700__4308881 | 2017 | Before | 2017-09-02 08:12 | 2017-09-02 13:20 | 1 | 307.8 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman replaced a blown transformer fuse due to a starling | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2017-09-02 14:15 | COMPLETED |  | 2017-09-02 08:19 | 2017-09-02 18:10 | 2017-09-02 18:13 | -117.1983 | 45.3777
4W8 | 1814115 | CPCC | CPCC1163818 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | SB_055922__4414832 | 2017 | Before | 2017-09-15 13:23 | 2017-09-15 19:03 | 178 | 60404.3 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | SOURCE: B/O primary connector, crew coming from Pendleton Crew repaired a broken jumper at 055922 | DISTRIBUTION | DEVICE | MANUAL | 2017-09-15 20:38 | COMPLETED |  | 2017-09-15 13:28 | 2017-09-15 19:42 | 2017-09-15 19:43 | -117.2152 | 45.3355
4W8 | 1815429 | CPCC | CPCC1164763 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_237500_852830222 | 2017 | Before | 2017-09-20 00:32 | 2017-09-20 02:30 | 1 | 117.967 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman replaced a blown transformer fuse, cause unknown | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2017-09-20 03:45 | COMPLETED |  | 2017-09-20 00:33 | 2017-09-20 11:29 | 2017-09-20 11:33 | -117.2763 | 45.375
4W8 | 1817363 | CPCC | CPCC1165577 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_170900_101040327 | 2017 | Before | 2017-09-27 09:03 | 2017-09-27 09:55 | 11 | 574.383 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Line Fuse Open, Patrolling for cause, No Cause Found, refused and restored | DISTRIBUTION | DEVICE | AUTO | 2017-09-27 12:15 | COMPLETED |  | 2017-09-27 09:03 | 2017-09-27 19:48 | 2017-09-27 19:49 | -117.2299 | 45.3951
4W8 | 1822289 | CPCC | CPCC1168525 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_259602_899040118 | 2017 | Before | 2017-10-17 19:28 | 2017-10-17 20:23 | 1 | 54.817 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: Serviceman replaced B/o Connector and restored customers | DISTRIBUTION | CUSTOMER | AUTO | 2017-10-17 22:00 | COMPLETED |  | 2017-10-17 19:28 | 2017-10-17 20:40 | 2017-10-17 20:43 | -117.2518 | 45.3623
4W8 | 1823904 | CPCC | CPCC1170533 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_199201_101040291 | 2017 | Before | 2017-10-22 11:40 | 2017-10-22 14:56 | 1 | 196.4 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: Broken high side jumper, cause was wind. Repairs made. | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2017-10-22 16:45 | COMPLETED |  | 2017-10-22 11:40 | 2017-10-22 14:57 | 2017-10-22 14:58 | -117.2306 | 45.3706
4W8 | 1827523 | CPCC | CPCC1172293 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_234302_163440222 | 2017 | Before | 2017-11-06 15:54 | 2017-11-06 17:28 | 1 | 94.417 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: fuse open at transformer - no cause found - tested then refused | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2017-11-06 19:00 | COMPLETED |  | 2017-11-06 15:54 | 2017-11-07 04:03 | 2017-11-07 04:08 | -117.158 | 45.3716
4W8 | 1831417 | CPCC | CPCC1175988 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_118900_750140204 | 2017 | Before | 2017-11-22 07:59 | 2017-11-22 08:38 | 4 | 156.4 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | INSULATOR OH |  |  |  | SOURCE: Found blown fuse on FP 118900; patrolled, nothing found, re-fused was due to a b/o insulator | DISTRIBUTION | DEVICE | AUTO | 2017-11-22 10:30 | COMPLETED |  | 2017-11-22 07:59 | 2017-11-27 14:17 | 2017-11-22 10:09 | -117.2749 | 45.4105
4W8 | 1831418 | CPCC | CPCC1175995 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_118900_750140204 | 2017 | Before | 2017-11-22 08:38 | 2017-11-22 09:57 | 14 | 1095.267 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | INSULATOR OH |  |  |  | SOURCE: As serviceman was driving away, saw fuse on FP 118900 opened up again, will patrol again, found b/o insulator on FP 0244/120901 | DISTRIBUTION | DEVICE | MANUAL | 2017-11-22 12:00 | COMPLETED |  | 2017-11-22 08:38 | 2017-11-22 10:06 | 2017-11-22 10:09 | -117.2749 | 45.4105
4W8 | 1831590 | CPCC | CPCC1176103 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_297420_304570078 | 2017 | Before | 2017-11-22 20:00 | 2017-11-23 02:25 | 21 | 8076.6 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Tree on line, ARCOS Callout completed for 1 lineman to help remove and make repairs, wire is down across river, 2 additional Lineman called out from Pendleton to assist, all repairs complete and all customers restored | DISTRIBUTION | DEVICE | MANUAL | 2017-11-23 04:30 | COMPLETED |  | 2017-11-22 20:00 | 2017-11-23 06:36 | 2017-11-23 06:39 | -117.2123 | 45.271
4W8 | 1831633 | CPCC | CPCC1176144 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_199900_101040304 | 2017 | Before | 2017-11-23 12:15 | 2017-11-23 14:04 | 5 | 545.083 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | LIGHTNING ARRESTER OH |  |  |  | SOURCE: Cleared blown lightning arrestor -- re-fused | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2017-11-23 14:45 | COMPLETED |  | 2017-11-23 12:15 | 2017-11-23 16:47 | 2017-11-23 16:48 | -117.2308 | 45.3813
4W8 | 1832115 | CPCC | CPCC1176629 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_210200_579890079 | 2017 | Before | 2017-11-26 17:27 | 2017-11-26 20:29 | 2 | 362.967 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: line fuse opened at FP 210200, serviceman patrolled out from this fuse, no cause found, refused and holding, serivceman reporting wind in the area and believes lines | DISTRIBUTION | DEVICE | AUTO | 2017-11-26 20:30 | COMPLETED |  | 2017-11-26 17:27 | 2017-11-26 21:20 | 2017-11-26 21:23 | -117.2083 | 45.4601
4W8 | 1833358 | CPCC | CPCC1177195 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_280903_304570156 | 2017 | Before | 2017-12-01 13:43 | 2017-12-01 14:33 | 2 | 100.4 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Tree branch fell across transformer, serviceman removed and refused, restored all customers | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2017-12-01 17:00 | COMPLETED |  | 2017-12-01 14:19 | 2017-12-01 15:12 | 2017-12-01 15:14 | -117.2076 | 45.277
4W8 | 1836316 | CPCC | CPCC1178620 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_330600_579890067 | 2017 | Before | 2017-12-16 00:02 | 2017-12-16 03:28 | 31 | 6388.583 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | SNOW, SLEET AND BLIZZARD |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman refused line fuses blown due to snow loading on line | DISTRIBUTION | DEVICE | AUTO | 2017-12-16 05:15 | COMPLETED |  | 2017-12-16 02:14 | 2017-12-16 06:38 | 2017-12-16 06:43 | -117.2092 | 45.4353
4W8 | 1837918 | CPCC | CPCC1179941 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_137101_852830185 | 2017 | Before | 2017-12-22 23:54 | 2017-12-23 00:40 | 3 | 137.55 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman replaced the blown line fuse at F/P 137101 Cause unknown | DISTRIBUTION | DEVICE | AUTO | 2017-12-23 03:00 | COMPLETED |  | 2017-12-22 23:54 | 2017-12-23 06:06 | 2017-12-23 06:09 | -117.2559 | 45.3847
4W8 | 1842982 | CPCC | CPCC1184436 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_199704_101040273 | 2018 | Before | 2018-01-19 03:35 | 2018-01-19 04:52 | 42 | 3233.3 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | SNOW, SLEET AND BLIZZARD |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: patroled & refused | DISTRIBUTION | DEVICE | AUTO | 2018-01-19 07:00 | COMPLETED |  | 2018-01-19 03:52 | 2018-01-19 04:53 | 2018-01-19 04:54 | -117.23 | 45.3769
4W8 | 1851469 | CPCC | CPCC1191490 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_057901_69740153 | 2018 | Before | 2018-02-28 14:31 | 2018-02-28 14:36 | 0 | 0 | 1 | 4.617 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: Serviceman replaced B/O Connector, restored customers | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2018-02-28 14:31 | 2018-02-28 14:45 | 2018-02-28 14:49 | -117.2145 | 45.4262
4W8 | 1858684 | CPCC | CPCC1195961 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_170900_101040327 | 2018 | Before | 2018-03-27 08:15 | 2018-03-27 09:31 | 6 | 453.6 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: refused | DISTRIBUTION | DEVICE | MANUAL | 2018-03-27 12:00 | COMPLETED |  | 2018-03-27 09:14 | 2018-03-27 17:22 | 2018-03-27 17:26 | -117.2299 | 45.3951
4W8 | 1858912 | CPCC | CPCC1196045 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_302502_933390306 | 2018 | Before | 2018-03-28 08:08 | 2018-03-28 11:31 | 12 | 2428.4 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | LIGHTNING ARRESTER OH |  |  |  | SOURCE: b/o arrestor | DISTRIBUTION | DEVICE | MANUAL | 2018-03-28 13:00 | COMPLETED |  | 2018-03-28 08:08 | 2018-03-28 15:06 | 2018-03-28 15:11 | -117.2459 | 45.3599
4W8 | 1859653 | CPCC | CPCC1196562 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_220500_101040204 | 2018 | Before | 2018-04-02 03:34 | 2018-04-02 05:38 | 26 | 3223.567 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown line fuse, serviceman is patrolling. No cause, found. Refused and customers are back on. | DISTRIBUTION | DEVICE | AUTO | 2018-04-02 07:15 | COMPLETED |  | 2018-04-02 04:36 | 2018-04-02 06:17 | 2018-04-02 06:20 | -117.1874 | 45.3744
4W8 | 1859655 | CPCC | CPCC1196542 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_054900_69740133 | 2018 | Before | 2018-04-01 19:57 | 2018-04-01 20:51 | 3 | 163.35 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown transformer fuse, cause unknown. Refused and customers are back on. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2018-04-01 22:30 | COMPLETED |  | 2018-04-01 19:57 | 2018-04-02 06:17 | 2018-04-02 06:20 | -117.2205 | 45.4259
4W8 | 1862498 | CPCC | CPCC1198426 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_011300_633620116 | 2018 | Before | 2018-04-13 07:31 | 2018-04-13 09:56 | 18 | 2610 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Blown riser fuse, on primary cable | DISTRIBUTION | DEVICE | MANUAL | 2018-04-13 14:01 | COMPLETED |  | 2018-04-13 07:31 | 2018-04-13 12:22 | 2018-04-13 12:25 | -117.2684 | 45.4159
4W8 | 1862833 | CPCC | CPCC1198637 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_119580_789340123 | 2018 | Before | 2018-04-15 10:30 | 2018-04-15 13:14 | 1 | 164.417 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman repaired the secondary service drop due to a tree rubbing on the conductors | DISTRIBUTION | CUSTOMER | AUTO | 2018-04-15 13:30 | COMPLETED |  | 2018-04-15 10:30 | 2018-04-15 21:30 | 2018-04-15 21:35 | -117.2729 | 45.4046
4W8 | 1862735 | CPCC | CPCC1198537 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_092300_579890054 | 2018 | Before | 2018-04-14 14:10 | 2018-04-14 20:23 | 2 | 746.067 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: serviceman reports that there was a deteriorated fuse, refused the cutout and customers are back in service | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2018-04-14 23:00 | COMPLETED |  | 2018-04-14 14:10 | 2018-04-14 20:44 | 2018-04-14 20:45 | -117.2039 | 45.4893
4W8 | 1866026 | CPCC | CPCC1200110 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_105200_69740173 | 2018 | Before | 2018-04-29 05:41 | 2018-04-29 06:37 | 2 | 110.933 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: refused | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2018-04-29 08:45 | COMPLETED |  | 2018-04-29 05:41 | 2018-04-29 06:37 | 2018-04-29 06:40 | -117.1779 | 45.4009
4W8 | 1866932 | CPCC | CPCC1200873 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_199000__3275393 | 2018 | Before | 2018-05-03 08:22 | 2018-05-03 09:11 | 1 | 49.05 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: serviceman reports that this was a bad connector, made repairs and customer is back in service | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2018-05-03 11:45 | COMPLETED |  | 2018-05-03 08:22 | 2018-05-03 12:31 | 2018-05-03 12:35 | -117.2304 | 45.3668
4W8 | 1868776 | CPCC | CPCC1202225 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_030004_69740156 | 2018 | Before | 2018-05-12 09:48 | 2018-05-12 11:23 | 38 | 3582.133 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (PROTECTED SPECIES) (BMTS) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Tap fuses blown -- patrolled line & found hawk on the line -- cleared & re-fused | DISTRIBUTION | DEVICE | AUTO | 2018-05-12 13:15 | COMPLETED |  | 2018-05-12 09:48 | 2018-05-12 17:10 | 2018-05-12 17:10 | -117.1872 | 45.4116
4W8 | 1872576 | CPCC | CPCC1204309 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_070003_69740114 | 2018 | Before | 2018-05-30 20:26 | 2018-05-30 21:21 | 2 | 110.033 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Line Fuse Open, Serviceman patrolled and found no cause, refused and restored | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2018-05-30 20:26 | 2018-05-30 23:18 | 2018-05-30 23:20 | -117.2505 | 45.3965
4W8 | 1873111 | CPCC | CPCC1204580 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_320720_997300300 | 2018 | Before | 2018-06-01 20:53 | 2018-06-01 22:35 | 1 | 101.967 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | SOURCE: replaced bad connectors at the weatherhead | DISTRIBUTION | CUSTOMER | AUTO | 2018-06-02 | COMPLETED |  | 2018-06-01 20:53 | 2018-06-02 07:00 | 2018-06-02 07:01 | -117.229 | 45.3486
4W8 | 1873573 | CPCC | CPCC1204736 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_030004_69740156 | 2018 | Before | 2018-06-03 19:17 | 2018-06-04 01:28 | 31 | 11504.1 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: 2 tap fuses blown -- patrolling line -- ran Arcos for help to patrol -- cleared tree branch from line & re-fused | DISTRIBUTION | DEVICE | MANUAL | 2018-06-04 03:00 | COMPLETED |  | 2018-06-03 19:17 | 2018-06-04 17:09 | 2018-06-04 17:10 | -117.1872 | 45.4116
4W8 | 1873670 | CPCC | CPCC1204828 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_207100_267850161 | 2018 | Before | 2018-06-04 13:40 | 2018-06-04 19:31 | 1 | 351.117 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Broken Cutout, Crew to repair, help coming from Pendleton | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2018-06-04 21:30 | COMPLETED |  | 2018-06-04 13:40 | 2018-06-05 01:35 | 2018-06-05 01:40 | -117.2117 | 45.2807
4W8 | 1873917 | CPCC | CPCC1204981 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_264800_163440183 | 2018 | Before | 2018-06-05 16:10 | 2018-06-05 16:54 | 1 | 43.767 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: hot tap found lifted, service restored | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2018-06-05 19:30 | COMPLETED |  | 2018-06-05 16:10 | 2018-06-05 22:18 | 2018-06-05 22:20 | -117.1568 | 45.3651
4W8 | 1875196 | CPCC | CPCC1205785 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_330600_579890067 | 2018 | Before | 2018-06-10 13:10 | 2018-06-11 00:04 | 32 | 20913.6 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | POLE OH |  |  |  | SOURCE: Tap fuses blown -- patrolled line to report of pole fire -- ran Arcos for a crew PROSPER: change time to first out 06/10/2018 13:10:18, was 06/10/2018 10:42:00 | DISTRIBUTION | DEVICE | MANUAL | 2018-06-11 08:15 | COMPLETED |  | 2018-06-10 13:18 | 2018-06-11 14:42 | 2018-06-11 07:15 | -117.2092 | 45.4353
4W8 | 1878368 | CPCC | CPCC1211204 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | EPS_CB4W8 | 2018 | Before | 2018-06-22 03:03 | 2018-06-22 03:47 | 1478 | 64785.667 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Loss of transmission line, cause under investigation | DISTRIBUTION | DEVICE | AUTO | 2018-06-22 05:15 | COMPLETED |  | 2018-06-22 03:12 | 2018-06-22 12:58 | 2018-06-22 05:55 | -117.2824 | 45.418
4W8 | 1879571 | CPCC | CPCC1212115 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_264800_163440183 | 2018 | Before | 2018-06-26 08:56 | 2018-06-26 15:29 | 1 | 393.25 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown XFMR fuse, cause unknown. Refused and holding. Service restored. | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2018-06-26 19:00 | COMPLETED |  | 2018-06-26 08:56 | 2018-06-27 08:35 | 2018-06-27 08:40 | -117.1568 | 45.3651
4W8 | 1879639 | CPCC | CPCC1212174 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_296105_1560102781 | 2018 | Before | 2018-06-26 17:57 | 2018-06-26 23:33 | 9 | 3023.55 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Dip fuse blown, bad cutout | DISTRIBUTION | DEVICE | MANUAL | 2018-06-27 | COMPLETED |  | 2018-06-26 17:57 | 2018-06-27 11:12 | 2018-06-27 11:15 | -117.2168 | 45.3541
4W8 | 1880257 | CPCC | CPCC1212750 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_037800_69740178 | 2018 | Before | 2018-06-29 10:08 | 2018-06-29 16:18 | 1 | 370 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (PROTECTED SPECIES) (BMTS) |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: B/O cut outs caused by hawk's on line | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2018-06-29 16:30 | COMPLETED |  | 2018-06-29 11:14 | 2018-06-29 16:34 | 2018-06-29 16:35 | -117.174 | 45.4239
4W8 | 1881666 | CPCC | CPCC1213808 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_219800_101040178 | 2018 | Before | 2018-07-05 11:14 | 2018-07-05 13:14 | 3 | 359.6 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: cut out replaced | DISTRIBUTION | DEVICE | MANUAL | 2018-07-05 15:45 | COMPLETED |  | 2018-07-05 11:14 | 2018-07-05 17:33 | 2018-07-05 17:35 | -117.1882 | 45.3791
4W8 | 1881951 | CPCC | CPCC1213981 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_199704_101040273 | 2018 | Before | 2018-07-06 15:15 | 2018-07-06 18:01 | 14 | 2318.4 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: b/o cut out | DISTRIBUTION | DEVICE | MANUAL | 2018-07-06 20:15 | COMPLETED |  | 2018-07-06 15:15 | 2018-07-06 18:32 | 2018-07-06 18:35 | -117.23 | 45.3769
4W8 | 1885283 | CPCC | CPCC1216503 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_365180_163440126 | 2018 | Before | 2018-07-16 21:27 | 2018-07-16 23:04 | 3 | 291.05 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE ONLY -UG ( NO CAUSE FOUND) |  |  |  | SOURCE: Blown XFRM fuse. No cause found. Refused. Service is on. | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2018-07-17 04:30 | COMPLETED |  | 2018-07-16 21:27 | 2018-07-17 04:37 | 2018-07-17 04:40 | -117.1335 | 45.3401
4W8 | 1885393 | CPCC | CPCC1216537 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_054900_69740133 | 2018 | Before | 2018-07-17 08:05 | 2018-07-17 09:28 | 3 | 248.8 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown transformer fuse, no cause found | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2018-07-17 10:45 | COMPLETED |  | 2018-07-17 08:05 | 2018-07-17 09:57 | 2018-07-17 10:00 | -117.2205 | 45.4259
4W8 | 1890627 | CPCC | CPCC1219365 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_280600_579890077 | 2018 | Before | 2018-08-04 10:48 | 2018-08-04 11:44 | 1 | 55.967 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Open Fuse, No Cause Found, refused and restored | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2018-08-04 14:00 | COMPLETED |  | 2018-08-04 10:48 | 2018-08-04 18:05 | 2018-08-04 18:10 | -117.2087 | 45.4504
4W8 | 1895571 | CPCC | CPCC1222028 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_309211_933390268 | 2018 | Before | 2018-08-23 10:06 | 2018-08-23 10:33 | 1 | 26.783 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: | DISTRIBUTION | CUSTOMER | AUTO | 2018-08-23 12:45 | COMPLETED |  | 2018-08-23 10:06 | 2018-08-23 10:33 | 2018-08-23 10:35 | -117.2311 | 45.3557
4W8 | 1896021 | CPCC | CPCC1222303 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_110900_69740201 | 2018 | Before | 2018-08-25 05:32 | 2018-08-25 11:00 | 5 | 1640.167 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown line fuse, patrolled and did not find a cause. Refused and customers are back on. | DISTRIBUTION | DEVICE | MANUAL | 2018-08-25 12:00 | COMPLETED |  | 2018-08-25 05:32 | 2018-08-25 11:31 | 2018-08-25 11:35 | -117.1673 | 45.4102
4W8 | 1896327 | CPCC | CPCC1222570 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_330600_579890067 | 2018 | Before | 2018-08-26 17:26 | 2018-08-26 22:16 | 32 | 9284.267 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman refused tap line ok. Cause is unknown. | DISTRIBUTION | DEVICE | MANUAL | 2018-08-26 23:00 | COMPLETED |  | 2018-08-26 17:26 | 2018-08-27 00:45 | 2018-08-27 00:45 | -117.2092 | 45.4353
4W8 | 1897672 | CPCC | CPCC1225408 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_240200_1560098377 | 2018 | Before | 2018-08-31 22:42 | 2018-09-01 02:44 | 1 | 241.717 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman replaced blown transformer fuse, no cause found | DISTRIBUTION | CUSTOMER | MANUAL | 2018-09-01 05:00 | COMPLETED |  | 2018-08-31 22:42 | 2018-09-01 08:15 | 2018-09-01 08:15 | -117.1461 | 45.3704
4W8 | 1901329 | CPCC | CPCC1227774 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_030003_1560029384 | 2018 | Before | 2018-09-17 06:55 | 2018-09-17 08:15 | 10 | 795.5 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Line Fuse Open, Serviceman patrolled and found no cause, refused and restored | DISTRIBUTION | DEVICE | AUTO | 2018-09-17 09:30 | COMPLETED |  | 2018-09-17 06:56 | 2018-09-17 15:39 | 2018-09-17 15:40 | -117.1887 | 45.4124
4W8 | 1903360 | CPCC | CPCC1230905 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_118501_789340121 | 2018 | Before | 2018-09-26 19:31 | 2018-09-26 20:49 | 1 | 77.883 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown transformer fuse, No Cause found, re- fused and restored | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2018-09-26 22:45 | COMPLETED |  | 2018-09-26 19:31 | 2018-09-27 06:47 | 2018-09-27 06:50 | -117.2755 | 45.4037
4W8 | 1908305 | CPCC | CPCC1234082 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_264800_163440183 | 2018 | Before | 2018-10-18 15:42 | 2018-10-18 16:41 | 1 | 59.7 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2018-10-18 18:15 | COMPLETED |  | 2018-10-18 15:42 | 2018-10-18 16:42 | 2018-10-18 16:45 | -117.1568 | 45.3651
4W8 | 1909687 | CPCC | CPCC1234943 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_200800_101040176 | 2018 | Before | 2018-10-25 18:16 | 2018-10-25 19:45 | 1 | 89.183 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | SOURCE: Crew to Change B/O Transformer | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2018-10-25 18:16 | 2018-10-25 19:54 | 2018-10-25 19:55 | -117.2283 | 45.3783
4W8 | 1910536 | CPCC | CPCC1235622 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_234302_163440222 | 2018 | Before | 2018-10-30 07:27 | 2018-10-30 08:05 | 1 | 38.05 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: refused | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2018-10-30 10:00 | COMPLETED |  | 2018-10-30 07:28 | 2018-10-30 08:15 | 2018-10-30 08:20 | -117.158 | 45.3716
4W8 | 1911242 | CPCC | CPCC1236004 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_019202__4348717 | 2018 | Before | 2018-11-02 09:08 | 2018-11-02 11:34 | 2 | 190.966 | 0 | 0 | 2 | Y | N | N | N | N |  | INTERFERENCE | DIG-IN (NON-PACIFICORP PERSONNEL) |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: found fuse open at 019202 | DISTRIBUTION | DEVICE | MANUAL | 2018-11-02 18:45 | COMPLETED |  | 2018-11-02 09:09 | 2018-11-02 16:25 | 2018-11-02 16:30 | -117.251 | 45.4142
4W8 | 1912281 | CPCC | CPCC1236934 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_202700_101040255 | 2018 | Before | 2018-11-07 20:57 | 2018-11-08 08:01 | 8 | 5310.933 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: | DISTRIBUTION | DEVICE | MANUAL | 2018-11-08 09:30 | COMPLETED |  | 2018-11-07 20:57 | 2018-11-08 08:41 | 2018-11-08 08:45 | -117.2245 | 45.3778
4W8 | 1919884 | CPCC | CPCC1247671 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_198900_101040272 | 2018 | After | 2018-12-14 07:30 | 2018-12-14 08:21 | 2 | 101.8 | 0 | 0 | 1 | Y | N | N | N | Y | OR Consolidated 12-14-2018 | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown transformer, no cause found | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2018-12-14 10:00 | COMPLETED |  | 2018-12-14 07:30 | 2018-12-14 08:58 | 2018-12-14 09:00 | -117.2321 | 45.3798
4W8 | 1919976 | CPCC | CPCC1248280 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | TR_295600_304570113 | 2018 | After | 2018-12-14 11:50 | 2018-12-14 14:05 | 3 | 405.15 | 0 | 0 | 1 | Y | N | N | N | Y | OR Consolidated 12-14-2018 | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: serviceman found tree thru line at 297701 | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2018-12-14 16:30 | COMPLETED |  | 2018-12-14 11:50 | 2018-12-14 14:33 | 2018-12-14 14:35 | -117.2159 | 45.2738
4W8 | 1928066 | CPCC | CPCC1256502 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_299920_304570087 | 2019 | After | 2019-01-17 08:44 | 2019-01-17 10:04 | 10 | 805.333 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Blown line line fuse, caused by B/O cut out | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2019-01-17 08:45 | 2019-01-17 12:34 | 2019-01-17 12:35 | -117.208 | 45.2782
4W8 | 1935071 | CPCC | CPCC1261308 | PP | OR | ENTERPRISE | ENTERPRISE (OR) | OH_330502_579890068 | 2019 | After | 2019-02-12 10:37 | 2019-02-12 15:02 | 7 | 1853.367 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: Broken jumper, need 3rd man, will come from pemdleton | DISTRIBUTION | DEVICE | MANUAL | 2019-02-12 16:00 | COMPLETED |  | 2019-02-12 10:37 | 2019-02-12 15:53 | 2019-02-12 15:55 | -117.2076 | 45.4338
5A15 | 602711 | CPCC | CPCC395838 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_215710_626300456 | 2007 | Before | 2007-01-19 13:02 | 2007-01-19 13:58 | 3 | 167.2 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: svcman replaced b/o trf cutout fuse and customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 602712 | CPCC | CPCC395840 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_214780_626300421 | 2007 | Before | 2007-01-19 13:23 | 2007-01-19 13:58 | 1 | 34.7 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: associate to outage #395838, b/o connectivity in cadops. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 599132 | CPCC | CPCC392584 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | LINECUT-21898 | 2007 | Before | 2007-01-07 11:04 | 2007-01-07 14:55 | 1 | 230.667 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Fuse open on pole 092600. neutral swung up and hit phase. Moved neutral down. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9362 | 46.1943
5A15 | 604203 | CPCC | CPCC399266 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_167002_543460377 | 2007 | Before | 2007-02-12 18:47 | 2007-02-12 21:57 | 1 | 190.117 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Triplex in tree had to replace broke neutral | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 598867 | CPCC | CPCC392573 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_093680_543460299 | 2007 | Before | 2007-01-07 09:48 | 2007-01-07 14:50 | 1 | 301.883 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Associated with outage 392573. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 598553 | CPCC | CPCC391484 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_218601_626300520 | 2007 | Before | 2007-01-02 12:42 | 2007-01-02 15:25 | 1 | 163.717 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: svcman made repairs to burnt up service wire that was caused by tree damage. Customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 619365 | CPCC | CPCC421226 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_091500_543460309 | 2007 | Before | 2007-06-07 12:20 | 2007-06-07 13:11 | 6 | 306.4 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: svcman replaced a blown trf cutout fuse. cause is unknown. customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 612458 | CPCC | CPCC414180 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2007 | Before | 2007-04-12 03:00 | 2007-04-12 05:49 | 1709 | 288165.883 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | TRANSMISSION REQUESTED |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Open CB for emergency switching for compass 18191 to repair 2 different spans on the 115Kv. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 611507 | CPCC | CPCC415786 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_216607_626300479 | 2007 | Before | 2007-04-28 08:50 | 2007-04-28 09:45 | 1 | 55 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: cut out bad | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 607150 | CPCC | CPCC410519 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_216202_626300613 | 2007 | Before | 2007-03-16 16:02 | 2007-03-16 16:35 | 1 | 33.233 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: Serviceman replaced a B/O secondary connection at the transformer, customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 610016 | CPCC | CPCC413768 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2007 | Before | 2007-04-09 18:27 | 2007-04-09 22:58 | 1709 | 464392.267 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE | WEATHER | LIGHTNING | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Static line down at Lewis Clark Sub | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 608230 | CPCC | CPCC410995 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | LINECUT-22651 | 2007 | Before | 2007-03-20 09:46 | 2007-03-20 11:08 | 4 | 329.8 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: crew de-energized line so they could put primary neut back up. associate to outage #410986. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.965 | 46.1812
5A15 | 644865 | CPCC | CPCC452940 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2007 | Before | 2007-11-12 06:12 | 2007-11-13 01:57 | 1748 | 1239341.8 | 0 | 0 | 6 | Y | N | N | N | Y | 685 - 2007-11-12 to 2007-11-12 OR Clatsop/Astoria | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | PROSPER: wire down over several locations. Made repairs and customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 646915 | CPCC | CPCC450060 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_217602_626300402 | 2007 | Before | 2007-10-25 12:32 | 2007-10-25 13:29 | 1 | 56.967 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: svcman replaced bad connector at the trf and customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 644470 | CPCC | CPCC446627 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_083904_825180461 | 2007 | Before | 2007-10-16 15:44 | 2007-10-16 18:07 | 1 | 143.433 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: changed out service & connections | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 648944 | CPCC | CPCC464158 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_166980_543460345 | 2007 | Before | 2007-12-06 13:14 | 2007-12-07 20:54 | 1 | 1900.3 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 648952 | CPCC | CPCC464173 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_090600_543460289 | 2007 | Before | 2007-12-06 14:20 | 2007-12-07 20:52 | 1 | 1832.467 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 648954 | CPCC | CPCC464177 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_050042_825180506 | 2007 | Before | 2007-12-06 14:25 | 2007-12-07 20:52 | 1 | 1827.183 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 648958 | CPCC | CPCC464182 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_165900_543460362 | 2007 | Before | 2007-12-06 14:32 | 2007-12-07 20:52 | 2 | 3639.433 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 648972 | CPCC | CPCC464266 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_274801_915350405 | 2007 | Before | 2007-12-06 18:34 | 2007-12-07 20:52 | 1 | 1577.45 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 644580 | CPCC | CPCC452583 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | Line Cut-26024 | 2007 | Before | 2007-11-12 04:42 | 2007-11-12 06:00 | 1748 | 135324.333 | 0 | 0 | 1 | Y | N | N | N | Y | 685 - 2007-11-12 to 2007-11-12 OR Clatsop/Astoria | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Outage due to loss of Transmission. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9095 | 46.1516
5A15 | 648263 | CPCC | CPCC449543 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_165080_543460375 | 2007 | Before | 2007-10-23 07:43 | 2007-10-23 15:53 | 1 | 490.333 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | PROSPER: crew needed for bad neut on an ug svc. repairs complete and customer back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 647086 | CPCC | CPCC454221 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_091500_543460309 | 2007 | Before | 2007-11-12 15:53 | 2007-11-13 13:19 | 1 | 1286.033 | 0 | 0 | 1 | Y | N | N | N | Y | 685 - 2007-11-12 to 2007-11-12 OR Clatsop/Astoria | WEATHER | WIND | WEATHER | WIND | SECONDARY CONDUCTOR OH |  |  |  |  | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 647091 | CPCC | CPCC454242 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_165504_1580286052 | 2007 | Before | 2007-11-12 15:10 | 2007-11-13 05:13 | 31 | 26157.283 | 0 | 0 | 1 | Y | N | N | N | Y | 685 - 2007-11-12 to 2007-11-12 OR Clatsop/Astoria | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Wire down, made repairs and customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9287 | 46.1777
5A15 | 646376 | CPCC | CPCC446389 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_172580_1580005238 | 2007 | Before | 2007-10-14 11:30 | 2007-10-14 13:21 | 1 | 111.117 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: bad secondary conn at transformer | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 649234 | CPCC | CPCC459229 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2007 | Before | 2007-12-02 12:31 | 2007-12-06 08:08 | 1745 | 6023901.515 | 0 | 0 | 29 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 649236 | CPCC | CPCC461006 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2007 | Before | 2007-12-02 20:51 | 2007-12-06 08:44 | 710 | 3391310.85 | 0 | 0 | 11 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Outage due to loss of transmission | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 650075 | CPCC | CPCC454842 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_082906_825180280 | 2007 | Before | 2007-11-14 15:53 | 2007-11-14 16:02 | 118 | 1052.167 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | INSULATOR OH |  |  |  | PROSPER: crew took 10 min outage to make repairs to primary wire that came off of insulator. pahse very close to system neut. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9551 | 46.1989
5A15 | 642941 | CPCC | CPCC444223 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_090801_543460281 | 2007 | Before | 2007-09-30 12:32 | 2007-09-30 16:35 | 1 | 242.533 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | OTHER, KNOWN CAUSE |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: changed out OH service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 643406 | CPCC | CPCC443371 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2007 | Before | 2007-09-24 13:30 | 2007-09-24 14:58 | 696 | 61340.8 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | SPLICE B/O OH |  |  |  | PROSPER: CB opened at sub to allow crew to put wire back up that had come down when a sleeve failed after log truck tore down wire at a different location on the same circuit. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 643509 | CPCC | CPCC444785 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_215982_626300442 | 2007 | Before | 2007-10-03 11:35 | 2007-10-03 12:17 | 10 | 419.833 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | TRANSFORMER PADMOUNT/SUBMERSIBLE UG |  |  |  | PROSPER: crew replacing leaking pad mount trf. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 643149 | CPCC | CPCC443355 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2007 | Before | 2007-09-24 12:55 | 2007-09-24 15:00 | 1725 | 149596.916 | 0 | 0 | 3 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: log truck tore down primary line. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 655991 | CPCC | CPCC465061 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_223500_626300667 | 2007 | Before | 2007-12-08 13:06 | 2007-12-08 13:49 | 1 | 43.117 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  |  | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 650942 | CPCC | CPCC456923 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_167002_543460377 | 2007 | Before | 2007-11-25 14:01 | 2007-11-25 15:03 | 5 | 313.333 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 653457 | CPCC | CPCC464822 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_088902_825180433 | 2007 | Before | 2007-12-08 07:40 | 2007-12-08 09:49 | 1 | 129.083 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  |  | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 656851 | CPCC | CPCC465172 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_222603_626300665 | 2007 | Before | 2007-12-08 16:06 | 2007-12-08 20:02 | 1 | 235.833 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Repaired broken neutral | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 656875 | CPCC | CPCC466827 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_165902_543460235 | 2007 | Before | 2007-12-19 09:30 | 2007-12-19 11:29 | 1 | 119.017 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: crew made repairs to bad neut at the weatherhead and customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 651864 | CPCC | CPCC454977 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_188841_825180533 | 2007 | Before | 2007-11-15 19:57 | 2007-11-15 22:53 | 6 | 1060.5 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Crew made repairs due to tree through lines | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.964 | 46.1811
5A15 | 652686 | CPCC | CPCC454595 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_167000_543460376 | 2007 | Before | 2007-11-13 09:41 | 2007-11-13 15:00 | 1 | 319.05 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND | WEATHER | WIND | SECONDARY CONDUCTOR OH |  |  |  |  | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 655226 | CPCC | CPCC467312 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_079780_825180489 | 2007 | Before | 2007-12-20 15:26 | 2007-12-20 16:30 | 1 | 63.767 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | PROSPER: svcman reports bad ug service wire. crew installed a service saver and customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 653135 | CPCC | CPCC464108 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_184341_825180536 | 2007 | Before | 2007-12-06 11:17 | 2007-12-07 20:54 | 1 | 2017.317 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 653136 | CPCC | CPCC464111 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_188600_825180534 | 2007 | Before | 2007-12-06 11:18 | 2007-12-07 20:54 | 2 | 4033.833 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9657 | 46.1792
5A15 | 653148 | CPCC | CPCC464149 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_165904_543460359 | 2007 | Before | 2007-12-06 12:28 | 2007-12-07 20:54 | 1 | 1946.333 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 653150 | CPCC | CPCC464153 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_058080_825180377 | 2007 | Before | 2007-12-06 12:38 | 2007-12-07 20:54 | 1 | 1936.417 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 656554 | CPCC | CPCC465112 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_223500_626300667 | 2007 | Before | 2007-12-08 14:10 | 2007-12-08 20:05 | 1 | 354.4 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  |  | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 656555 | CPCC | CPCC465113 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_213500_626300561 | 2007 | Before | 2007-12-08 14:10 | 2007-12-08 17:40 | 1 | 210.067 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  |  | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 652313 | CPCC | CPCC463603 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_223500_626300667 | 2007 | Before | 2007-12-05 17:46 | 2007-12-06 07:53 | 1 | 847.1 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 653158 | CPCC | CPCC464224 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_222603_626300665 | 2007 | Before | 2007-12-06 16:20 | 2007-12-07 20:52 | 1 | 1712.483 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 654862 | CPCC | CPCC464962 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_213500_626300561 | 2007 | Before | 2007-12-08 09:57 | 2007-12-08 13:49 | 1 | 232.8 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  |  | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 654863 | CPCC | CPCC464963 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_214604_626300532 | 2007 | Before | 2007-12-08 09:59 | 2007-12-08 13:49 | 1 | 230.183 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  |  | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 656136 | CPCC | CPCC468969 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_165608_543460213 | 2007 | Before | 2007-12-30 17:24 | 2007-12-30 18:25 | 9 | 545.55 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: blown transformer fuse | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 651507 | CPCC | CPCC464297 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_223500_626300667 | 2007 | Before | 2007-12-06 20:28 | 2007-12-07 20:52 | 1 | 1464.117 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 654864 | CPCC | CPCC464965 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_088902_825180433 | 2007 | Before | 2007-12-08 10:04 | 2007-12-08 10:05 | 0 | 0 | 7 | 6.767 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  |  | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 655296 | CPCC | CPCC468838 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_222603_626300665 | 2007 | Before | 2007-12-29 13:59 | 2007-12-29 18:38 | 3 | 837.7 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | PROSPER: call crew to replace transformer bank | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 656600 | CPCC | CPCC466810 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_217510_1580146502 | 2007 | Before | 2007-12-19 08:10 | 2007-12-19 10:49 | 1 | 159.35 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | PROSPER: crew replaced trf that was damaged in wind storm earlier this month. customers service entrance was damaged as well. they are still in service but will be required to get repairs made. local district to note this account. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 654076 | CPCC | CPCC466528 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_054104_825180363 | 2007 | Before | 2007-12-17 10:33 | 2007-12-17 11:33 | 1 | 60.35 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: svcman replaced bad connector at the weatherhead and customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 652399 | CPCC | CPCC454555 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_068210_825180409 | 2007 | Before | 2007-11-13 07:57 | 2007-11-13 11:47 | 1 | 230.117 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND | WEATHER | WIND | SECONDARY CONDUCTOR OH |  |  |  |  | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 652406 | CPCC | CPCC454572 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_222500_626300669 | 2007 | Before | 2007-11-13 08:55 | 2007-11-13 14:51 | 1 | 355.8 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  |  | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 652409 | CPCC | CPCC454576 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_215604_626300476 | 2007 | Before | 2007-11-13 09:02 | 2007-11-13 14:54 | 1 | 352.467 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND | WEATHER | WIND | SECONDARY CONDUCTOR OH |  |  |  |  | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 653240 | CPCC | CPCC454685 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_091701_543460282 | 2007 | Before | 2007-11-13 16:52 | 2007-11-13 18:36 | 1 | 103.467 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: bad connector | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 652854 | CPCC | CPCC464059 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_214780_626300421 | 2007 | Before | 2007-12-06 09:18 | 2007-12-07 20:54 | 1 | 2135.667 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 652860 | CPCC | CPCC464072 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_095002_543460269 | 2007 | Before | 2007-12-06 09:33 | 2007-12-07 10:10 | 2 | 2955.167 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 652865 | CPCC | CPCC464084 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_091605_543460210 | 2007 | Before | 2007-12-06 08:54 | 2007-12-06 10:12 | 652 | 51095.067 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: crew put wire back up. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9373 | 46.1939
5A15 | 652877 | CPCC | CPCC464198 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_166502_543460215 | 2007 | Before | 2007-12-06 14:58 | 2007-12-07 20:52 | 1 | 1794.133 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 655409 | CPCC | CPCC464523 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_223500_626300667 | 2007 | Before | 2007-12-07 13:13 | 2007-12-08 15:12 | 1 | 1558.433 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 655411 | CPCC | CPCC464526 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_165904_543460359 | 2007 | Before | 2007-12-07 13:17 | 2007-12-08 15:11 | 1 | 1554.117 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 650807 | CPCC | CPCC458490 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2007 | Before | 2007-12-02 10:56 | 2007-12-02 11:32 | 1745 | 62412.833 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE | TREES | TREE - NON-PREVENTABLE | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: tree on transmission line | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 655423 | CPCC | CPCC464543 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_090600_543460289 | 2007 | Before | 2007-12-07 13:26 | 2007-12-08 15:11 | 1 | 1545.45 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 655426 | CPCC | CPCC464547 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_088902_825180433 | 2007 | Before | 2007-12-07 13:27 | 2007-12-08 15:11 | 1 | 1544.1 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 654213 | CPCC | CPCC469328 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_222603_626300665 | 2008 | Before | 2008-01-02 09:14 | 2008-01-02 14:12 | 3 | 894.95 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | PROSPER: refer to outage #469326, for crew response times. crew replaced bad order trf and cutout. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 654612 | CPCC | CPCC465920 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_086900_825180441 | 2007 | Before | 2007-12-12 09:35 | 2007-12-12 10:46 | 1 | 71.033 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | OTHER, KNOWN CAUSE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: svcman tightened connections in the secondary hand hole, tightened connections in the meterbase and then tested voltage to be good with the beast and all is fine. customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 655863 | CPCC | CPCC468947 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_222603_626300665 | 2007 | Before | 2007-12-30 10:52 | 2007-12-30 14:48 | 3 | 706.7 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | OVERLOAD |  |  | TRANSFORMER OH |  |  |  | PROSPER: cust faulted secondary shorted transformer bank , need replaced | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 656747 | CPCC | CPCC470325 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2008 | Before | 2008-01-04 05:55 | 2008-01-04 06:38 | 1746 | 75223.5 | 0 | 0 | 1 | Y | N | N | N | Y | 708 - 2008-01-04 to 2008-01-04 OR Clatsop | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 652582 | CPCC | CPCC464025 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_089780_543460279 | 2007 | Before | 2007-12-06 07:42 | 2007-12-06 07:58 | 1 | 16.033 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 652586 | CPCC | CPCC464035 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_052104_825180336 | 2007 | Before | 2007-12-06 08:10 | 2007-12-07 20:54 | 1 | 2204.367 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 652587 | CPCC | CPCC464036 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_216401_626300601 | 2007 | Before | 2007-12-06 08:14 | 2007-12-07 20:54 | 1 | 2200.283 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 652589 | CPCC | CPCC464040 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_166500_543460351 | 2007 | Before | 2007-12-06 08:16 | 2007-12-07 20:54 | 1 | 2198.133 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 652596 | CPCC | CPCC463795 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_216607_626300479 | 2007 | Before | 2007-12-05 20:09 | 2007-12-06 07:59 | 1 | 710.067 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 654686 | CPCC | CPCC467513 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_220604_626300662 | 2007 | Before | 2007-12-22 12:31 | 2007-12-22 13:21 | 3 | 151.3 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: broken transformer cutout jumper | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 670522 | CPCC | CPCC490921 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_095201_543460255 | 2008 | Before | 2008-03-03 20:51 | 2008-03-03 23:00 | 5 | 647.25 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: cut out had to be replaced | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9295 | 46.188
5A15 | 672990 | CPCC | CPCC496032 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_214780_626300421 | 2008 | Before | 2008-04-14 14:25 | 2008-04-14 14:35 | 1 | 10.667 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | PROSPER: This was taken care of by serviceman already. Cust supposedly called in at 1pm and also called serviceman at same time. Tag just now coming through? Replaced connestors at transformer. Cust back in power. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 670972 | CPCC | CPCC493324 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | Line Cut-28351 | 2008 | Before | 2008-03-22 20:56 | 2008-03-23 01:43 | 2 | 573.167 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | INTERFERENCE | VEHICLE ACCIDENT | POLE OH |  |  |  | PROSPER: Car/ pole accident, tap line cut clear by serviceman. Mills, Dick, Karns, Kaplan to assist, Heidi Barendse & Denning Jackson to Flag. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9343 | 46.1926
5A15 | 670973 | CPCC | CPCC493325 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | MAB217900_626300452 | 2008 | Before | 2008-03-22 22:33 | 2008-03-23 00:47 | 1027 | 137327.017 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | INTERFERENCE | VEHICLE ACCIDENT | POLE OH |  |  |  | PROSPER: outage # 493324 is for the car hit pole, this outage is for deenergizing partial feeder to make repairs. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9252 | 46.1688
5A15 | 675392 | CPCC | CPCC498134 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_218500_626300523 | 2008 | Before | 2008-04-27 15:52 | 2008-04-27 16:47 | 1 | 54.983 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: cut door bad | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 670819 | CPCC | CPCC495607 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_214781_626300426 | 2008 | Before | 2008-04-11 17:04 | 2008-04-11 20:52 | 14 | 3193.4 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | PROSPER: Blown elbow, and B/O Transformer, replaced same. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 674526 | CPCC | CPCC497119 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_216706_626300475 | 2008 | Before | 2008-04-20 23:05 | 2008-04-20 23:53 | 6 | 286.1 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: blown transformer fuse , no cause found | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 669434 | CPCC | CPCC491443 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_088800_825180428 | 2008 | Before | 2008-03-07 17:40 | 2008-03-07 18:45 | 1 | 65.083 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 666727 | ORSD | ORSD486470 | PP | OR | CLATSOP (ASTORIA) | WARRENTON |  | 2008 | Before | 2008-01-29 04:44 | 2008-01-29 07:41 | 666 | 117882 | 0 | 0 | 1 | Y | Y | Y | Y | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  |  | 375 |  |  | PROSPER: burnt off B phase jumper on transmission line at 4:44 am . svcman opened breakers at the sub at 7:41 am (this is when all of the A & C phase customers were de-energized. crew making repairs to burnt jumper. P44577 | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 666379 | CPCC | CPCC487443 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2008 | Before | 2008-02-04 10:48 | 2008-02-04 11:13 | 1740 | 43819 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 679683 | CPCC | CPCC505593 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_050080_825180348 | 2008 | Before | 2008-06-10 09:08 | 2008-06-10 13:10 | 1 | 242.1 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: finishing appointment, will call when enroute. left message at 1147. Serviceman found old trip olink fuse that was rotten. customer back in full service | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 679684 | CPCC | CPCC505594 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_067540_825180391 | 2008 | Before | 2008-06-10 09:09 | 2008-06-10 13:11 | 1 | 241.85 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: finishing appointment, will call when enroute. Serviceman found old trip olink fuse that was rotten. customer back in full service | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 663555 | CPCC | CPCC484812 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2008 | Before | 2008-01-29 07:41 | 2008-01-29 09:00 | 1740 | 138098 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF SUBSTATION |  |  | POWER TRANSFORMER SUB |  |  |  | PROSPER: Burnt off B phase jumper on transmission line at 4:44 am . svcman opened breakers at sub at 7:41 am (this is when all of the A & C phase customers were de-energized. crew making repairs to burnt jumper. Changed Off time 0444 to 0741. P44577 | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 663556 | CPCC | CPCC485033 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2008 | Before | 2008-01-29 09:54 | 2008-01-29 10:21 | 1740 | 46980 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF SUBSTATION |  |  | POWER TRANSFORMER SUB |  |  |  | PROSPER: Power transformer issue. Changed OFF from 0645 to 0954. P44577 | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 659918 | CPCC | CPCC480621 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_093401_1580085309 | 2008 | Before | 2008-01-18 10:54 | 2008-01-18 11:48 | 15 | 798.25 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | LIGHTNING ARRESTER OH |  |  |  | PROSPER: crew took outage to replace bad arrestor. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9332 | 46.1918
5A15 | 657000 | CPCC | CPCC465543 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_221601_626300410 | 2007 | Before | 2007-12-10 10:06 | 2007-12-10 11:53 | 1 | 107.367 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: svcman has restored power. broken neutral. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 659612 | CPCC | CPCC481883 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_217402_626300593 | 2008 | Before | 2008-01-23 10:20 | 2008-01-23 12:26 | 1 | 125.767 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: svcman replaced all secondary connections at the trf and customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 657102 | CPCC | CPCC464728 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_222603_626300665 | 2007 | Before | 2007-12-07 19:26 | 2007-12-08 15:11 | 1 | 1185.8 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  |  | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 657545 | CPCC | CPCC469026 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_222603_626300665 | 2007 | Before | 2007-12-31 11:07 | 2007-12-31 15:21 | 3 | 763.9 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | PROSPER: crew replaced bad trf. customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 658084 | CPCC | CPCC478704 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_188841_825180533 | 2008 | Before | 2008-01-11 11:15 | 2008-01-11 13:25 | 6 | 784.1 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | OTHER UTILITY/CONTRACTOR |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: trackhoe bumped primary line and caused the line fuse to blow. crew reports line was not damaged they replaced the fuse and all customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.964 | 46.1811
5A15 | 698675 | CPCC | CPCC525883 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_094500_543460293 | 2008 | Before | 2008-10-07 06:14 | 2008-10-07 09:43 | 1 | 208.55 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: fp 094500 fuse blew. Refused and holding. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 702399 | CPCC | CPCC554431 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_221404_626300679 | 2009 | Before | 2009-02-25 18:20 | 2009-02-25 21:09 | 1 | 169.15 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | DETERIORATION OR ROTTING | CUT-OUT B/O OH |  |  |  | PROSPER: Crew replaced arcing cut out | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 696375 | CPCC | CPCC522788 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_216300_626300607 | 2008 | Before | 2008-09-16 08:35 | 2008-09-16 10:24 | 1 | 109.283 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: Replaced B/O connector at weatherhead. Full power restored. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 700874 | CPCC | CPCC531077 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | Line Cut-31987 | 2008 | Before | 2008-11-09 16:24 | 2008-11-09 20:05 | 5 | 1103.833 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: Bad underground. Closed at NO 211780. Customers are back on. Repairs to be made later. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9346 | 46.1661
5A15 | 700170 | CPCC | CPCC528463 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | Line Cut-31732 | 2008 | Before | 2008-10-27 20:23 | 2008-10-27 22:30 | 722 | 91850.433 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: Burnt open jumper on pole 274804. Made repairs and customers are back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9095 | 46.1536
5A15 | 700172 | CPCC | CPCC528483 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2008 | Before | 2008-10-27 21:29 | 2008-10-27 22:30 | 1031 | 63750.167 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: Took outage to make repairs to burnt open jumper on pole 274804. Outage 528477 contains original calls. Repairs made, closed breaker and customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 692551 | CPCC | CPCC516767 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_053404_825180305 | 2008 | Before | 2008-08-12 09:41 | 2008-08-12 13:29 | 1 | 227.667 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | PROSPER: b/o transformer. crew replaced and customer back in service | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 703486 | CPCC | CPCC555747 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_189841_825180517 | 2009 | Before | 2009-03-04 07:46 | 2009-03-04 10:01 | 1 | 135.167 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: Crew replaced the B/O cutouts on pole# 189841, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 704673 | CPCC | CPCC551566 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_222610_1580311775 | 2009 | Before | 2009-02-08 00:03 | 2009-02-08 01:32 | 8 | 704.8 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Line fuse blew. Patrolled line and did not find anything. Refused and customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9143 | 46.1643
5A15 | 703538 | CPCC | CPCC535286 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | Line Cut-32364 | 2008 | Before | 2008-12-13 14:24 | 2008-12-13 15:34 | 1 | 70.083 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9651 | 46.1813
5A15 | 704091 | CPCC | CPCC548493 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_067120_825180406 | 2009 | Before | 2009-01-10 18:04 | 2009-01-10 18:51 | 2 | 93.767 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: Pole fire, need to replace cutout and glass. See outage 548483 for arrival times. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 702928 | CPCC | CPCC554547 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | Line Cut-33665 | 2009 | Before | 2009-02-26 07:06 | 2009-02-26 10:35 | 679 | 141843.1 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | SPLICE B/O OH |  |  |  | PROSPER: Line down outside sub. Splice failed 8 spans from sub. Crew relaced and all customers back in service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9106 | 46.164
5A15 | 702929 | CPCC | CPCC554548 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2009 | Before | 2009-02-26 08:40 | 2009-02-26 10:35 | 1083 | 124924.05 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | B/O EQUIPMENT | SPLICE B/O OH |  |  |  | PROSPER: Breaker was open at 08:40. Earlier calls for breaker opperations in cadops makes time for outage show earlier. Associate to 554547. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 705766 | CPCC | CPCC549911 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_187800_825180537 | 2009 | Before | 2009-01-21 14:18 | 2009-01-21 15:04 | 1 | 46.533 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman founda blown line fuse and from talking to the customer was told that a crane had bumped line ealier in the day. Nothing was damaged so he refused and it held. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 704573 | CPCC | CPCC555992 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_095006_543460257 | 2009 | Before | 2009-03-06 09:03 | 2009-03-06 09:50 | 47 | 2223.1 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | CONSTRUCTION |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Crew took an outage to install a bird perch. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9291 | 46.1849
5A15 | 709037 | CPCC | CPCC557164 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | MAB217900_626300452 | 2009 | Before | 2009-03-16 03:06 | 2009-03-16 07:19 | 1048 | 189541.617 | 0 | 0 | 2 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | INTERFERENCE | VEHICLE ACCIDENT | POLE OH |  |  |  | PROSPER: Car hit pole and broke pole. Open SW 5A120 to make emergency repairs. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9252 | 46.1688
5A15 | 689618 | CPCC | CPCC519528 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_089882_825180265 | 2008 | Before | 2008-08-24 22:02 | 2008-08-24 23:55 | 7 | 790.883 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | OTHER UG (EXPLAIN IN COMMENTS FIELD) |  |  |  | PROSPER: car-pedistal refuse padmount | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 726505 | CPCC | CPCC563456 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2009 | Before | 2009-05-02 21:24 | 2009-05-02 22:08 | 1109 | 48352.4 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | INTENTIONAL TO CLEAR TROUBLE |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: Assurance to repair jumper on line regulator. Verify issue, changed OFF time from 1813 to 2124. P44577. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 724166 | CPCC | CPCC567749 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_054008_825180365 | 2009 | Before | 2009-06-01 08:30 | 2009-06-01 10:19 | 1 | 108.8 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Per serviceman: service wire burned in two (unknown cause). Serviceman replaced service wire. customer back in service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 722248 | CPCC | CPCC563457 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_091605_543460210 | 2009 | Before | 2009-05-02 18:14 | 2009-05-02 23:30 | 152 | 47999.067 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: wire down | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9373 | 46.1939
5A15 | 722251 | CPCC | CPCC563480 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_088802_825180426 | 2009 | Before | 2009-05-02 18:11 | 2009-05-02 23:30 | 507 | 161834.4 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: wire down | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9439 | 46.197
5A15 | 727068 | CPCC | CPCC564770 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_215902_626300447 | 2009 | Before | 2009-05-12 06:44 | 2009-05-12 08:24 | 5 | 500.75 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: Burnt up cut-out. Crew to replace. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 722758 | CPCC | CPCC570579 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_068110_825180408 | 2009 | Before | 2009-06-10 17:14 | 2009-06-10 20:38 | 1 | 204.283 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Going to take an hour to get here. Bad neutral on secondary service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 720382 | CPCC | CPCC565312 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_082701_825180462 | 2009 | Before | 2009-05-16 10:14 | 2009-05-16 12:25 | 1 | 131.3 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: blown transformer fuse, cause unknown | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 717604 | CPCC | CPCC541780 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_068110_825180408 | 2008 | Before | 2008-12-24 17:03 | 2008-12-24 17:45 | 3 | 126.35 | 0 | 0 | 1 | Y | N | N | N | N |  | ENVIRONMENT | FIRE/SMOKE (NOT DUE TO FAULTS) |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Transformer fuse blew due to a structure fire. Serviceman cut secondary in clear and refused trasnformer. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 716808 | CPCC | CPCC541348 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_215904_1580006860 | 2008 | Before | 2008-12-24 06:53 | 2008-12-24 10:04 | 31 | 5937.533 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | LOAD BREAK ELBOW UG |  |  |  | PROSPER: crew to switch out bad ug pistol | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9298 | 46.1694
5A15 | 715652 | CPCC | CPCC538637 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_187800_825180537 | 2008 | Before | 2008-12-21 14:24 | 2008-12-21 16:27 | 1 | 122.067 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | SNOW, SLEET AND BLIZZARD | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Serviceman made repairs to what they could get to. Several trees down in area and park is closed for the winter. District will make orders to go back for final repairs. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 719308 | CPCC | CPCC565122 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_164600_543460367 | 2009 | Before | 2009-05-14 12:33 | 2009-05-14 14:06 | 1 | 92.883 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | PROSPER: Serviceman replaced a deteriorated secondary connector at xfmr. Customer back in service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 716492 | CPCC | CPCC544710 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_217602_626300402 | 2008 | Before | 2008-12-31 20:24 | 2008-12-31 21:08 | 1 | 43.4 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 716493 | CPCC | CPCC544714 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_217603_1580006301 | 2008 | Before | 2008-12-31 20:33 | 2008-12-31 21:08 | 1 | 35.233 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 716494 | CPCC | CPCC544719 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | Line Cut-32820 | 2008 | Before | 2008-12-31 20:25 | 2008-12-31 21:07 | 92 | 3888.533 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9251 | 46.1654
5A15 | 716496 | CPCC | CPCC544721 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_217600_626300518 | 2008 | Before | 2008-12-31 21:04 | 2008-12-31 21:07 | 0 | 0 | 82 | 236.433 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9239 | 46.1651
5A15 | 717025 | CPCC | CPCC544876 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_216607_626300479 | 2009 | Before | 2009-01-01 10:04 | 2009-01-01 11:48 | 1 | 103.617 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: Bad connector at pole | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 717493 | CPCC | CPCC533963 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_164700_543460365 | 2008 | Before | 2008-12-05 21:00 | 2008-12-05 23:02 | 1 | 121.817 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 719100 | CPCC | CPCC537989 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_052003_825180345 | 2008 | Before | 2008-12-21 02:20 | 2008-12-21 07:05 | 79 | 22550.55 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | ICE | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Primary wire down. Tree limb fell through. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9554 | 46.1992
5A15 | 719109 | CPCC | CPCC538117 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_052003_825180345 | 2008 | Before | 2008-12-21 05:45 | 2008-12-21 07:05 | 83 | 6577.75 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Took out for emergency repair on outage 537989. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9554 | 46.1992
5A15 | 720760 | CPCC | CPCC566908 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2009 | Before | 2009-05-29 15:21 | 2009-05-29 15:21 | 0 | 0 | 1768 | 147.333 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: T & R | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 718763 | CPCC | CPCC535790 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_216307_626300603 | 2008 | Before | 2008-12-15 19:05 | 2008-12-15 20:20 | 7 | 520.8 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: Replaced cutout door. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 734000 | CPCC | CPCC574259 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | Line Cut-36088 | 2009 | Before | 2009-07-05 15:01 | 2009-07-05 16:53 | 13 | 1449.933 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: Broken primary jumper. Made repairs and all customers are back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.926 | 46.1657
5A15 | 729516 | CPCC | CPCC562698 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_213500_626300561 | 2009 | Before | 2009-04-28 06:18 | 2009-04-28 09:01 | 3 | 490.1 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: Crew replaced a B/O cutout on pole# 213500, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 713244 | CPCC | CPCC538248 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_165608_543460213 | 2008 | Before | 2008-12-21 08:38 | 2008-12-21 10:03 | 1 | 84.717 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | SNOW, SLEET AND BLIZZARD | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: tree through service / service repaired/replaced | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 709274 | CPCC | CPCC555609 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_216705_626300477 | 2009 | Before | 2009-03-03 08:53 | 2009-03-03 09:51 | 1 | 57.617 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Service man found open service neutral at the pole and repaired | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 710915 | CPCC | CPCC560506 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_094401_543460249 | 2009 | Before | 2009-04-11 15:06 | 2009-04-11 18:15 | 1 | 188.4 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: conn at pole | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 712187 | CPCC | CPCC547184 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_222701_626300659 | 2009 | Before | 2009-01-05 12:17 | 2009-01-05 13:50 | 1 | 92.683 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Re-fused transformer. No cause found. Power restored. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 711445 | CPCC | CPCC560577 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_090801_543460281 | 2009 | Before | 2009-04-12 12:58 | 2009-04-12 14:45 | 1 | 106.85 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: open neutral | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 749566 | CPCC | CPCC597784 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | Line Cut-39231 | 2009 | Before | 2009-11-16 06:36 | 2009-11-16 06:48 | 1775 | 19968.75 | 0 | 0 | 1 | Y | N | N | N | Y | 855 - 2009-11-16 to 2009-11-16 OR Clatsop | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9097 | 46.151
5A15 | 751163 | CPCC | CPCC598222 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2009 | Before | 2009-11-16 17:43 | 2009-11-16 17:43 | 0 | 0 | 1775 | 147.917 | 1 | Y | N | N | N | Y | 855 - 2009-11-16 to 2009-11-16 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: T & R due to storm | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 753899 | CPCC | CPCC624406 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | Line Cut-41961 | 2010 | Before | 2010-03-29 10:05 | 2010-03-29 10:17 | 1774 | 21288 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Loss of x-mission | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9097 | 46.151
5A15 | 750011 | CPCC | CPCC600169 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | Line Cut-39456 | 2009 | Before | 2009-11-22 03:54 | 2009-11-22 05:13 | 1775 | 140225 | 0 | 0 | 1 | Y | N | N | N | Y | 858 - 2009-11-22 to 2009-11-22 OR Clatsop | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE | WEATHER | WIND | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Transmission line tripped open, sectionalized and restored power to the substation | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9095 | 46.1516
5A15 | 752368 | CPCC | CPCC598750 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_090802_1580312156 | 2009 | Before | 2009-11-17 06:00 | 2009-11-17 12:08 | 15 | 5524.25 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Tree through line, primary down. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9407 | 46.1963
5A15 | 753557 | CPCC | CPCC612547 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2010 | Before | 2010-01-17 00:51 | 2010-01-17 00:51 | 0 | 0 | 1776 | 59.2 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: trip and reclose | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 749271 | CPCC | CPCC596738 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_217602_626300402 | 2009 | Before | 2009-11-07 09:13 | 2009-11-07 10:22 | 9 | 621.45 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | B/O EQUIPMENT | CONNECTOR OH |  |  |  | PROSPER: Serviceman changed out B/O secondary connectors | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 750894 | CPCC | CPCC598176 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2009 | Before | 2009-11-16 16:47 | 2009-11-16 16:47 | 0 | 0 | 1775 | 147.917 | 1 | Y | N | N | N | Y | 855 - 2009-11-16 to 2009-11-16 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: T & R due to storm | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 750897 | CPCC | CPCC598182 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_222610_1580311775 | 2009 | Before | 2009-11-16 16:51 | 2009-11-16 18:56 | 18 | 2248.2 | 0 | 0 | 1 | Y | N | N | N | Y | 855 - 2009-11-16 to 2009-11-16 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Blown line fuses. Serviceman patrolling. Wind slapped phases together and blew fuses. Serviceman refused and all customers are back in service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9143 | 46.1643
5A15 | 751689 | CPCC | CPCC598409 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_052003_825180345 | 2009 | Before | 2009-11-16 20:53 | 2009-11-17 04:15 | 80 | 19049.467 | 0 | 0 | 2 | Y | N | N | N | Y | 855 - 2009-11-16 to 2009-11-16 OR Clatsop | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Wire down due to tree. Repairs made and customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9554 | 46.1992
5A15 | 753632 | CPCC | CPCC624349 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_187800_1580419676 | 2010 | Before | 2010-03-29 09:12 | 2010-03-29 17:45 | 3 | 1541.5 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Tree took down primary and blew tapline fuse. Crew made repairs. Customers back in service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.965 | 46.1813
5A15 | 749313 | CPCC | CPCC599222 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_164600_543460367 | 2009 | Before | 2009-11-19 17:51 | 2009-11-19 19:31 | 1 | 99.967 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: Serviceman reports B/O cutout | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 753271 | CPCC | CPCC599146 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2009 | Before | 2009-11-19 06:56 | 2009-11-19 06:56 | 0 | 0 | 1775 | 147.917 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: trip and reclose | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 749737 | CPCC | CPCC599033 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_053009_825180343 | 2009 | Before | 2009-11-18 10:24 | 2009-11-18 11:11 | 4 | 187.333 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | B/O EQUIPMENT | INSULATOR OH |  |  |  | PROSPER: Crew took an emergency outage to make repairs to b/o insulators on pole | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 749741 | CPCC | CPCC599057 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | Line Cut-39332 | 2009 | Before | 2009-11-18 11:12 | 2009-11-18 11:30 | 8 | 149.333 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | B/O EQUIPMENT | DEAD END B/O OH |  |  |  | PROSPER: Crew took emergency outage on pole# 083903 to change out some B/O deadend bells. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9533 | 46.1989
5A15 | 752896 | CPCC | CPCC598836 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_089810_543460273 | 2009 | Before | 2009-11-17 08:45 | 2009-11-17 12:20 | 1 | 215.15 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: CALLED CUSTOMER, POWER IS RESTORED | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 752931 | CPCC | CPCC601303 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_079940_825180415 | 2009 | Before | 2009-11-24 11:45 | 2009-11-24 14:37 | 1 | 171.7 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Serviceman swapping trucks and will go on after. Broken secondary neutral at pole due to a tree and wind. Serviceman made repairs and customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 751421 | CPCC | CPCC598252 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2009 | Before | 2009-11-16 18:50 | 2009-11-16 18:50 | 0 | 0 | 1757 | 146.417 | 1 | Y | N | N | N | Y | 855 - 2009-11-16 to 2009-11-16 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: T & R due to storm | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 751424 | CPCC | CPCC598259 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2009 | Before | 2009-11-16 18:58 | 2009-11-16 18:58 | 0 | 0 | 1775 | 147.917 | 1 | Y | N | N | N | Y | 855 - 2009-11-16 to 2009-11-16 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: T & R due to storm | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 751425 | CPCC | CPCC598262 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2009 | Before | 2009-11-16 19:03 | 2009-11-16 19:03 | 0 | 0 | 1775 | 59.167 | 1 | Y | N | N | N | Y | 855 - 2009-11-16 to 2009-11-16 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: T & R due to storm | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 751427 | CPCC | CPCC598282 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_088802_825180426 | 2009 | Before | 2009-11-16 16:35 | 2009-11-16 20:52 | 193 | 49510.933 | 0 | 0 | 1 | Y | N | N | N | Y | 855 - 2009-11-16 to 2009-11-16 OR Clatsop | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Blown line fuse on pole 088802. Serviceman patrolled line out. No cause found. He refused line and it held. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9439 | 46.197
5A15 | 753373 | CPCC | CPCC624327 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_274801_915350405 | 2010 | Before | 2010-03-29 08:43 | 2010-03-29 09:32 | 3 | 144.75 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Deteriorated x-fmr fuse. Serviceman replaced fuse and fuse held. All customers back in service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 750635 | CPCC | CPCC598120 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | Line Cut-39271 | 2009 | Before | 2009-11-16 15:50 | 2009-11-16 16:13 | 1775 | 41416.667 | 0 | 0 | 1 | Y | N | N | N | Y | 855 - 2009-11-16 to 2009-11-16 OR Clatsop | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9097 | 46.1509
5A15 | 749471 | CPCC | CPCC599008 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_057005_825180386 | 2009 | Before | 2009-11-18 08:17 | 2009-11-18 10:34 | 1 | 137.567 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: left message. Crew found b/o connectors at weatherhead and repalced. Customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 749472 | CPCC | CPCC599009 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_089904_1580312224 | 2009 | Before | 2009-11-18 08:14 | 2009-11-18 09:45 | 1 | 91.183 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: Crew found b/o cut-out and repaired. Customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 751079 | CPCC | CPCC601164 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | Line Cut-39550 | 2009 | Before | 2009-11-23 14:33 | 2009-11-23 14:43 | 1776 | 17227.2 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9097 | 46.1509
5A15 | 751874 | CPCC | CPCC601731 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_168101_543460230 | 2009 | Before | 2009-11-27 12:23 | 2009-11-27 15:21 | 1 | 178.083 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | PROSPER: Crew changed out a B/O transformer on pole# 168101, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 752642 | CPCC | CPCC598817 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_187800_1580419676 | 2009 | Before | 2009-11-17 08:21 | 2009-11-17 17:58 | 3 | 1730 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Blown line fuses. Wire down in several locations due to trees and wind. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.965 | 46.1813
5A15 | 748311 | CPCC | CPCC582606 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_054104_825180363 | 2009 | Before | 2009-08-16 13:26 | 2009-08-16 15:02 | 1 | 95.1 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: truck tore down service | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 747615 | CPCC | CPCC589921 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_212782_626300543 | 2009 | Before | 2009-09-29 19:01 | 2009-09-29 21:21 | 1 | 140.233 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | PROSPER: Bad leg on secondary. Istalled service saver | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 747363 | CPCC | CPCC590127 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | UG213780_626300082 | 2009 | Before | 2009-09-30 19:20 | 2009-09-30 20:33 | 5 | 365.5 | 0 | 0 | 1 | Y | N | N | N | N |  | OPERATIONAL | INCORRECT RECORDS |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: Dig in while working on repairing a service | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9335 | 46.1661
5A15 | 742983 | CPCC | CPCC593982 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_220605_626300672 | 2009 | Before | 2009-10-15 23:22 | 2009-10-16 01:18 | 1 | 116.017 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | PROSPER: replaced nuetral connectors | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 756251 | CPCC | CPCC623760 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2010 | Before | 2010-03-29 00:33 | 2010-03-29 00:33 | 0 | 0 | 1777 | 148.083 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: feeder oper | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 756256 | CPCC | CPCC623765 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2010 | Before | 2010-03-29 01:45 | 2010-03-29 01:45 | 0 | 0 | 1777 | 59.233 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: feeder oper | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 757049 | CPCC | CPCC624001 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | Line Cut-41948 | 2010 | Before | 2010-03-29 07:18 | 2010-03-29 07:22 | 0 | 0 | 1777 | 7108 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Loss of x-mission | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9097 | 46.151
5A15 | 754347 | CPCC | CPCC613204 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | MAB217900_626300452 | 2010 | Before | 2010-01-18 02:53 | 2010-01-18 04:45 | 1054 | 117556.133 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | TREES | TREE - NON-PREVENTABLE | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: wind blowing tree into line, burning, opened switch to isolate | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9252 | 46.1688
5A15 | 754348 | CPCC | CPCC613205 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2010 | Before | 2010-01-18 02:56 | 2010-01-18 02:56 | 0 | 0 | 722 | 60.167 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: feeder oper | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 754349 | CPCC | CPCC613206 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2010 | Before | 2010-01-18 02:56 | 2010-01-18 02:56 | 0 | 0 | 722 | 156.433 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: feeder oper | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 754350 | CPCC | CPCC613207 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2010 | Before | 2010-01-18 02:56 | 2010-01-18 04:20 | 722 | 60587.833 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | REGULATOR B/O OH |  |  |  | PROSPER: Feeder locked out due to pole top reg failure on pole 217803. Crew cut reg in the clear and closed breaker. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 755135 | CPCC | CPCC613352 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_057005_825180386 | 2010 | Before | 2010-01-18 12:29 | 2010-01-18 14:06 | 1 | 97.4 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: B/O o/h service. Serviceman replaced service. Customer still having issues but they are due to customer owned equipment. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 755971 | CPCC | CPCC617362 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_215680_626300503 | 2010 | Before | 2010-02-05 22:59 | 2010-02-06 02:57 | 1 | 238 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | SECONDARY CABLE UG |  |  |  | PROSPER: b/o secondary T tap/connections, calling crew. repaired, power on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 754438 | CPCC | CPCC624540 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | Line Cut-41989 | 2010 | Before | 2010-03-29 10:44 | 2010-03-29 10:46 | 0 | 0 | 1774 | 3577.567 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Loss of Transmission | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9097 | 46.151
5A15 | 754075 | CPCC | CPCC613180 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2010 | Before | 2010-01-18 00:42 | 2010-01-18 00:42 | 0 | 0 | 1776 | 59.2 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: feeder oper | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 754077 | CPCC | CPCC613183 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_222610_1580311775 | 2010 | Before | 2010-01-18 00:51 | 2010-01-18 02:44 | 25 | 2829.583 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: replaced fuse | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9143 | 46.1643
5A15 | 755253 | CPCC | CPCC603483 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_216107_626300616 | 2009 | Before | 2009-12-07 09:27 | 2009-12-07 10:32 | 1 | 64.467 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: B/O secondary connector at the weatherhead. Serviceman replaced connector. Customer back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 756859 | CPCC | CPCC628515 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_217783_626300482 | 2010 | Before | 2010-04-18 09:38 | 2010-04-18 11:51 | 1 | 132.283 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: part of outage # 628516 bad cut out | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 756860 | CPCC | CPCC628516 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_217704_626300455 | 2010 | Before | 2010-04-18 10:13 | 2010-04-18 11:50 | 1 | 96.533 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: cut out bad | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 756514 | CPCC | CPCC623766 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_222610_1580311775 | 2010 | Before | 2010-03-29 01:52 | 2010-03-29 07:05 | 26 | 8119.8 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Blown tap-line fuses on pole# 222610 due to wind. Serviceman replaced fuses and fuses held all customers back in service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9143 | 46.1643
5A15 | 756522 | CPCC | CPCC623777 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2010 | Before | 2010-03-29 03:15 | 2010-03-29 03:15 | 0 | 0 | 1777 | 148.083 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: feeder oper | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 756928 | CPCC | CPCC621575 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2010 | Before | 2010-03-12 05:51 | 2010-03-12 05:51 | 0 | 0 | 1776 | 148 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: T & R. cause unknown | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 755781 | CPCC | CPCC628315 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2010 | Before | 2010-04-16 02:37 | 2010-04-16 02:37 | 0 | 0 | 1777 | 148.083 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: T and R. Bad order UG. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 755782 | CPCC | CPCC628318 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_215904_1580006860 | 2010 | Before | 2010-04-16 02:59 | 2010-04-16 05:21 | 31 | 4408.717 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: Blown dip fuse. Bad order UG. Switched bad section out and customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9298 | 46.1694
5A15 | 758981 | CPCC | CPCC612224 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_187800_1580419676 | 2010 | Before | 2010-01-15 08:49 | 2010-01-15 10:56 | 3 | 382.4 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Crew made repairs to the overhead primary that was taken down by a tree, customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.965 | 46.1813
5A15 | 740090 | CPCC | CPCC597348 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_082801_1580003247 | 2009 | Before | 2009-11-12 16:46 | 2009-11-12 18:04 | 23 | 1789.4 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: patrolling, b/o cutout, replaced, poweron. Associatted to Outage 597351 | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9551 | 46.1962
5A15 | 740092 | CPCC | CPCC597350 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_080901_825180504 | 2009 | Before | 2009-11-12 16:47 | 2009-11-12 18:05 | 5 | 386.583 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: patrolling, b/o cutout, replaced, poweron. Associatted to Outage 597351 | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 740093 | CPCC | CPCC597351 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_088802_825180426 | 2009 | Before | 2009-11-12 16:48 | 2009-11-12 19:30 | 204 | 15733.833 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: patrolling, b/o cutout, replaced, poweron. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9439 | 46.197
5A15 | 740094 | CPCC | CPCC597355 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_050041_825180352 | 2009 | Before | 2009-11-12 16:49 | 2009-11-12 18:01 | 1 | 71.767 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: patrolling, b/o cutout, replaced, poweron. Associatted to Outage 597351 | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 740095 | CPCC | CPCC597361 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_054006_825180388 | 2009 | Before | 2009-11-12 16:51 | 2009-11-12 17:58 | 40 | 2705.333 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: patrolling, b/o cutout, replaced, poweron. Associatted to Outage 597351 | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9522 | 46.1992
5A15 | 740096 | CPCC | CPCC597362 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_050042_825180506 | 2009 | Before | 2009-11-12 16:51 | 2009-11-12 18:02 | 1 | 70.583 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: patrolling, b/o cutout, replaced, poweron. Associatted to Outage 597351 | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 740097 | CPCC | CPCC597369 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_086900_825180441 | 2009 | Before | 2009-11-12 17:03 | 2009-11-12 18:02 | 5 | 295.75 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: patrolling, b/o cutout, replaced, poweron. Associatted to Outage 597351 | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 740098 | CPCC | CPCC597372 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_065580_825180390 | 2009 | Before | 2009-11-12 17:19 | 2009-11-12 18:00 | 1 | 40.733 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: patrolling, b/o cutout, replaced, poweron. Associatted to Outage 597351 | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 740100 | CPCC | CPCC597377 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_056003_825180368 | 2009 | Before | 2009-11-12 18:02 | 2009-11-12 18:04 | 0 | 0 | 1 | 2.883 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: patrolling, b/o cutout, replaced, poweron. Associatted to Outage 597351 | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 740101 | CPCC | CPCC597378 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_056003_825180368 | 2009 | Before | 2009-11-12 18:06 | 2009-11-12 18:09 | 0 | 0 | 1 | 2.967 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: patrolling, b/o cutout, replaced, poweron. Associatted to Outage 597351 | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 740103 | CPCC | CPCC597390 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_057004_825180382 | 2009 | Before | 2009-11-12 19:50 | 2009-11-13 01:03 | 19 | 5945.417 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: suspect b/o u.g. repaired u.g. primary | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9467 | 46.1992
5A15 | 738546 | CPCC | CPCC580426 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_053100_825180339 | 2009 | Before | 2009-08-03 15:01 | 2009-08-03 16:11 | 1 | 69.8 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Serviceman already on site. A boat with sails up was being pulled through area and tore secondary service down. Crew to make repairs. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 737400 | CPCC | CPCC587968 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | Line Cut-37967 | 2009 | Before | 2009-09-19 09:56 | 2009-09-19 10:14 | 1774 | 31932 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE | EQUIPMENT FAILURE | POLE FIRE | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: pole fire 115kV | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 739846 | CPCC | CPCC597345 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2009 | Before | 2009-11-12 16:40 | 2009-11-12 16:40 | 0 | 0 | 1775 | 59.167 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: T and R patrolling, b/o cutout, replaced, poweron. Associatted to Outage 597351 | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 739847 | CPCC | CPCC597346 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2009 | Before | 2009-11-12 16:41 | 2009-11-12 16:41 | 0 | 0 | 1775 | 147.917 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: T and r, patrolling, b/o cutout, replaced, poweron. Associatted to Outage 597351 | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 776355 | CPCC | CPCC638125 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2010 | Before | 2010-06-08 09:49 | 2010-06-08 09:49 | 0 | 0 | 1778 | 148.167 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: T&R, no cause found. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 777989 | CPCC | CPCC631699 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_214780_626300421 | 2010 | Before | 2010-05-03 10:43 | 2010-05-03 13:00 | 1 | 137.15 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | PROSPER: b/o ug secondary hot leg to one building. Crew to repair. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 778381 | CPCC | CPCC636141 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_055001_825180389 | 2010 | Before | 2010-05-21 12:55 | 2010-05-21 14:01 | 3 | 198.7 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: Crew replaced b/o cutout. All customers back in service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 774110 | CPCC | CPCC647486 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | Line Cut-44315 | 2010 | Before | 2010-07-29 11:03 | 2010-07-29 11:03 | 0 | 0 | 1780 | 89 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Transmission T&R. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9097 | 46.151
5A15 | 777776 | CPCC | CPCC643933 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_217402_626300593 | 2010 | Before | 2010-07-15 08:53 | 2010-07-15 09:07 | 5 | 69.667 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: Blown x-fmr fuse due to b/o cut-out. Crew replaced. Customers back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 770283 | CPCC | CPCC638925 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_223800_626300660 | 2010 | Before | 2010-06-12 11:31 | 2010-06-12 13:34 | 1 | 123.3 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | PROSPER: replaced connector at wx/head | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 769530 | CPCC | CPCC607676 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_216707_626300487 | 2009 | Before | 2009-12-22 08:59 | 2009-12-22 10:13 | 1 | 73.217 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: B/O secondary neutral connector. Serviceman replaced connector. Customer back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 768087 | CPCC | CPCC619208 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_057005_825180386 | 2010 | Before | 2010-02-24 07:07 | 2010-02-24 09:05 | 4 | 472.333 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Serviceman made repairs to the overhead secondary neutral that rotted apart, customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 781344 | CPCC | CPCC646890 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_069143_825180413 | 2010 | Before | 2010-07-26 19:27 | 2010-07-26 21:05 | 1 | 98.117 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Repaired secondary neutral connection | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 782524 | CPCC | CPCC646043 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_167280_543460387 | 2010 | Before | 2010-07-25 12:40 | 2010-07-25 15:10 | 1 | 149.517 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | PROSPER: Bad order secondaru UG. Service saver has been installed and customer is back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 783313 | CPCC | CPCC633332 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_221404_626300679 | 2010 | Before | 2010-05-13 15:12 | 2010-05-13 17:31 | 1 | 138.833 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | OTHER UTILITY/CONTRACTOR |  |  | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | PROSPER: Serviceman replaced meter broken by lawn mower | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 781761 | CPCC | CPCC632611 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_189800_825180516 | 2010 | Before | 2010-05-07 07:48 | 2010-05-07 08:41 | 4 | 212 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: dispatch contacted GF, he stated will send crew response, will call when enroute(07:57), serviceman located open fuse/broken cut-out @ FP# 189800, repaired, outage restored. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 761810 | CPCC | CPCC629714 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | Line Cut-42523 | 2010 | Before | 2010-04-26 10:34 | 2010-04-26 13:15 | 1 | 160.3 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | PROSPER: B/O x-fmr. Crew replaced x-fmr. Customer back in service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9624 | 46.1786
5A15 | 760313 | CPCC | CPCC612520 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_223800_626300660 | 2010 | Before | 2010-01-16 11:09 | 2010-01-16 11:57 | 1 | 48.2 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: replaced deteriorated xfmr fuse | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 760322 | CPCC | CPCC612548 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_215904_1580006860 | 2010 | Before | 2010-01-17 00:59 | 2010-01-17 04:36 | 31 | 6747.15 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: suspect bad ug primary blown dip fuse, crew to investagate | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9298 | 46.1694
5A15 | 763095 | CPCC | CPCC627961 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_274801_915350405 | 2010 | Before | 2010-04-12 21:14 | 2010-04-12 22:16 | 1 | 61.7 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | PROSPER: secondary connector | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 763935 | CPCC | CPCC629618 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_189602_825180519 | 2010 | Before | 2010-04-24 21:17 | 2010-04-25 01:07 | 1 | 230 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Crew replaced deteriorated o/h service | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 760426 | CPCC | CPCC615666 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_067204_825180399 | 2010 | Before | 2010-01-24 10:18 | 2010-01-24 11:46 | 1 | 87.25 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | PROSPER: replaced connector | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 761225 | CPCC | CPCC625583 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_220305_626300684 | 2010 | Before | 2010-03-30 14:35 | 2010-03-30 15:33 | 2 | 116.1 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman found blown xfmr fuse due to wind and rain storm. He repalced it and customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 766016 | CPCC | CPCC619994 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_214780_626300421 | 2010 | Before | 2010-03-01 18:00 | 2010-03-01 21:48 | 1 | 227.617 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | PROSPER: Bad order secondary U/G. Made repairs and customer is back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 765658 | CPCC | CPCC612030 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2010 | Before | 2010-01-13 18:04 | 2010-01-13 18:04 | 0 | 0 | 1776 | 148 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TERMINATION UG |  |  |  | PROSPER: T/R | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 765659 | CPCC | CPCC612032 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_053201_825180326 | 2010 | Before | 2010-01-13 18:20 | 2010-01-13 22:27 | 6 | 1482 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TERMINATION UG |  |  |  | PROSPER: patrolled, riser open, b/o u..g.? calling crew, crew found b/o termination, replaced, power back on/normal | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.955 | 46.2025
5A15 | 763668 | CPCC | CPCC629542 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_189602_825180519 | 2010 | Before | 2010-04-24 09:54 | 2010-04-24 14:07 | 1 | 252.35 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: found burnt secondary in trees, requested to call crew to replace secondary. crew loading material. serviceman says maybe claims from customers on this job later | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 766131 | CPCC | CPCC606528 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_090801_543460281 | 2009 | Before | 2009-12-14 10:10 | 2009-12-14 11:45 | 4 | 380.2 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Per serviceman: deteriorated x-fmr fuse on pole# 090801. Serviceman replaced fuse and fuse held. Customer back in service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 801840 | CPCC | CPCC655007 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_218601_626300520 | 2010 | Before | 2010-09-19 06:46 | 2010-09-19 11:15 | 1 | 269.667 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | PROSPER: Crew changed bad order xfmr | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 804522 | CPCC | CPCC686372 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2011 | Before | 2011-03-02 05:35 | 2011-03-02 05:35 | 0 | 0 | 1788 | 149 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: T&R due to wind slapping phases together. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 801146 | CPCC | CPCC664501 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_095002_543460269 | 2010 | Before | 2010-11-13 08:18 | 2010-11-13 11:17 | 2 | 358.7 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: Burnt up cutout, crew needed. Repairs made and customers | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 795242 | CPCC | CPCC653934 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_167280_543460387 | 2010 | Before | 2010-09-12 18:31 | 2010-09-12 20:48 | 1 | 137.4 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | PROSPER: bad order u/g service. Service saver installed | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 797220 | CPCC | CPCC668259 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2010 | Before | 2010-12-03 17:25 | 2010-12-03 17:25 | 0 | 0 | 1784 | 148.667 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | SPLICE B/O OH |  |  |  | PROSPER: T&R due to b/o primary splice. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 797221 | CPCC | CPCC668260 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2010 | Before | 2010-12-03 17:25 | 2010-12-03 17:25 | 0 | 0 | 1784 | 356.8 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | SPLICE B/O OH |  |  |  | PROSPER: T&R due to b/o primary splice. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 797222 | CPCC | CPCC668261 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2010 | Before | 2010-12-03 17:25 | 2010-12-03 20:35 | 1784 | 338632.933 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SPLICE B/O OH |  |  |  | PROSPER: Crew to make repairs, splice failed which caused primary wire down. Crew to replace splice. Repairs completed, Customers on | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 793726 | CPCC | CPCC664960 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_216300_626300607 | 2010 | Before | 2010-11-16 13:27 | 2010-11-16 14:04 | 3 | 112.2 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | PROSPER: Crew replacing b/o x-fmr. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 795468 | CPCC | CPCC652997 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_088902_825180433 | 2010 | Before | 2010-09-05 09:19 | 2010-09-05 10:25 | 1 | 66.217 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: replaced broken service neutral deteriorated. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 794781 | CPCC | CPCC661603 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_057005_825180386 | 2010 | Before | 2010-10-25 11:38 | 2010-10-25 15:13 | 1 | 214.4 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | PROSPER: serviceman is replacing deteriorated OH Secondary connectors @ WeatherHead. repairs made, full power restored | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 805559 | CPCC | CPCC675138 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2011 | Before | 2011-01-10 10:05 | 2011-01-10 10:25 | 1291 | 26314.883 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | B/O EQUIPMENT | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: Crew opened breaker to make repairs to b/o jumper on regulator. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 806328 | CPCC | CPCC671271 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2010 | Before | 2010-12-18 12:01 | 2010-12-18 12:09 | 1784 | 14569.333 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Loss of transmission line | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 804790 | CPCC | CPCC686409 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_222610_1580311775 | 2011 | Before | 2011-03-02 05:46 | 2011-03-02 08:18 | 25 | 3802.917 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: 2 open line fuses. Serviceman patrolled and found no cause (wind suspected). Serviceman replaced fuses and they held. Customers back in service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9143 | 46.1643
5A15 | 804794 | CPCC | CPCC686413 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_169100_1580286070 | 2011 | Before | 2011-03-02 07:09 | 2011-03-02 09:46 | 2 | 313.7 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: Burnt off jumper on primary dip. Crew needed to make repairs. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9222 | 46.1722
5A15 | 807156 | CPCC | CPCC687897 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_222500_626300669 | 2011 | Before | 2011-03-11 11:18 | 2011-03-11 12:29 | 1 | 70.833 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Serviceman replaced b/o secondary connectors at the weatherhead. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 807554 | CPCC | CPCC698356 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2011 | Before | 2011-03-26 07:14 | 2011-03-26 07:14 | 0 | 0 | 1789 | 149.083 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: feeder operation | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 807558 | CPCC | CPCC698369 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_057004_825180382 | 2011 | Before | 2011-03-26 07:22 | 2011-03-26 19:14 | 30 | 21363 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: bad ug pri. Repairs made and customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9467 | 46.1992
5A15 | 808348 | CPCC | CPCC671296 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | Line Cut-47106 | 2010 | Before | 2010-12-18 12:01 | 2010-12-18 12:09 | 1785 | 14161 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Loss of transmission line | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9097 | 46.151
5A15 | 805253 | CPCC | CPCC679844 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2011 | Before | 2011-02-14 09:58 | 2011-02-14 09:58 | 0 | 0 | 1787 | 59.567 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: T&R due to b/o ug primary cable. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 805254 | CPCC | CPCC679847 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_166301_543460372 | 2011 | Before | 2011-02-14 10:02 | 2011-02-14 11:30 | 8 | 705.6 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: Blown dip fus due to b/o ug primary. Crew switched customers back in service @ 11:30 and are making repairs to cable. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.927 | 46.1753
5A15 | 807604 | CPCC | CPCC678664 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_211780_626300554 | 2011 | Before | 2011-02-08 20:11 | 2011-02-08 21:38 | 1 | 87.75 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Crew arrived and found bad leg on secondary. Attached service saver outage restored. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 805299 | CPCC | CPCC675082 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2011 | Before | 2011-01-10 08:38 | 2011-01-10 08:39 | 0 | 0 | 1785 | 148.75 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: T&R due to b/o jumper | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 805300 | CPCC | CPCC675085 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | Line Cut-47443 | 2011 | Before | 2011-01-10 08:42 | 2011-01-10 10:25 | 418 | 42907.7 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: Burnt open jumper on regulator bank on pole# 217803. Crew made repairs. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9252 | 46.1684
5A15 | 805301 | CPCC | CPCC675093 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_084901_825180457 | 2011 | Before | 2011-01-10 08:48 | 2011-01-10 10:25 | 1 | 96.633 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: Bad connectivity in Cad ops. Please associate to outage# 675085. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 805302 | CPCC | CPCC675094 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_187800_825180537 | 2011 | Before | 2011-01-10 08:49 | 2011-01-10 10:25 | 1 | 96.033 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: Bad connectivity in Cad ops. Please associate to outage# 675085. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 805303 | CPCC | CPCC675095 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_166301_543460372 | 2011 | Before | 2011-01-10 08:51 | 2011-01-10 10:25 | 13 | 1227.417 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: Bad connectivity in Cad ops. Please associate to outage# 675085. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.927 | 46.1753
5A15 | 805691 | CPCC | CPCC697650 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_217903_626300451 | 2011 | Before | 2011-03-21 16:48 | 2011-03-21 17:55 | 1 | 67.133 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | PROSPER: Servicemanm found bad connector, and repaired. Outage restored. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 805304 | CPCC | CPCC675109 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_167105_543460382 | 2011 | Before | 2011-01-10 09:01 | 2011-01-10 10:25 | 21 | 1769.95 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: Bad connectivity in Cad ops. Please associate to outage# 675085. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9248 | 46.1721
5A15 | 805305 | CPCC | CPCC675111 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_085901_825180451 | 2011 | Before | 2011-01-10 09:02 | 2011-01-10 10:25 | 1 | 83.283 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: Bad connectivity in Cad ops. Please associate to outage# 675085. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 805307 | CPCC | CPCC675115 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_082801_1580003247 | 2011 | Before | 2011-01-10 09:06 | 2011-01-10 10:25 | 26 | 2063.1 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: Bad connectivity in Cad ops. Please associate to outage# 675085. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9551 | 46.1962
5A15 | 805308 | CPCC | CPCC675119 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_087901_825180444 | 2011 | Before | 2011-01-10 08:46 | 2011-01-10 10:25 | 11 | 1091.75 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: Bad connectivity in Cad ops. Please associate to outage# 675085. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9467 | 46.1982
5A15 | 805310 | CPCC | CPCC675123 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_080901_825180504 | 2011 | Before | 2011-01-10 09:16 | 2011-01-10 10:25 | 1 | 69.4 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: Bad connectivity in Cad ops. Please associate to outage# 675085. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 805311 | CPCC | CPCC675126 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_050041_825180352 | 2011 | Before | 2011-01-10 09:30 | 2011-01-10 10:25 | 1 | 54.767 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: Bad connectivity in Cad ops. Please associate to outage# 675085. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 805314 | CPCC | CPCC675131 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_090703_543460286 | 2011 | Before | 2011-01-10 09:38 | 2011-01-10 10:25 | 4 | 188.267 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: Bad connectivity in Cad ops. Please associate to outage# 675085. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 788668 | CPCC | CPCC663596 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | Line Cut-46386 | 2010 | Before | 2010-11-08 08:44 | 2010-11-08 10:54 | 6 | 781.1 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | SPLICE B/O OH |  |  |  | PROSPER: B/O splice on the o/h primary failed and one phase open. Crew onsite making repairs. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9143 | 46.1643
5A15 | 788669 | CPCC | CPCC663597 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | Line Cut-46387 | 2010 | Before | 2010-11-08 08:45 | 2010-11-08 10:54 | 10 | 1288.167 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | B/O EQUIPMENT | SPLICE B/O OH |  |  |  | PROSPER: Crew open other two phases to make repairs to b/o splice. Notes from original outage: B/O splice on the o/h primary failed and one phase open. Crew onsite making repairs. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9143 | 46.1643
5A15 | 824293 | CPCC | CPCC712914 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_167203_543460384 | 2011 | Before | 2011-07-18 14:05 | 2011-07-18 16:02 | 1 | 117.2 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: Crew needed to replace the B/O secondary connectors at the transformer. Customer is back in full service | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 826725 | CPCC | CPCC703735 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_215604_626300476 | 2011 | Before | 2011-04-29 12:52 | 2011-04-29 13:41 | 1 | 48.833 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: Serviceman replaced b/o secondary connectors. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 824549 | CPCC | CPCC712928 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_167203_543460384 | 2011 | Before | 2011-07-18 15:17 | 2011-07-18 16:02 | 4 | 181.333 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | B/O EQUIPMENT | CONNECTOR OH |  |  |  | PROSPER: Crew took outage on transformer# 167203 to replace the B/O secondary connectors at the transformer. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 817875 | CPCC | CPCC685014 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2011 | Before | 2011-02-25 09:21 | 2011-02-25 09:21 | 0 | 0 | 1788 | 149 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: T&R, no cause found | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 820644 | CPCC | CPCC699475 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2011 | Before | 2011-03-30 12:27 | 2011-03-30 12:28 | 0 | 0 | 1789 | 149.083 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: feeder operation | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 820647 | CPCC | CPCC699480 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_057004_825180382 | 2011 | Before | 2011-03-30 12:39 | 2011-03-30 20:05 | 30 | 13386 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: Serviceman found blown dip fuse. Crew is on site to test ug primary cable. Crew found deteriorated ug primary cable and are working on repairs. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9467 | 46.1992
5A15 | 819493 | CPCC | CPCC696088 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_083907_825180459 | 2011 | Before | 2011-03-15 13:50 | 2011-03-15 15:05 | 1 | 75.183 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Serviceman made repairs to b/o downed service. Customer back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 823753 | CPCC | CPCC712822 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2011 | Before | 2011-07-18 01:15 | 2011-07-18 01:15 | 0 | 0 | 1799 | 149.917 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | POLE OH |  |  |  | PROSPER: Car hit pole, pole is being replaced. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 830352 | CPCC | CPCC704539 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_088905_825180435 | 2011 | Before | 2011-05-07 15:52 | 2011-05-07 17:23 | 1 | 90.483 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Service was tore down by moving van. Customers will need electrician to repair meterbase. Rehung service meter is still cut in the clear for repairs. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 816705 | CPCC | CPCC675495 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2011 | Before | 2011-01-13 04:05 | 2011-01-13 04:05 | 0 | 0 | 1785 | 59.5 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | POLE OH |  |  |  | PROSPER: T&R due to pole fire | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 816706 | CPCC | CPCC675496 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2011 | Before | 2011-01-13 04:05 | 2011-01-13 07:40 | 1785 | 384072.5 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | POLE OH |  |  |  | PROSPER: Pole fire on pole# 223501 and burnt off jumpers on pole# 224501. Crew to repair jumpers and then replace pole. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 815150 | CPCC | CPCC679307 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_222610_1580311775 | 2011 | Before | 2011-02-12 14:55 | 2011-02-12 19:00 | 26 | 6380.4 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: blown fuse, refused and holding | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9143 | 46.1643
5A15 | 816405 | CPCC | CPCC671790 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_087906_825180261 | 2010 | Before | 2010-12-20 13:15 | 2010-12-20 13:17 | 0 | 0 | 4 | 7.333 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | B/O EQUIPMENT | CUT-OUT B/O OH |  |  |  | PROSPER: no outage non reportable: closed in error, outage remodel(671792) | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 816406 | CPCC | CPCC671792 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_087906_825180261 | 2010 | Before | 2010-12-20 13:17 | 2010-12-20 13:51 | 4 | 132.4 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | B/O EQUIPMENT | CUT-OUT B/O OH |  |  |  | PROSPER: crew located faulted OH C/O while performing work in area, created emergency damage repair outage to replace/repair, work complete, outage restored | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 814888 | CPCC | CPCC679255 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2011 | Before | 2011-02-12 14:44 | 2011-02-12 14:44 | 0 | 0 | 1786 | 148.833 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: feeder operation | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 861490 | CPCC | CPCC732826 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_222610_1580311775 | 2011 | Before | 2011-11-22 23:52 | 2011-11-23 11:25 | 25 | 17326.667 | 0 | 0 | 1 | Y | N | N | N | Y | 2011-11-22 to 2011-11-23 OR Clatsop | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Primary line down due to wind/tree. Crew made repairs. PROSPER: Customer call transfered from CPCC732218. Changed start date/time to match CPCC732218. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2011-11-23 11:07 | 2011-12-09 10:07 | 2011-11-23 21:46 | -123.9143 | 46.1643
5A15 | 855134 | CPCC | CPCC727766 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_187800_825180537 | 2011 | Before | 2011-10-31 08:20 | 2011-10-31 15:06 | 1 | 406.15 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | SOURCE: cell(08:28)serviceman reporting low voltage to site, suspects Faulted UG Secondary Cable, crew to locate/repair/restore full power(09:19), completed & restored | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2011-10-31 15:00 | COMPLETED |  | 2011-10-31 08:20 | 2011-10-31 16:06 | 2011-10-31 16:14 | -123.965 | 46.1813
5A15 | 861013 | CPCC | CPCC732217 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2011 | Before | 2011-11-22 23:50 | 2011-11-22 23:50 | 0 | 0 | 1801 | 150.083 | 1 | Y | N | N | N | Y | 2011-11-22 to 2011-11-23 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: T and R. Cause Wind. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2011-11-22 23:50 | 2011-11-22 23:50 | 2011-11-23 00:01 | -123.9098 | 46.1511
5A15 | 861430 | CPCC | CPCC732308 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2011 | Before | 2011-11-22 23:52 | 2011-11-23 10:55 | 1801 | 1190464.1 | 0 | 0 | 2 | Y | N | N | N | Y | 2011-11-22 to 2011-11-23 OR Clatsop | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: locked out due to primary wire down tree/wind. Crew made repairs. Customers back in service. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2011-11-23 01:23 | 2011-11-30 09:03 | 2011-11-23 18:16 | -123.9098 | 46.1511
5A15 | 858045 | CPCC | CPCC729549 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2011 | Before | 2011-11-12 00:17 | 2011-11-12 01:36 | 1800 | 142170 | 0 | 0 | 1 | Y | N | N | N | Y | 2011-11-12 to 2011-11-12 OR Clatsop | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  |  | DISTRIBUTION | DEVICE | AUTO | 2011-11-12 03:30 | COMPLETED |  | 2011-11-12 00:19 | 2011-11-12 01:36 | 2011-11-12 01:43 | -123.9098 | 46.1511
5A15 | 844482 | CPCC | CPCC718383 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_216305_626300604 | 2011 | Before | 2011-08-23 22:10 | 2011-08-23 22:37 | 5 | 136.917 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: Took emergency outage to replace cutout. See outage 718376 for original call. Repairs made and customers are back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 862126 | CPCC | CPCC733426 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_165400_543460214 | 2011 | Before | 2011-11-27 08:03 | 2011-11-27 09:11 | 1 | 68.5 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman arrived and found deteriorated fuse and replaced it outage restored. | DISTRIBUTION | CUSTOMER | AUTO |  | COMPLETED |  | 2011-11-27 08:03 | 2011-11-27 09:11 | 2011-11-27 16:55 | -123.9292 | 46.1772
5A15 | 861905 | CPCC | CPCC733326 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_094200_543460262 | 2011 | Before | 2011-11-25 18:49 | 2011-11-25 19:45 | 1 | 56.25 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Open secondary neutral in service. Repairs made and customer is back on. | DISTRIBUTION | CUSTOMER | AUTO |  | COMPLETED |  | 2011-11-25 18:49 | 2011-11-25 19:45 | 2011-11-26 06:06 | -123.9309 | 46.1875
5A15 | 860497 | CPCC | CPCC730980 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | MAB217900_626300452 | 2011 | Before | 2011-11-21 17:25 | 2011-11-22 01:14 | 1063 | 497802.9 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | POLE FIRE | POLE OH |  |  |  | SOURCE: Pole fire, caused needed pole replacement gang switch opened to work safely. | DISTRIBUTION | DEVICE | MANUAL | 2011-11-22 01:30 | COMPLETED |  | 2011-11-21 21:28 | 2011-11-29 13:38 | 2011-11-22 03:06 | -123.9252 | 46.1688
5A15 | 860986 | CPCC | CPCC731980 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2011 | Before | 2011-11-22 21:13 | 2011-11-22 21:13 | 0 | 0 | 1784 | 148.667 | 1 | Y | N | N | N | Y | 2011-11-22 to 2011-11-23 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: T&R | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2011-11-22 21:13 | 2011-11-22 21:13 | 2011-11-22 22:42 | -123.9098 | 46.1511
5A15 | 861006 | CPCC | CPCC731993 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_222610_1580311775 | 2011 | Before | 2011-11-22 21:39 | 2011-11-22 22:51 | 9 | 650.4 | 0 | 0 | 1 | Y | N | N | N | Y | 2011-11-22 to 2011-11-23 OR Clatsop | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman opened the C phase tapline fuse at pole# 222610 to take the slack out of the overhead primary. | DISTRIBUTION | DEVICE | AUTO | 2011-11-23 00:45 | COMPLETED |  | 2011-11-22 21:39 | 2011-11-22 22:51 | 2011-11-22 23:16 | -123.9143 | 46.1643
5A15 | 861513 | CPCC | CPCC732884 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_217580_1580467874 | 2011 | Before | 2011-11-23 13:07 | 2011-11-23 22:32 | 1 | 564.983 | 0 | 0 | 1 | Y | N | N | N | Y | 2011-11-22 to 2011-11-23 OR Clatsop | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: Burned off jumper. Crew made repairs. Customer back in full service. | DISTRIBUTION | CUSTOMER | AUTO |  | COMPLETED |  | 2011-11-23 13:07 | 2011-11-23 22:32 | 2011-11-23 22:51 | -123.9267 | 46.1634
5A15 | 860990 | CPCC | CPCC731798 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_222610_1580311775 | 2011 | Before | 2011-11-22 16:14 | 2011-11-22 22:51 | 17 | 6760.617 | 0 | 0 | 1 | Y | N | N | N | Y | 2011-11-22 to 2011-11-23 OR Clatsop | OTHER | OTHER, KNOWN CAUSE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman found open tapline fuses. Phases slapping together. Will re-fuse when wind calms down. | DISTRIBUTION | DEVICE | MANUAL | 2011-11-23 00:15 | COMPLETED |  | 2011-11-22 16:14 | 2011-11-22 22:51 | 2011-11-22 23:11 | -123.9143 | 46.1643
5A15 | 862054 | CPCC | CPCC733412 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_222610_1580311775 | 2011 | Before | 2011-11-26 19:37 | 2011-11-26 20:08 | 18 | 549.6 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | WEATHER | WIND | DEAD END B/O OH |  |  |  | SOURCE: Associated to outage 733405. Took outage for emergency repairs. Repairs complete. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2011-11-26 19:37 | 2011-11-26 20:08 | 2011-11-26 21:15 | -123.9143 | 46.1643
5A15 | 862055 | CPCC | CPCC733405 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_222610_1580311775 | 2011 | Before | 2011-11-26 17:07 | 2011-11-26 20:08 | 8 | 1449.6 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | DEAD END B/O OH |  |  |  | SOURCE: Serviceman arrived and found blown line fuse investigated to find low line needs 4 man crew. Wind broke dead end bells and primary dropped into the neutral. Repairs complete. | DISTRIBUTION | DEVICE | MANUAL | 2011-11-26 23:30 | COMPLETED |  | 2011-11-26 17:07 | 2011-11-26 20:08 | 2011-11-26 21:15 | -123.9143 | 46.1643
5A15 | 861539 | CPCC | CPCC732607 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_275804_915350408 | 2011 | Before | 2011-11-23 07:53 | 2011-11-24 01:14 | 1 | 1041.5 | 0 | 0 | 1 | Y | N | N | N | Y | 2011-11-22 to 2011-11-23 OR Clatsop | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Crew needed to remove a tree from the overhead neutral and pole. branch removed | DISTRIBUTION | CUSTOMER | AUTO |  | COMPLETED |  | 2011-11-23 07:53 | 2011-11-24 01:14 | 2011-11-24 03:01 | -123.9086 | 46.1536
5A15 | 860985 | CPCC | CPCC731991 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2011 | Before | 2011-11-22 21:35 | 2011-11-22 21:35 | 0 | 0 | 1784 | 148.667 | 1 | Y | N | N | N | Y | 2011-11-22 to 2011-11-23 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: T&R | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2011-11-22 21:35 | 2011-11-22 21:35 | 2011-11-22 22:42 | -123.9098 | 46.1511
5A15 | 862119 | CPCC | CPCC733431 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_165400_543460214 | 2011 | Before | 2011-11-27 09:17 | 2011-11-27 14:04 | 1 | 286.267 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | SOURCE: serviceman found odd voltage need 4 man crew to replace xfrmr. B/O 10kv xfrmr replaced it outage restored. | DISTRIBUTION | CUSTOMER | MANUAL | 2011-11-27 13:30 | COMPLETED |  | 2011-11-27 09:17 | 2011-11-27 14:04 | 2011-11-27 16:55 | -123.9292 | 46.1772
5A15 | 839663 | CPCC | CPCC723352 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2011 | Before | 2011-09-26 12:10 | 2011-09-26 12:10 | 0 | 0 | 1799 | 149.917 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: T&R due to tree branch | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 839666 | CPCC | CPCC723359 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_189840_825180286 | 2011 | Before | 2011-09-26 12:42 | 2011-09-26 14:24 | 14 | 1437.567 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Blown dip fuse. U/G cable also has a reverse riser at the other end with some overhead wire. Serviceman believes a limb on the overhead caused dip fuse to blow. Crew removed branch and replaced fuse. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9616 | 46.1821
5A15 | 841228 | CPCC | CPCC722700 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_215580_626300504 | 2011 | Before | 2011-09-19 20:10 | 2011-09-19 20:40 | 14 | 420 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | TRANSFORMER PADMOUNT/SUBMERSIBLE UG |  |  |  | PROSPER: Leaking transformer. Took outage to make repairs. Replaced transformer and customers are back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 837730 | CPCC | CPCC713340 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_089904_1580312224 | 2011 | Before | 2011-07-21 16:31 | 2011-07-21 18:51 | 1 | 139.55 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: Serviceman arrived and found b/o power bank needs crew to make repairs. Change cutout, made repairs and outage restored. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 839715 | CPCC | CPCC722317 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2011 | Before | 2011-09-17 14:51 | 2011-09-17 14:51 | 0 | 0 | 1799 | 149.917 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: T&R | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.9098 | 46.1511
5A15 | 839716 | CPCC | CPCC722319 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_089904_1580312224 | 2011 | Before | 2011-09-17 15:30 | 2011-09-17 16:37 | 1 | 67.183 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: T&R | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A15 | 876804 | CPCC | CPCC743741 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_217903_626300451 | 2012 | Before | 2012-01-20 22:20 | 2012-01-21 01:07 | 6 | 1003.1 | 0 | 0 | 1 | Y | N | N | N | Y | 2012-01-17 to 2012-01-21 OR CoastPlus | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Blown transformer fuse. Burnt up cutout door. Replaced and customers are back on. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-01-21 01:30 | COMPLETED |  | 2012-01-20 22:20 | 2012-01-21 01:07 | 2012-01-21 02:52 | -123.9251 | 46.1694
5A15 | 867505 | CPCC | CPCC734970 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2011 | Before | 2011-12-09 17:45 | 2011-12-09 17:45 | 0 | 0 | 1802 | 150.167 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | SOURCE: T and R. Primary wire down cause was deteriorated connector. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2011-12-09 17:45 | 2011-12-09 17:45 | 2011-12-09 20:56 | -123.9098 | 46.1511
5A15 | 879526 | CPCC | CPCC745591 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_091506_543460307 | 2012 | Before | 2012-01-30 07:42 | 2012-01-30 09:44 | 1 | 122.3 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: Serviceman replaced the B/O secondary connectors at the pole, customer is back in full service. | DISTRIBUTION | CUSTOMER | AUTO | 2012-01-30 10:45 | COMPLETED |  | 2012-01-30 07:42 | 2012-01-30 09:44 | 2012-01-30 12:46 | -123.937 | 46.1927
5A15 | 873465 | CPCC | CPCC739293 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_165608_543460213 | 2012 | Before | 2012-01-10 19:49 | 2012-01-10 20:41 | 1 | 52.233 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: tree branch rubbed through the service | DISTRIBUTION | CUSTOMER | AUTO | 2012-01-10 23:00 | COMPLETED |  | 2012-01-10 19:49 | 2012-01-10 20:41 | 2012-01-11 04:01 | -123.9296 | 46.1793
5A15 | 874711 | CPCC | CPCC740272 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_090600_543460289 | 2012 | Before | 2012-01-17 17:47 | 2012-01-17 19:18 | 9 | 819.75 | 0 | 0 | 1 | Y | N | N | N | Y | 2012-01-17 to 2012-01-21 OR CoastPlus | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Melted out fuse | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-01-17 21:00 | COMPLETED |  | 2012-01-17 17:47 | 2012-01-17 19:18 | 2012-01-17 22:37 | -123.9391 | 46.1947
5A15 | 867506 | CPCC | CPCC734971 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2011 | Before | 2011-12-09 17:45 | 2011-12-09 20:41 | 1803 | 317328 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | SOURCE: Line down Hwy 101 and King, crew responding. Crew reports that we have a deteriorated connector on primary. Repairs made and customers are back on. | DISTRIBUTION | DEVICE | AUTO | 2011-12-09 20:45 | COMPLETED |  | 2011-12-09 17:45 | 2011-12-09 20:55 | 2011-12-09 20:56 | -123.9098 | 46.1511
5A15 | 879527 | CPCC | CPCC745597 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_091500_543460309 | 2012 | Before | 2012-01-30 08:37 | 2012-01-30 09:44 | 1 | 67.45 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: Serviceman replaced the B/O secondary connectors at the pole, customer is back in full service. | DISTRIBUTION | CUSTOMER | AUTO | 2012-01-30 11:45 | COMPLETED |  | 2012-01-30 08:37 | 2012-01-30 09:44 | 2012-01-30 12:46 | -123.9375 | 46.193
5A15 | 865858 | CPCC | CPCC734242 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_165402_543460379 | 2011 | Before | 2011-12-04 10:09 | 2011-12-04 10:21 | 1 | 12.333 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Tree limb came down the to wind storm back on Nov 24th. Service finally went down. Cut service in the clear. Customer need electrician to make repairs. | DISTRIBUTION | CUSTOMER | AUTO | 2011-12-04 13:15 | COMPLETED |  | 2011-12-04 10:09 | 2011-12-04 10:21 | 2011-12-04 10:26 | -123.9284 | 46.1762
5A15 | 895978 | CPCC | CPCC762452 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2012 | Before | 2012-03-31 02:06 | 2012-03-31 02:06 | 0 | 0 | 1802 | 60.067 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CROSS ARM OH |  |  |  | SOURCE: T and R. wire down | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-03-31 02:06 | 2012-03-31 02:06 | 2012-03-31 10:45 | -123.9098 | 46.1511
5A15 | 896004 | CPCC | CPCC762695 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_222610_1580502271 | 2012 | Before | 2012-03-31 10:35 | 2012-03-31 11:34 | 14 | 830.9 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | CROSS ARM OH |  |  |  | SOURCE: open fuses to replace x arm and wire down with outage 762669 | DISTRIBUTION | DEVICE | MANUAL | 2012-03-31 16:45 | COMPLETED |  | 2012-03-31 10:35 | 2012-03-31 11:34 | 2012-03-31 11:36 | -123.9143 | 46.1643
5A15 | 889201 | CPCC | CPCC753737 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_217704_626300455 | 2012 | Before | 2012-03-12 15:26 | 2012-03-12 15:48 | 1 | 22.1 | 0 | 0 | 1 | Y | N | N | N | Y | 2012-03-12 to 2012-03-13 OR CoastPlus | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | CONNECTOR OH |  |  |  | SOURCE: Serviceman opened x-fmr to make repairs to b/o secondary connector. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2012-03-12 15:26 | 2012-03-12 15:48 | 2012-03-12 17:10 | -123.9251 | 46.1671
5A15 | 896799 | CPCC | CPCC763418 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_216305_626300604 | 2012 | Before | 2012-04-02 09:17 | 2012-04-02 10:46 | 1 | 89.333 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman replaced the B/O secondary service, customer is back in full service. | DISTRIBUTION | CUSTOMER | AUTO | 2012-04-02 12:30 | COMPLETED |  | 2012-04-02 09:17 | 2012-04-02 10:46 | 2012-04-02 15:37 | -123.9267 | 46.1607
5A15 | 895298 | CPCC | CPCC761722 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | Line Cut-60236 | 2012 | Before | 2012-03-29 01:12 | 2012-03-29 03:30 | 46 | 6357.967 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: Serviceman found broken jumper, will make repairs, need 3 man crew. Repairs made, | DISTRIBUTION | DEVICE | AUTO | 2012-03-29 04:15 | COMPLETED |  | 2012-03-29 01:12 | 2012-03-29 03:30 | 2012-03-29 06:05 | -123.9291 | 46.1849
5A15 | 895316 | CPCC | CPCC761756 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_222610_1580311775 | 2012 | Before | 2012-03-29 04:49 | 2012-03-29 06:31 | 19 | 1929.133 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman arrived and found 2 blown fuses will patrol and report. Nothing found on patrol closed fuses on test and they held. | DISTRIBUTION | DEVICE | AUTO | 2012-03-29 08:00 | COMPLETED |  | 2012-03-29 04:49 | 2012-03-29 06:31 | 2012-03-29 06:35 | -123.9143 | 46.1643
5A15 | 896005 | CPCC | CPCC762669 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_222610_1580502271 | 2012 | Before | 2012-03-31 09:00 | 2012-03-31 11:34 | 2 | 308.633 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CROSS ARM OH |  |  |  | SOURCE: blown line fuse wire down need crew | DISTRIBUTION | DEVICE | MANUAL | 2012-03-31 15:00 | COMPLETED |  | 2012-03-31 09:00 | 2012-03-31 11:34 | 2012-03-31 11:36 | -123.9143 | 46.1643
5A15 | 905646 | CPCC | CPCC769301 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_173300_825180531 | 2012 | Before | 2012-05-12 11:57 | 2012-05-12 15:24 | 1 | 206.333 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: crew to replace cut out | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2012-05-12 17:00 | COMPLETED |  | 2012-05-12 11:57 | 2012-05-12 15:24 | 2012-05-12 15:54 | -123.9553 | 46.1745
5A15 | 890440 | CPCC | CPCC756110 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2012 | Before | 2012-03-15 02:54 | 2012-03-15 02:54 | 0 | 0 | 1802 | 150.167 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: T&R cause unknown | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-03-15 02:54 | 2012-03-15 02:54 | 2012-03-15 06:45 | -123.9098 | 46.1511
5A15 | 895489 | CPCC | CPCC761967 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_068204_825180411 | 2012 | Before | 2012-03-29 10:12 | 2012-03-29 11:25 | 1 | 73.383 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Open secondary due to wind. Serviceman made repairs to secondary. | DISTRIBUTION | CUSTOMER | AUTO | 2012-03-29 13:15 | COMPLETED |  | 2012-03-29 10:12 | 2012-03-29 11:26 | 2012-03-29 15:20 | -123.9647 | 46.2027
5A15 | 926810 | CPCC | CPCC780964 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_089882_825180265 | 2012 | Before | 2012-07-24 16:37 | 2012-07-24 18:56 | 6 | 838.2 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | TRANSFORMER PADMOUNT/SUBMERSIBLE UG |  |  |  | SOURCE: partial power on need crew to replace padmount transformer | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-07-24 19:45 | COMPLETED |  | 2012-07-24 16:37 | 2012-07-24 18:56 | 2012-07-24 19:01 | -123.9432 | 46.1964
5A15 | 916870 | CPCC | CPCC775328 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_091500_543460309 | 2012 | Before | 2012-06-25 09:32 | 2012-06-25 10:38 | 5 | 332 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: Crew making repairs to b/o connectors. | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2012-06-25 11:45 | COMPLETED |  | 2012-06-25 09:32 | 2012-06-25 10:38 | 2012-06-25 14:36 | -123.9375 | 46.193
5A15 | 924315 | CPCC | CPCC779455 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_166180_543460407 | 2012 | Before | 2012-07-17 09:04 | 2012-07-17 09:10 | 16 | 99.733 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | SECONDARY CABLE UG |  |  |  | SOURCE: serviceman complete customers are back in service | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2012-07-17 09:04 | 2012-07-17 09:10 | 2012-07-17 09:17 | -123.9268 | 46.1719
5A15 | 1304144 | CPCC | CPCC785799 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_053107_825180331 | 2012 | Before | 2012-08-25 13:45 | 2012-08-25 14:41 | 5 | 281.75 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | TRANSFORMER OH |  |  |  | SOURCE: crew to replace transformer | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-08-25 16:45 | COMPLETED |  | 2012-08-25 13:45 | 2012-08-25 14:41 | 2012-08-25 16:10 | -123.9542 | 46.2016
5A15 | 1325353 | CPCC | CPCC797858 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | Line Cut-68895 | 2012 | Before | 2012-11-19 07:51 | 2012-11-19 15:38 | 1808 | 845240 | 0 | 0 | 1 | Y | N | N | N | Y | 11-19-2012 to 11-20-2012 OR CoastPlus | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Loss of transmission | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-11-19 08:06 | 2012-11-19 15:42 | 2012-11-19 23:40 | -123.9098 | 46.1508
5A15 | 1328444 | CPCC | CPCC802150 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2012 | Before | 2012-12-01 10:06 | 2012-12-01 10:06 | 0 | 0 | 1808 | 150.667 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: T & R caused by line down from broken conductor (bird weight) See outage #802152 | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-12-01 10:06 | 2012-12-01 10:06 | 2012-12-01 16:40 | -123.9098 | 46.1511
5A15 | 1320859 | CPCC | CPCC795999 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_057005_825180386 | 2012 | Before | 2012-11-08 05:25 | 2012-11-08 07:26 | 6 | 726.4 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | SOURCE: Serviceman reports outage caused by bad transformer, crew needed to replace. Crew made repairs. Outage resolved. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-11-08 08:30 | COMPLETED |  | 2012-11-08 05:25 | 2012-11-08 07:26 | 2012-11-08 07:30 | -123.9471 | 46.1992
5A15 | 1319081 | CPCC | CPCC794898 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_215680_626300503 | 2012 | Before | 2012-10-29 06:41 | 2012-10-29 12:14 | 29 | 9653.133 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | TRANSFORMER PADMOUNT/SUBMERSIBLE UG |  |  |  | SOURCE: crew complete with necessary repairs, customers are back in service | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2012-10-29 12:00 | COMPLETED |  | 2012-10-29 06:41 | 2012-10-29 12:14 | 2012-10-29 13:45 | -123.9287 | 46.1645
5A15 | 1324599 | CPCC | CPCC797450 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_082906_825180280 | 2012 | Before | 2012-11-18 21:58 | 2012-11-18 22:43 | 109 | 4943.15 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Part of outage#797382 Crew opened fuses for safe work practice on line down. Work completed. | DISTRIBUTION | DEVICE | AUTO | 2012-11-19 01:00 | COMPLETED |  | 2012-11-18 21:58 | 2012-11-21 09:01 | 2012-11-19 04:06 | -123.9551 | 46.1989
5A15 | 1314898 | CPCC | CPCC791794 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_052003_825180345 | 2012 | Before | 2012-10-12 20:20 | 2012-10-13 02:10 | 83 | 17810.784 | 0 | 0 | 2 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman found center phase fuse blown @ 052003. Serviceman found tree took down line at 079901. Repaired line & restored power | DISTRIBUTION | DEVICE | MANUAL | 2012-10-13 00:45 | COMPLETED |  | 2012-10-12 20:33 | 2012-10-13 02:48 | 2012-10-13 07:46 | -123.9554 | 46.1992
5A15 | 1314905 | CPCC | CPCC791785 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2012 | Before | 2012-10-12 20:17 | 2012-10-12 20:17 | 0 | 0 | 1808 | 90.4 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: T & R was caused by pole fire due to bird of prey nesting PROSPER: tree through line on CPCC791794 | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-10-12 20:17 | 2012-11-05 13:17 | 2012-10-13 07:56 | -123.9098 | 46.1511
5A15 | 1315504 | CPCC | CPCC792403 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_216300_626300607 | 2012 | Before | 2012-10-15 16:54 | 2012-10-15 20:14 | 1 | 200.45 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Tree rubbed through secondary service. Crew made repairs. | DISTRIBUTION | CUSTOMER | AUTO | 2012-10-15 20:00 | COMPLETED |  | 2012-10-15 16:54 | 2012-10-15 20:14 | 2012-10-15 20:26 | -123.9272 | 46.1599
5A15 | 1325364 | CPCC | CPCC797691 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2012 | Before | 2012-11-19 07:30 | 2012-11-19 07:31 | 0 | 0 | 1808 | 421.867 | 1 | Y | N | N | N | Y | 11-19-2012 to 11-20-2012 OR CoastPlus | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: T&R due to tree in the line | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-11-19 07:30 | 2012-11-19 07:31 | 2012-11-19 23:50 | -123.9098 | 46.1511
5A15 | 1324545 | CPCC | CPCC797371 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2012 | Before | 2012-11-18 17:53 | 2012-11-18 17:53 | 0 | 0 | 1808 | 60.267 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: T and R. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-11-18 17:53 | 2012-11-18 17:53 | 2012-11-18 19:55 | -123.9098 | 46.1511
5A15 | 1325741 | CPCC | CPCC798911 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_221307_626300685 | 2012 | Before | 2012-11-19 16:13 | 2012-11-20 09:16 | 1 | 1022.833 | 0 | 0 | 1 | Y | N | N | N | Y | 11-19-2012 to 11-20-2012 OR CoastPlus | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Tree on service, crew needed. | DISTRIBUTION | CUSTOMER | AUTO |  | COMPLETED |  | 2012-11-19 16:13 | 2012-11-20 09:16 | 2012-11-20 12:41 | -123.9172 | 46.1608
5A15 | 1328446 | CPCC | CPCC802152 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_165715_543460363 | 2012 | Before | 2012-12-01 10:10 | 2012-12-01 13:28 | 16 | 3163.2 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD SUSPECTED, NO MORTALITY |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman found blown fuse @ 165715, line down @ 164701. 3 man crew called out and enroute. Cause was bird weight (flock of birds on #6 copper took line down). Line repaired, power restored. | DISTRIBUTION | DEVICE | AUTO | 2012-12-01 13:15 | COMPLETED |  | 2012-12-01 10:10 | 2013-01-07 14:13 | 2012-12-01 16:40 | -123.93 | 46.18
5A15 | 1324598 | CPCC | CPCC797382 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_082906_825180280 | 2012 | Before | 2012-11-18 19:13 | 2012-11-18 22:43 | 23 | 4829.567 | 0 | 0 | 2 | Y | N | N | N | N |  | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman arrived and found blown line fuse, will patrol and report. Serviceman found line down, needs 3 man crew to repair. He will open remaining phases to mitigate backfeed. Repairs made. | DISTRIBUTION | DEVICE | AUTO | 2012-11-18 22:15 | COMPLETED |  | 2012-11-18 19:13 | 2012-11-18 22:43 | 2012-11-19 04:06 | -123.9551 | 46.1989
5A15 | 1324544 | CPCC | CPCC797373 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_222500_626300669 | 2012 | Before | 2012-11-18 18:16 | 2012-11-18 18:48 | 1 | 32.75 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | OTHER, KNOWN CAUSE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Secondary lead pulled out of transformer, no damage. Repairs made and customers are back on. | DISTRIBUTION | CUSTOMER | AUTO | 2012-11-18 21:15 | COMPLETED |  | 2012-11-18 18:16 | 2012-11-18 18:48 | 2012-11-18 19:55 | -123.9144 | 46.1634
5A15 | 1318997 | CPCC | CPCC794894 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2012 | Before | 2012-10-29 06:04 | 2012-10-29 06:04 | 0 | 0 | 1808 | 150.667 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | LOAD BREAK ELBOW UG |  |  |  | SOURCE: T & R at substation due to a deteriorated elbow on outage 369978 | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-10-29 06:04 | 2012-10-29 06:04 | 2012-10-29 08:25 | -123.9098 | 46.1511
5A15 | 1333431 | CPCC | CPCC807178 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_165900_543460362 | 2012 | Before | 2012-12-18 06:39 | 2012-12-18 09:27 | 2 | 336.6 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Blown fuse due to downed copper service. Crew made repairs. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-12-18 09:45 | COMPLETED |  | 2012-12-18 06:39 | 2012-12-18 09:27 | 2012-12-18 16:00 | -123.9296 | 46.1841
5A15 | 1333434 | CPCC | CPCC807236 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_222705_626300657 | 2012 | Before | 2012-12-18 11:15 | 2012-12-18 11:42 | 1 | 27 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: B/O secondary connector. Serviceman replaced it. | DISTRIBUTION | CUSTOMER | AUTO | 2012-12-18 14:15 | COMPLETED |  | 2012-12-18 11:15 | 2012-12-18 11:42 | 2012-12-18 16:01 | -123.9147 | 46.1663
5A15 | 1338971 | CPCC | CPCC815741 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | Line Cut-71811 | 2013 | Before | 2013-01-07 09:24 | 2013-01-07 09:43 | 10 | 186.833 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | INTENTIONAL TO CLEAR TROUBLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: crew needed to open the tap line to remove a bird from the line. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2013-01-07 09:24 | 2013-01-07 09:43 | 2013-01-07 16:40 | -123.9271 | 46.1659
5A15 | 1332999 | CPCC | CPCC806279 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | Line Cut-70254 | 2012 | Before | 2012-12-17 01:30 | 2012-12-17 15:47 | 1808 | 961598.65 | 0 | 0 | 4 | Y | N | N | Y | Y | 2012-12-15 to 2012-12-17 OR CoastPlus | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: CB 5A15 locked open due to wire down. Crew made repairs. All customers back on except 1. Crew made repairs to last customer. All customers on. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-12-17 02:16 | 2012-12-17 15:47 | 2012-12-17 15:59 | -123.9095 | 46.1516
5A15 | 1344980 | CPCC | CPCC819357 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_069143_825180413 | 2013 | Before | 2013-02-07 13:34 | 2013-02-07 14:35 | 1 | 60.833 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: Serviceman replaced b/o secondary connector. | DISTRIBUTION | CUSTOMER | AUTO | 2013-02-07 16:45 | COMPLETED |  | 2013-02-07 13:34 | 2013-02-07 14:35 | 2013-02-07 16:00 | -123.963 | 46.201
5A15 | 1347078 | CPCC | CPCC820619 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_187800_1580419676 | 2013 | Before | 2013-02-21 09:35 | 2013-02-21 10:49 | 3 | 221.7 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | B/O EQUIPMENT | CROSS ARM OH |  |  |  | SOURCE: Crew took emergency outage to replace b/o crossarm. | DISTRIBUTION | DEVICE | MANUAL | 2013-02-21 12:00 | COMPLETED |  | 2013-02-21 09:35 | 2013-02-21 10:49 | 2013-02-21 11:25 | -123.965 | 46.1813
5A15 | 1344875 | CPCC | CPCC819317 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_216406_626300595 | 2013 | Before | 2013-02-06 22:35 | 2013-02-06 23:09 | 4 | 132.933 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | DETERIORATION OR ROTTING | CONNECTOR OH |  |  |  | SOURCE: Serviceman decided to deenergize xfrmr to repair connector. Part of outage 819316. Bad modelling.Repairs made outage resolved. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-02-07 01:45 | COMPLETED |  | 2013-02-06 22:35 | 2013-02-07 13:34 | 2013-02-07 00:45 | -123.9259 | 46.1619
5A15 | 1344876 | CPCC | CPCC819316 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_216406_626300595 | 2013 | Before | 2013-02-06 22:10 | 2013-02-06 23:08 | 1 | 58.317 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | SOURCE: Bad secondary connection. Serviceman made repairs. | DISTRIBUTION | CUSTOMER | AUTO | 2013-02-07 01:15 | COMPLETED |  | 2013-02-06 22:10 | 2013-02-06 23:08 | 2013-02-07 00:45 | -123.9259 | 46.1619
5A15 | 1352556 | CPCC | CPCC824335 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_223700_626300658 | 2013 | Before | 2013-03-21 11:23 | 2013-03-21 12:09 | 1 | 45.45 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Truck damaged o/h service. Serviceman making repairs. | DISTRIBUTION | CUSTOMER | AUTO | 2013-03-21 14:30 | COMPLETED |  | 2013-03-21 11:23 | 2013-03-21 12:09 | 2013-03-21 13:45 | -123.9128 | 46.166
5A15 | 1352142 | CPCC | CPCC824082 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_165402_543460379 | 2013 | Before | 2013-03-20 10:01 | 2013-03-20 10:52 | 1 | 51.55 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: Serviceman replaced the B/O overhead secondary neutral connector, customer is back in full service. | DISTRIBUTION | CUSTOMER | AUTO | 2013-03-20 13:00 | COMPLETED |  | 2013-03-20 10:01 | 2013-03-20 10:52 | 2013-03-20 11:26 | -123.9284 | 46.1762
5A15 | 1362991 | CPCC | CPCC830955 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2013 | Before | 2013-05-07 02:00 | 2013-05-07 02:00 | 0 | 0 | 1812 | 151 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: T and R. Bad order UG. Outage 830956. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2013-05-07 02:00 | 2013-05-07 02:00 | 2013-05-07 06:47 | -123.9098 | 46.1511
5A15 | 1367609 | CPCC | CPCC833965 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | Line Cut-75193 | 2013 | Before | 2013-05-23 21:59 | 2013-05-23 22:03 | 0 | 0 | 1813 | 7252 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE | TREES | TREE - NON-PREVENTABLE | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Loss of transmission due to a tree in the 115 KV line | DISTRIBUTION | DEVICE | AUTO | 2013-05-24 01:15 | COMPLETED |  | 2013-05-23 22:02 | 2013-05-24 09:46 | 2013-05-24 03:51 | -123.9097 | 46.1509
5A15 | 1365670 | CPCC | CPCC832925 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_165402_543460379 | 2013 | Before | 2013-05-16 18:39 | 2013-05-16 20:05 | 7 | 605.85 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Broken transformer fuse, refused and customers are back on. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-05-16 21:45 | COMPLETED |  | 2013-05-16 18:39 | 2013-05-20 13:59 | 2013-05-16 20:32 | -123.9284 | 46.1762
5A15 | 1366579 | CPCC | CPCC833182 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | Line Cut-75078 | 2013 | Before | 2013-05-20 09:49 | 2013-05-20 12:31 | 7 | 1137.267 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | B/O EQUIPMENT | POLE OH |  |  |  | SOURCE: Crew took outage to replace b/o pole | DISTRIBUTION | DEVICE | MANUAL | 2013-05-20 13:00 | COMPLETED |  | 2013-05-20 09:49 | 2013-05-20 12:31 | 2013-05-20 15:25 | -123.9246 | 46.1736
5A15 | 1372294 | CPCC | CPCC836882 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_165503_543460369 | 2013 | Before | 2013-06-13 09:47 | 2013-06-13 09:55 | 24 | 183.6 | 0 | 0 | 1 | Y | N | N | N | Y | 06/13/2013 0:00:00 to 06/13/2013 23:59:59 OR CoastPlus | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | DETERIORATION OR ROTTING | PRIMARY CABLE UG |  |  |  | SOURCE: Crew took outage to make repairs to u/g primary cable in riser on pole. | DISTRIBUTION | DEVICE | MANUAL | 2013-06-13 11:00 | COMPLETED |  | 2013-06-13 09:47 | 2013-06-13 09:55 | 2013-06-13 11:46 | -123.9296 | 46.1778
5A15 | 1362992 | CPCC | CPCC830956 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_215904_1580006860 | 2013 | Before | 2013-05-07 02:02 | 2013-05-07 06:44 | 31 | 8067.683 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Page sent. Blown dip fuse. Bad order UG. | DISTRIBUTION | DEVICE | MANUAL | 2013-05-07 09:00 | COMPLETED |  | 2013-05-07 02:02 | 2013-05-07 06:44 | 2013-05-07 06:47 | -123.9298 | 46.1694
5A15 | 1367450 | CPCC | CPCC833890 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_167203_543460384 | 2013 | Before | 2013-05-23 12:00 | 2013-05-23 13:24 | 1 | 83.85 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: Serviceman replaced b/o secondary connector. | DISTRIBUTION | CUSTOMER | AUTO | 2013-05-23 15:00 | COMPLETED |  | 2013-05-23 12:00 | 2013-05-23 13:24 | 2013-05-23 14:21 | -123.9253 | 46.174
5A15 | 1387253 | CPCC | CPCC844218 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2013 | Before | 2013-07-31 08:42 | 2013-07-31 08:42 | 0 | 0 | 1813 | 151.083 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: T&R due to b/o ug primary | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2013-07-31 08:42 | 2013-07-31 08:42 | 2013-07-31 15:11 | -123.9098 | 46.1511
5A15 | 1387533 | CPCC | CPCC844371 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_214604_626300532 | 2013 | Before | 2013-08-01 08:52 | 2013-08-01 09:34 | 4 | 167.667 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Deteriorated x-fmr fuse. Serviceman replaced fuse and it held. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-08-01 12:00 | COMPLETED |  | 2013-08-01 08:52 | 2013-08-01 09:34 | 2013-08-01 12:37 | -123.9316 | 46.1646
5A15 | 1382681 | CPCC | CPCC842258 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2013 | Before | 2013-07-16 20:48 | 2013-07-16 20:48 | 0 | 0 | 1723 | 143.583 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: T&R | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2013-07-16 20:48 | 2013-07-16 20:48 | 2013-07-16 21:45 | -123.9098 | 46.1511
5A15 | 1397883 | CPCC | CPCC850410 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2013 | Before | 2013-08-27 09:25 | 2013-08-27 09:25 | 0 | 0 | 1813 | 151.083 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD SUSPECTED, NO MORTALITY |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: T & R, Serviceman replaced fuse and power is restored. Suspected bird. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2013-08-27 09:25 | 2013-08-27 09:25 | 2013-08-27 16:02 | -123.9098 | 46.1511
5A15 | 1382644 | CPCC | CPCC842192 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2013 | Before | 2013-07-16 17:21 | 2013-07-16 17:21 | 0 | 0 | 1813 | 151.083 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: T&R Bad Pri UG, mapping is such that it cant be modeled at this time | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2013-07-16 17:21 | 2013-07-17 15:32 | 2013-07-16 20:39 | -123.9098 | 46.1511
5A15 | 1397881 | CPCC | CPCC850414 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_089904_1580312224 | 2013 | Before | 2013-08-27 09:33 | 2013-08-27 10:16 | 1 | 42.983 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD SUSPECTED, NO MORTALITY |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman replaced fuse and power is restored. Suspected bird. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-08-27 12:45 | COMPLETED |  | 2013-08-27 09:33 | 2013-08-27 10:16 | 2013-08-27 16:02 | -123.9425 | 46.1976
5A15 | 1395892 | CPCC | CPCC847952 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_089700_543460285 | 2013 | Before | 2013-08-22 11:24 | 2013-08-22 12:19 | 1 | 54.483 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: Serviceman replaced b/o secondary connectors at the x-fmr bank. | DISTRIBUTION | CUSTOMER | AUTO | 2013-08-22 14:30 | COMPLETED |  | 2013-08-22 11:24 | 2013-08-22 12:19 | 2013-08-22 13:50 | -123.9417 | 46.1959
5A15 | 1387252 | CPCC | CPCC844223 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_079904_825180484 | 2013 | Before | 2013-07-31 08:51 | 2013-07-31 11:37 | 19 | 3154.467 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Crew isolated the B/O underground primary between transformer# 079880 and transformer# 079780. Customers are back in full service. | DISTRIBUTION | DEVICE | MANUAL | 2013-07-31 13:30 | COMPLETED |  | 2013-07-31 08:51 | 2013-07-31 11:37 | 2013-07-31 15:11 | -123.9626 | 46.1979
5A15 | 1382716 | CPCC | CPCC842196 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_167105_543460381 | 2013 | Before | 2013-07-16 17:24 | 2013-07-16 23:26 | 91 | 32966.297 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: bad pri UG, crew to make repairs | DISTRIBUTION | DEVICE | MANUAL | 2013-07-17 00:30 | COMPLETED |  | 2013-07-16 17:24 | 2013-07-17 15:33 | 2013-07-16 23:31 | -123.9248 | 46.1721
5A15 | 1382722 | CPCC | CPCC842264 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2013 | Before | 2013-07-16 21:56 | 2013-07-16 21:56 | 0 | 0 | 1723 | 86.15 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: crew testing pri ug | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2013-07-16 21:56 | 2013-07-16 21:56 | 2013-07-16 23:35 | -123.9098 | 46.1511
5A15 | 1411877 | CPCC | CPCC860958 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_215904_1580006860 | 2013 | Before | 2013-10-06 12:29 | 2013-10-06 14:23 | 15 | 1710.25 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | LIGHTNING ARRESTER OH |  |  |  | SOURCE: serviceman stated that thee was a blown fuse, will get crew to begin testing the primary, crw found a blown arrestor, will change it out | DISTRIBUTION | DEVICE | AUTO | 2013-10-06 16:00 | COMPLETED |  | 2013-10-06 12:54 | 2013-10-06 14:23 | 2013-10-06 15:40 | -123.9298 | 46.1694
5A15 | 1423950 | CPCC | CPCC867518 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | Line Cut-81270 | 2013 | Before | 2013-11-23 15:56 | 2013-11-23 17:06 | 122 | 8588.8 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | B/O EQUIPMENT | INSULATOR OH |  |  |  | SOURCE: open line fuse replace arm and glass | DISTRIBUTION | DEVICE | MANUAL | 2013-11-23 21:27 | COMPLETED |  | 2013-11-23 15:56 | 2013-11-23 17:06 | 2013-11-23 17:09 | -123.9244 | 46.1651
5A15 | 1407485 | CPCC | CPCC857022 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_222610_1580311775 | 2013 | Before | 2013-09-27 06:58 | 2013-09-27 09:21 | 27 | 3859.65 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman reports fuses open at FP 222610, no cause found. He will close in for test and report. Serviceman close in and circuit held. | DISTRIBUTION | DEVICE | AUTO | 2013-09-27 10:00 | COMPLETED |  | 2013-09-27 06:58 | 2013-09-27 09:21 | 2013-09-27 09:40 | -123.9143 | 46.1643
5A15 | 1416658 | CPCC | CPCC863575 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_165080_543460375 | 2013 | Before | 2013-10-24 16:02 | 2013-10-24 18:07 | 1 | 125.25 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | SOURCE: Serviceman found bad leg on secondary ug service. Called out 1 extra guy to help install service saver | DISTRIBUTION | CUSTOMER | AUTO | 2013-10-24 19:15 | COMPLETED |  | 2013-10-24 16:02 | 2013-10-24 18:08 | 2013-10-24 18:18 | -123.9284 | 46.1703
5A15 | 1410818 | CPCC | CPCC860625 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_221601_626300410 | 2013 | Before | 2013-10-03 14:52 | 2013-10-03 16:20 | 1 | 88.267 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | SOURCE: Serviceman replaced the deteriorated secondary connectors at the transformer, customer is back in full service. | DISTRIBUTION | CUSTOMER | AUTO | 2013-10-03 18:00 | COMPLETED |  | 2013-10-03 14:52 | 2013-10-03 16:20 | 2013-10-03 16:27 | -123.9173 | 46.1646
5A15 | 1417969 | CPCC | CPCC864500 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | Line Cut-80800 | 2013 | Before | 2013-10-29 10:57 | 2013-10-29 11:36 | 48 | 1868 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | INSULATOR OH |  |  |  | SOURCE: Serviceman report broken primary insulator with primary wire down on house. he opened jumpers at FP 069140 to isolate. Crew has made repairs and power is normal. | DISTRIBUTION | DEVICE | MANUAL | 2013-10-29 14:00 | COMPLETED |  | 2013-10-29 10:57 | 2013-10-29 11:36 | 2013-10-29 15:09 | -123.9631 | 46.2015
5A15 | 1416421 | CPCC | CPCC863172 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2013 | Before | 2013-10-22 23:59 | 2013-10-22 23:59 | 0 | 0 | 1814 | 151.167 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: T&R unknown cause | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2013-10-22 23:59 | 2013-10-22 23:59 | 2013-10-23 17:24 | -123.9098 | 46.1511
5A15 | 1411878 | CPCC | CPCC860949 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2013 | Before | 2013-10-06 12:21 | 2013-10-06 12:21 | 0 | 0 | 1814 | 151.167 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | LIGHTNING ARRESTER OH |  |  |  | SOURCE: T&R due to bad lightning arrestor | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2013-10-06 12:21 | 2013-10-06 12:21 | 2013-10-06 15:41 | -123.9098 | 46.1511
5A15 | 1406140 | CPCC | CPCC856238 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_216705_626300477 | 2013 | Before | 2013-09-22 09:52 | 2013-09-22 13:15 | 6 | 1218.9 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: crew replaced cut out | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-09-22 13:00 | COMPLETED |  | 2013-09-22 09:52 | 2013-09-22 13:15 | 2013-09-22 16:57 | -123.9277 | 46.1662
5A15 | 1416513 | CPCC | CPCC863421 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_087906_825180261 | 2013 | Before | 2013-10-23 18:10 | 2013-10-24 03:03 | 1 | 533.417 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | SOURCE: Crew arrived from portland, and will change out b/o xfrmr. crew replaced xfrmr. Outage restored | DISTRIBUTION | CUSTOMER | MANUAL | 2013-10-24 03:00 | COMPLETED |  | 2013-10-23 18:10 | 2013-10-24 03:03 | 2013-10-24 10:54 | -123.9455 | 46.1977
5A15 | 1407425 | CPCC | CPCC857010 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2013 | Before | 2013-09-27 03:38 | 2013-09-27 03:39 | 0 | 0 | 1814 | 151.167 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: T&R | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2013-09-27 03:38 | 2013-09-27 03:39 | 2013-09-27 06:36 | -123.9098 | 46.1511
5A15 | 1445074 | CPCC | CPCC885913 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_082001_825180417 | 2014 | Before | 2014-02-18 12:00 | 2014-02-18 12:51 | 2 | 101.467 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: Serviceman reports blown fuse on transformer due to b/o high side jumper. Crew made repairs. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-02-18 15:00 | COMPLETED |  | 2014-02-18 12:00 | 2014-02-18 12:51 | 2014-02-18 13:13 | -123.9561 | 46.1846
5A15 | 1437178 | CPCC | CPCC876678 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_217606_626300488 | 2014 | Before | 2014-01-20 15:52 | 2014-01-20 17:31 | 1 | 98.4 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman on another line down, will get to when finished with crew. Telco equipment was damaged and 1 service tore down. Repairs made to service. | DISTRIBUTION | CUSTOMER | AUTO | 2014-01-20 19:00 | COMPLETED |  | 2014-01-20 15:52 | 2014-01-20 17:31 | 2014-01-20 18:24 | -123.9255 | 46.1655
5A15 | 1435279 | CPCC | CPCC875584 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | Line Cut-82199 | 2014 | Before | 2014-01-11 19:33 | 2014-01-11 20:15 | 1816 | 76665.467 | 0 | 0 | 1 | Y | N | N | N | Y | 2014/01/11 to 2014/01/11 OR CoastPlus | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE | TREES | TREE - NON-PREVENTABLE | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Loss of transmission. Tree in Transmission line,. PROSPER: Changed Direct Cause from Tree. | DISTRIBUTION | DEVICE | AUTO | 2014-01-11 22:45 | COMPLETED |  | 2014-01-11 19:34 | 2014-01-22 13:21 | 2014-01-11 21:23 | -123.9097 | 46.151
5A15 | 1431507 | CPCC | CPCC872072 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_164701_543460244 | 2013 | Before | 2013-12-23 10:08 | 2013-12-23 10:50 | 7 | 298.433 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: Serviceman reports broken jumper on transformer cut-out. He has called for crew to help make repairs. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-12-23 13:15 | COMPLETED |  | 2013-12-23 10:08 | 2013-12-23 10:50 | 2013-12-23 16:04 | -123.9322 | 46.1802
5A15 | 1427076 | CPCC | CPCC869159 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2013 | Before | 2013-12-06 13:13 | 2013-12-06 13:13 | 0 | 0 | 1816 | 151.333 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: T&R at Substation | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2013-12-06 13:13 | 2013-12-06 13:13 | 2013-12-06 16:54 | -123.9098 | 46.1511
5A15 | 1429943 | CPCC | CPCC871582 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2013 | Before | 2013-12-18 00:04 | 2013-12-18 00:04 | 0 | 0 | 1816 | 151.333 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: T&R | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2013-12-18 00:04 | 2013-12-18 00:04 | 2013-12-18 16:59 | -123.9098 | 46.1511
5A15 | 1439872 | CPCC | CPCC878386 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_165501_543460352 | 2014 | Before | 2014-02-04 09:45 | 2014-02-04 11:07 | 15 | 1236.25 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman refused transformer# 165501 and it held, the cause was a rotted fuse, customers are back in full service. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-02-04 12:45 | COMPLETED |  | 2014-02-04 09:45 | 2014-02-04 11:07 | 2014-02-04 12:38 | -123.9296 | 46.1782
5A15 | 1457010 | CPCC | CPCC892847 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_216305_626300604 | 2014 | Before | 2014-04-11 15:31 | 2014-04-11 16:18 | 1 | 46.867 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Garbage truck tore down service and customers meterbase. Serviceman made repairs to service wire but can not be reconnected until customer makes repairs to meterbase. | DISTRIBUTION | CUSTOMER | AUTO | 2014-04-11 18:45 | COMPLETED |  | 2014-04-11 15:31 | 2014-04-11 16:18 | 2014-04-11 16:28 | -123.9267 | 46.1607
5A15 | 1463041 | CPCC | CPCC895858 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_167105_543460382 | 2014 | Before | 2014-05-01 13:29 | 2014-05-01 16:09 | 56 | 7766.147 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | LOAD BREAK ELBOW UG |  |  |  | SOURCE: Blown dip fuse due to b/o elbow. Crew made repairs. PROSPER: Bad modeling. Added 20 customers to CPCC895858. | DISTRIBUTION | DEVICE | MANUAL | 2014-05-01 17:00 | COMPLETED |  | 2014-05-01 13:29 | 2014-05-02 08:37 | 2014-05-01 16:14 | -123.9248 | 46.1721
5A15 | 1466426 | CPCC | CPCC897399 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_220401_626300682 | 2014 | Before | 2014-05-14 08:12 | 2014-05-14 09:33 | 3 | 240.35 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: B/O cut-out. Crew to replace. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-05-14 11:15 | COMPLETED |  | 2014-05-14 08:12 | 2014-05-14 09:33 | 2014-05-14 16:24 | -123.919 | 46.1615
5A15 | 1448840 | CPCC | CPCC888080 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_216307_626300603 | 2014 | Before | 2014-03-06 07:18 | 2014-03-06 08:40 | 7 | 577.033 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: serviceman states that there is a broken jumper, will make repairs | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-03-06 10:30 | COMPLETED |  | 2014-03-06 07:18 | 2014-03-06 08:40 | 2014-03-06 15:53 | -123.926 | 46.1608
5A15 | 1465372 | CPCC | CPCC897172 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_086904_825180448 | 2014 | Before | 2014-05-11 20:21 | 2014-05-11 21:02 | 5 | 201.333 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Deteriorated xfmr fuse. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-05-11 23:30 | COMPLETED |  | 2014-05-11 20:21 | 2014-05-11 21:02 | 2014-05-11 21:08 | -123.9479 | 46.1989
5A15 | 1463044 | CPCC | CPCC895856 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2014 | Before | 2014-05-01 13:18 | 2014-05-01 13:18 | 0 | 0 | 1811 | 150.917 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | LOAD BREAK ELBOW UG |  |  |  | SOURCE: T&R due to b/o elbow | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2014-05-01 13:18 | 2014-05-01 13:18 | 2014-05-01 16:15 | -123.9098 | 46.1511
5A15 | 1488626 | CPCC | CPCC910087 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_216607_626300479 | 2014 | Before | 2014-07-30 08:12 | 2014-07-30 10:26 | 1 | 133.633 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | SOURCE: Serviceman reports he replaced the neutral connectors at the transformer due to deterioration. No one at home to advise. OC will call customer to advise. | DISTRIBUTION | CUSTOMER | AUTO | 2014-07-30 11:15 | COMPLETED |  | 2014-07-30 08:12 | 2014-07-30 10:29 | 2014-07-30 13:59 | -123.9273 | 46.1656
5A15 | 1484441 | CPCC | CPCC907600 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2014 | Before | 2014-07-17 15:30 | 2014-07-17 15:31 | 0 | 0 | 1818 | 151.5 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: T&R, no cause found | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2014-07-17 15:30 | 2014-07-17 15:31 | 2014-07-17 17:48 | -123.9098 | 46.1511
5A15 | 1487358 | CPCC | CPCC909302 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_086905_825180447 | 2014 | Before | 2014-07-26 23:55 | 2014-07-27 00:41 | 3 | 138.05 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | TRANSFORMER OH |  |  |  | SOURCE: serviceman had been called out to this location earlier to a leaking transformer but was no immediate hazard see outage 909243, crew now there to change the leaking xfmr.crew complete, customers are back in service | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2014-07-26 23:55 | 2014-07-27 00:41 | 2014-07-27 02:44 | -123.9473 | 46.1989
5A15 | 1501835 | CPCC | CPCC918408 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_053404_825180305 | 2014 | Before | 2014-09-12 05:31 | 2014-09-12 09:29 | 1 | 238.283 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: bad neutral conn | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2014-09-12 10:15 | COMPLETED |  | 2014-09-12 05:31 | 2014-09-12 09:29 | 2014-09-12 09:33 | -123.955 | 46.2062
5A15 | 1515620 | CPCC | CPCC929835 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_093501_543460232 | 2014 | Before | 2014-11-06 06:14 | 2014-11-06 11:39 | 1 | 324.633 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Tree through secondary, repairs made , power restored | DISTRIBUTION | CUSTOMER | AUTO | 2014-11-06 09:15 | COMPLETED |  | 2014-11-06 06:14 | 2014-11-06 11:39 | 2014-11-06 13:53 | -123.934 | 46.1922
5A15 | 1500962 | CPCC | CPCC917850 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_223700_626300658 | 2014 | Before | 2014-09-09 12:34 | 2014-09-09 13:01 | 2 | 52.467 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Deteriorated x-fmr fuse. Serviceman replaced fuse. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-09-09 15:45 | COMPLETED |  | 2014-09-09 12:34 | 2014-09-09 13:01 | 2014-09-09 15:38 | -123.9128 | 46.166
5A15 | 1510719 | CPCC | CPCC923942 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2014 | Before | 2014-10-20 19:32 | 2014-10-20 19:32 | 0 | 0 | 1826 | 152.167 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: T&R due to b/o UG. Part of outage-923947 | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2014-10-20 19:32 | 2014-10-20 19:32 | 2014-10-21 02:05 | -123.9098 | 46.1511
5A15 | 1510724 | CPCC | CPCC923956 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_215904_626300431 | 2014 | Before | 2014-10-20 19:38 | 2014-10-20 22:30 | 49 | 8394.517 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: B/O Ug Crew looped up from normal open and restored power. | DISTRIBUTION | DEVICE | AUTO | 2014-10-21 | COMPLETED |  | 2014-10-20 20:54 | 2014-10-21 11:52 | 2014-10-21 02:08 | -123.9298 | 46.1694
5A15 | 1510725 | CPCC | CPCC923947 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_215904_626300431 | 2014 | Before | 2014-10-20 19:40 | 2014-10-20 22:34 | 43 | 7511.35 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: B/O Ug Crew looped up from normal open and restored power. | DISTRIBUTION | DEVICE | AUTO | 2014-10-20 22:45 | COMPLETED |  | 2014-10-20 19:43 | 2014-10-21 11:50 | 2014-10-21 02:08 | -123.9298 | 46.1694
5A15 | 1508909 | CPCC | CPCC922690 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_218615_626300524 | 2014 | Before | 2014-10-11 16:22 | 2014-10-11 18:04 | 1 | 102.3 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: B/O secondary connectors. | DISTRIBUTION | CUSTOMER | AUTO | 2014-10-11 19:30 | COMPLETED |  | 2014-10-11 16:22 | 2014-10-11 18:04 | 2014-10-12 00:15 | -123.9233 | 46.1649
5A15 | 1496714 | CPCC | CPCC915802 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_083906_825180477 | 2014 | Before | 2014-08-24 12:02 | 2014-08-24 12:42 | 1 | 39.467 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman found open fuse broke in half. Refused and restored power. | DISTRIBUTION | CUSTOMER | AUTO | 2014-08-24 15:15 | COMPLETED |  | 2014-08-24 12:02 | 2014-08-24 12:42 | 2014-08-24 13:43 | -123.9545 | 46.1975
5A15 | 1511253 | CPCC | CPCC924306 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_165503_543460369 | 2014 | Before | 2014-10-22 21:08 | 2014-10-23 00:08 | 28 | 5041.867 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Serviceman arrived and needs 3 man crew for B/O UG. Crew made repairs and restored power. | DISTRIBUTION | DEVICE | AUTO | 2014-10-23 00:45 | COMPLETED |  | 2014-10-22 21:40 | 2014-10-23 00:08 | 2014-10-23 04:34 | -123.9296 | 46.1778
5A15 | 1523061 | CPCC | CPCC936104 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2014 | Before | 2014-12-08 21:10 | 2014-12-08 21:10 | 0 | 0 | 1726 | 143.833 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: T&R Unknown | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2014-12-08 21:10 | 2014-12-09 01:07 | 2014-12-09 11:35 | -123.9098 | 46.1511
5A15 | 1520202 | CPCC | CPCC933873 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_169100_1580286070 | 2014 | Before | 2014-11-24 10:44 | 2014-11-24 11:27 | 2 | 86.833 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman found fuse open on pole # 169100; rotted fuse | DISTRIBUTION | DEVICE | AUTO | 2014-11-24 13:45 | COMPLETED |  | 2014-11-24 10:44 | 2014-11-24 11:27 | 2014-11-24 12:15 | -123.9222 | 46.1722
5A15 | 1520290 | CPCC | CPCC933933 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_169100_1580286070 | 2014 | Before | 2014-11-24 16:04 | 2014-11-24 16:43 | 2 | 78.967 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: serviceman reports that the city called him directly and had two cutouts blown, serviceman refused the cutouts and customers are back in service | DISTRIBUTION | DEVICE | AUTO | 2014-11-24 19:15 | COMPLETED |  | 2014-11-24 16:04 | 2014-11-24 16:43 | 2014-11-24 16:59 | -123.9222 | 46.1722
5A15 | 1520835 | CPCC | CPCC934352 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_222500_626300669 | 2014 | Before | 2014-11-26 21:20 | 2014-11-26 22:29 | 1 | 69.567 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman arrived and found tree caused line down made repairs and restored power. | DISTRIBUTION | CUSTOMER | AUTO | 2014-11-27 00:30 | COMPLETED |  | 2014-11-26 21:20 | 2014-11-26 22:29 | 2014-11-27 03:03 | -123.9144 | 46.1634
5A15 | 1540333 | CPCC | CPCC952309 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_090603_543460288 | 2015 | Before | 2015-02-22 09:19 | 2015-02-22 10:16 | 3 | 172 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: replaced B/O Cut out | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-02-22 12:30 | COMPLETED |  | 2015-02-22 09:20 | 2015-02-22 10:17 | 2015-02-22 10:19 | -123.9398 | 46.194
5A15 | 1523057 | CPCC | CPCC936106 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_082906_825180280 | 2014 | Before | 2014-12-08 21:23 | 2014-12-09 00:35 | 82 | 15787.733 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  |  | DISTRIBUTION | DEVICE | AUTO | 2014-12-09 02:00 | COMPLETED |  | 2014-12-08 21:23 | 2014-12-09 07:20 | 2014-12-09 11:35 | -123.9551 | 46.1989
5A15 | 1537741 | CPCC | CPCC951073 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_214603_626300496 | 2015 | Before | 2015-02-10 03:56 | 2015-02-10 06:20 | 9 | 1302 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: B/O cut-out. | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2015-02-10 07:30 | COMPLETED |  | 2015-02-10 03:56 | 2015-02-10 06:29 | 2015-02-10 06:33 | -123.9313 | 46.1652
5A15 | 1543079 | CPCC | CPCC953440 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_094500_543460293 | 2015 | Before | 2015-03-04 07:40 | 2015-03-04 09:08 | 1 | 87.533 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman reports transformer fuse blew on pole # 094500; re-fused and it held. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-03-04 10:45 | COMPLETED |  | 2015-03-04 07:41 | 2015-03-04 09:53 | 2015-03-04 09:53 | -123.9325 | 46.193
5A15 | 1545027 | CPCC | CPCC954595 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_057005_825180386 | 2015 | Before | 2015-03-15 13:37 | 2015-03-15 19:22 | 1 | 344.75 | 0 | 0 | 1 | Y | N | N | N | Y | 3/15/2015 Coast Plus | WEATHER | WIND |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman repaired service that was on garage | DISTRIBUTION | CUSTOMER | AUTO | 2015-03-15 16:45 | COMPLETED |  | 2015-03-15 13:37 | 2015-03-15 19:23 | 2015-03-15 19:28 | -123.9471 | 46.1992
5A15 | 1561964 | CPCC | CPCC965167 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_216406_626300595 | 2015 | Before | 2015-05-21 11:59 | 2015-05-21 13:00 | 1 | 61.667 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: Crew on site of wire down; found single phase still attached to truck;Serviceman reports the chicken catcher(wedge clamp) rotted, fell, so service line was low; the garbage truck pulled it down; no other damage done. Crew put line back up. | DISTRIBUTION | CUSTOMER | AUTO | 2015-05-21 15:00 | COMPLETED |  | 2015-05-21 11:59 | 2015-05-21 15:59 | 2015-05-21 16:02 | -123.9259 | 46.1619
5A15 | 1544173 | CPCC | CPCC954144 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_221601_626300410 | 2015 | Before | 2015-03-10 20:47 | 2015-03-10 22:52 | 6 | 752.2 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | SOURCE: replaced bad connector | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2015-03-10 20:47 | 2015-03-10 23:02 | 2015-03-10 23:03 | -123.9173 | 46.1646
5A15 | 1579488 | CPCC | CPCC976641 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_222610_1580311775 | 2015 | Before | 2015-07-13 15:33 | 2015-07-13 16:21 | 18 | 868.8 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman found fuse blown on pole 222610; says there is a construction crew down the road in same area, but they say they didn't cause outage. Didn't see anything else. Closed on test and it held. | DISTRIBUTION | DEVICE | AUTO | 2015-07-13 18:45 | COMPLETED |  | 2015-07-13 15:35 | 2015-07-13 16:22 | 2015-07-13 16:23 | -123.9143 | 46.1643
5A15 | 1567521 | CPCC | CPCC968639 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2015 | Before | 2015-06-09 20:56 | 2015-06-09 20:56 | 0 | 0 | 1835 | 91.75 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: T&R Unknown | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2015-06-09 20:56 | 2015-06-23 16:35 | 2015-06-09 23:33 | -123.9098 | 46.1511
5A15 | 1567752 | CPCC | CPCC968817 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_089904_1580312224 | 2015 | Before | 2015-06-10 11:25 | 2015-06-10 12:15 | 1 | 49.583 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman found fuse blown on pole # 089900; will patrol, did find transformer fuse blown as well. Tested transformer, good. Re-fused both transformer and line fuse and they held. Unknown cause | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-06-10 14:30 | COMPLETED |  | 2015-06-10 11:25 | 2015-06-10 13:03 | 2015-06-10 13:08 | -123.9425 | 46.1976
5A15 | 1572034 | CPCC | CPCC970968 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_054104_825180363 | 2015 | Before | 2015-06-24 17:35 | 2015-06-24 20:40 | 1 | 184.633 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | SOURCE: Serviceman repaired connectors, Customer Restored | DISTRIBUTION | CUSTOMER | AUTO | 2015-06-24 20:45 | COMPLETED |  | 2015-06-24 17:36 | 2015-06-24 21:05 | 2015-06-24 21:08 | -123.9527 | 46.2006
5A15 | 1593806 | CPCC | CPCC986294 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2015 | Before | 2015-08-29 10:06 | 2015-08-29 10:06 | 0 | 0 | 1779 | 59.3 | 1 | Y | N | N | N | Y | 2015-08-29 OR CoastPlus | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: T&R due to wind and trees | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2015-08-29 10:06 | 2015-08-29 19:57 | 2015-08-29 19:59 | -123.9098 | 46.1511
5A15 | 1589050 | CPCC | CPCC983332 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_216700_626300473 | 2015 | Before | 2015-08-12 18:24 | 2015-08-12 19:36 | 5 | 358.417 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | SPLICE B/O OH |  |  |  | SOURCE: Serviceman repaired overhead hot tap | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-08-12 21:30 | COMPLETED |  | 2015-08-12 18:24 | 2015-08-13 06:57 | 2015-08-13 06:59 | -123.927 | 46.167
5A15 | 1594022 | CPCC | CPCC986317 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_053107_825180331 | 2015 | Before | 2015-08-29 10:13 | 2015-08-29 14:05 | 1 | 232.583 | 0 | 0 | 1 | Y | N | N | N | Y | 2015-08-29 OR CoastPlus | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Complete per Astoria Manager | DISTRIBUTION | CUSTOMER | AUTO |  | COMPLETED |  | 2015-08-29 10:15 | 2015-08-30 06:03 | 2015-08-30 06:07 | -123.9542 | 46.2016
5A15 | 1594020 | CPCC | CPCC986254 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_090600_543460289 | 2015 | Before | 2015-08-29 09:34 | 2015-08-29 14:04 | 1 | 270.133 | 0 | 0 | 1 | Y | N | N | N | Y | 2015-08-29 OR CoastPlus | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Complete per Astoria Manager | DISTRIBUTION | CUSTOMER | AUTO |  | COMPLETED |  | 2015-08-29 09:34 | 2015-08-30 06:02 | 2015-08-30 06:07 | -123.9391 | 46.1947
5A15 | 1594023 | CPCC | CPCC986604 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_050042_825180506 | 2015 | Before | 2015-08-29 12:34 | 2015-08-29 14:13 | 1 | 98.717 | 0 | 0 | 1 | Y | N | N | N | Y | 2015-08-29 OR CoastPlus | TREES | TREE - TRIMMABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Complete per Astoria Manager | DISTRIBUTION | CUSTOMER | AUTO |  | COMPLETED |  | 2015-08-29 12:34 | 2015-08-30 06:03 | 2015-08-30 06:07 | -123.9614 | 46.199
5A15 | 1593814 | CPCC | CPCC986583 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_090802_1580312156 | 2015 | Before | 2015-08-29 12:17 | 2015-08-29 13:21 | 8 | 514.667 | 0 | 0 | 1 | Y | N | N | N | Y | 2015-08-29 OR CoastPlus | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: crew has made repairs, customers are back in service | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2015-08-29 12:17 | 2015-08-29 19:59 | 2015-08-29 20:03 | -123.9407 | 46.1963
5A15 | 1593818 | CPCC | CPCC986195 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_050041_825180352 | 2015 | Before | 2015-08-29 08:42 | 2015-08-29 14:02 | 1 | 320.35 | 0 | 0 | 1 | Y | N | N | N | Y | 2015-08-29 OR CoastPlus | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Complete per Astoria Manager | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-08-29 11:45 | COMPLETED |  | 2015-08-29 08:43 | 2015-08-29 20:00 | 2015-08-29 20:04 | -123.9614 | 46.1997
5A15 | 1593815 | CPCC | CPCC986191 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_091721_543460209 | 2015 | Before | 2015-08-29 08:37 | 2015-08-29 14:01 | 6 | 1944 | 0 | 0 | 1 | Y | N | N | N | Y | 2015-08-29 OR CoastPlus | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Complete per Astoria Manager | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-08-29 11:45 | COMPLETED |  | 2015-08-29 08:39 | 2015-08-29 20:00 | 2015-08-29 20:03 | -123.9401 | 46.196
5A15 | 1593820 | CPCC | CPCC986319 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_085910_825180453 | 2015 | Before | 2015-08-29 10:15 | 2015-08-29 14:03 | 1 | 227.217 | 0 | 0 | 1 | Y | N | N | N | Y | 2015-08-29 OR CoastPlus | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Complete per Astoria Manager | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2015-08-29 10:16 | 2015-08-29 20:00 | 2015-08-29 20:04 | -123.9508 | 46.1989
5A15 | 1594021 | CPCC | CPCC986258 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_216700_626300473 | 2015 | Before | 2015-08-29 09:34 | 2015-08-29 14:04 | 1 | 270.433 | 0 | 0 | 1 | Y | N | N | N | Y | 2015-08-29 OR CoastPlus | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Complete per Astoria Manager | DISTRIBUTION | CUSTOMER | AUTO |  | COMPLETED |  | 2015-08-29 09:35 | 2015-08-30 06:03 | 2015-08-30 06:07 | -123.927 | 46.167
5A15 | 1593817 | CPCC | CPCC986421 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_053104_1090307168 | 2015 | Before | 2015-08-29 10:40 | 2015-08-29 13:40 | 16 | 2876 | 0 | 0 | 1 | Y | N | N | N | Y | 2015-08-29 OR CoastPlus | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman found line fuse open on 053104, re-fused and it held. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2015-08-29 10:42 | 2015-08-29 20:00 | 2015-08-29 20:03 | -123.955 | 46.2012
5A15 | 1593821 | CPCC | CPCC986706 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_222600_626300378 | 2015 | Before | 2015-08-29 13:19 | 2015-08-29 14:06 | 1 | 46.9 | 0 | 0 | 1 | Y | N | N | N | Y | 2015-08-29 OR CoastPlus | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Complete per Astoria Manager | DISTRIBUTION | CUSTOMER | AUTO |  | COMPLETED |  | 2015-08-29 13:20 | 2015-08-29 20:00 | 2015-08-29 20:04 | -123.9151 | 46.1644
5A15 | 1593819 | CPCC | CPCC986339 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_080901_825180504 | 2015 | Before | 2015-08-29 10:26 | 2015-08-29 14:03 | 3 | 652.1 | 0 | 0 | 1 | Y | N | N | N | Y | 2015-08-29 OR CoastPlus | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Complete per Astoria Manager | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2015-08-29 10:27 | 2015-08-29 20:00 | 2015-08-29 20:04 | -123.9612 | 46.198
5A15 | 1593816 | CPCC | CPCC986180 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_051001_825180349 | 2015 | Before | 2015-08-29 08:27 | 2015-08-29 14:01 | 50 | 16705.833 | 0 | 0 | 1 | Y | N | N | N | Y | 2015-08-29 OR CoastPlus | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Complete per Astoria Manager | DISTRIBUTION | DEVICE | AUTO | 2015-08-29 11:30 | COMPLETED |  | 2015-08-29 08:27 | 2015-08-29 20:00 | 2015-08-29 20:03 | -123.9588 | 46.1997
5A15 | 1592567 | CPCC | CPCC985433 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_217502_626300517 | 2015 | Before | 2015-08-25 19:31 | 2015-08-25 21:15 | 1 | 103.667 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | SOURCE: serviceman reports that there is a bad connector at the weather head, will make repairs. Serviceman changed out the connector, customers are back in full service | DISTRIBUTION | CUSTOMER | AUTO | 2015-08-25 22:45 | COMPLETED |  | 2015-08-25 19:32 | 2015-08-25 22:03 | 2015-08-25 22:04 | -123.924 | 46.1637
5A15 | 1613763 | CPCC | CPCC1000770 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_184601_825180536 | 2015 | Before | 2015-11-18 08:51 | 2015-11-18 21:22 | 1 | 750.2 | 0 | 0 | 1 | Y | N | N | N | Y | OR Coast Plus 11-17-2015 | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: associate to outage 1000809 | DISTRIBUTION | CUSTOMER | AUTO | 2015-11-18 12:00 | COMPLETED |  | 2015-11-18 08:52 | 2015-11-18 23:41 | 2015-11-18 23:43 | -123.9752 | 46.1793
5A15 | 1628251 | CPCC | CPCC1016827 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_216705_626300477 | 2015 | Before | 2015-12-30 19:57 | 2015-12-30 22:00 | 6 | 740 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Serviceman replaced a bad cut out and made repairs to transformer connections Customers fed from Transformer 216706 | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-12-30 23:00 | COMPLETED |  | 2015-12-30 19:57 | 2015-12-31 07:11 | 2015-12-31 07:13 | -123.9277 | 46.1662
5A15 | 1614824 | CPCC | CPCC1001424 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_089904_1580312224 | 2015 | Before | 2015-11-23 07:52 | 2015-11-23 08:29 | 1 | 36.083 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: pole 089810 - has a broken jumper, crew to repair. see outage 1001429 | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-11-23 11:00 | COMPLETED |  | 2015-11-23 07:53 | 2015-11-23 12:15 | 2015-11-23 12:20 | -123.9425 | 46.1976
5A15 | 1626051 | CPCC | CPCC1014414 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_188841_825180533 | 2015 | Before | 2015-12-21 13:45 | 2015-12-21 17:22 | 6 | 1304 | 0 | 0 | 1 | Y | N | N | N | Y | OR Coast Plus 12-21-2015 | PLANNED | EMERGENCY DAMAGE REPAIR | TREES | TREE - NON-PREVENTABLE | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Opened fuse due to 1 span of primary down at the fuses. | DISTRIBUTION | DEVICE | AUTO | 2015-12-21 17:15 | COMPLETED |  | 2015-12-21 13:45 | 2015-12-22 12:38 | 2015-12-22 12:43 | -123.964 | 46.1811
5A15 | 1626174 | CPCC | CPCC1014381 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2015 | Before | 2015-12-21 13:25 | 2015-12-21 13:25 | 0 | 0 | 1821 | 60.7 | 1 | Y | N | N | N | Y | OR Coast Plus 12-21-2015 | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: T & R, primary wire down due to tree | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2015-12-21 13:25 | 2015-12-22 15:16 | 2015-12-22 15:18 | -123.9098 | 46.1511
5A15 | 1630908 | CPCC | CPCC1018676 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_053103_825180338 | 2016 | Before | 2016-01-12 18:26 | 2016-01-12 19:32 | 1 | 66.783 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman repaired a broken conductor at F/P 053107. No Outage PROSPER: Hazard | DISTRIBUTION | CUSTOMER | AUTO | 2016-01-12 21:30 | COMPLETED |  | 2016-01-12 18:26 | 2016-01-25 16:25 | 2016-01-13 07:05 | -123.9538 | 46.2006
5A15 | 1614825 | CPCC | CPCC1001429 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_089810_543460273 | 2015 | Before | 2015-11-23 07:52 | 2015-11-23 09:16 | 2 | 166.7 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: crew to repair a broken jumper | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2015-11-23 07:52 | 2015-11-23 12:16 | 2015-11-23 12:20 | -123.9413 | 46.1973
5A15 | 1634617 | CPCC | CPCC1021945 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_222610_1580311775 | 2016 | Before | 2016-01-29 05:06 | 2016-01-29 08:00 | 26 | 4520.1 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman reports road side phase conductor down between FP 222603 and FP 222605, crew opened at 0737 all phases. Crew repaired conductors PROSPER: Hazard | DISTRIBUTION | DEVICE | AUTO | 2016-01-29 09:30 | COMPLETED |  | 2016-01-29 05:07 | 2016-02-02 16:37 | 2016-01-29 14:24 | -123.9143 | 46.1643
5A15 | 1613256 | CPCC | CPCC1000493 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | Line Cut-98922 | 2015 | Before | 2015-11-17 23:42 | 2015-11-18 00:40 | 1821 | 105860.8 | 0 | 0 | 1 | Y | N | N | N | Y | OR Coast Plus 11-17-2015 | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Loss 115 kV transmission line, sectionalizing to restore power. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2015-11-17 23:57 | 2015-11-18 05:43 | 2015-11-18 05:43 | -123.9097 | 46.151
5A15 | 1618083 | CPCC | CPCC1004295 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_090802_1580312156 | 2015 | Before | 2015-12-06 18:31 | 2015-12-06 23:34 | 14 | 4242.467 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | POLE OH |  |  |  | SOURCE: Tree fell on line & broke pole & wire down -- did callout | DISTRIBUTION | DEVICE | AUTO | 2015-12-06 21:45 | COMPLETED |  | 2015-12-06 18:31 | 2015-12-07 00:03 | 2015-12-07 00:04 | -123.9407 | 46.1963
5A15 | 1628252 | CPCC | CPCC1016828 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_216706_626300475 | 2015 | Before | 2015-12-30 20:20 | 2015-12-30 21:41 | 5 | 407.833 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Serviceman replaced a bad cut out and made repairs to transformer connections | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-12-30 23:30 | COMPLETED |  | 2015-12-30 20:22 | 2015-12-31 07:12 | 2015-12-31 07:13 | -123.9277 | 46.1669
5A15 | 1613764 | CPCC | CPCC1000809 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_187800_1580419676 | 2015 | Before | 2015-11-18 10:27 | 2015-11-18 21:22 | 3 | 1963.6 | 0 | 0 | 1 | Y | N | N | N | Y | OR Coast Plus 11-17-2015 | PLANNED | EMERGENCY DAMAGE REPAIR | TREES | TREE - NON-PREVENTABLE | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Crew needed to repair wire down pole 186701 and 187800 (associate to outage 1000770). Repairs complete and all customers restored | DISTRIBUTION | DEVICE | AUTO | 2015-11-18 13:30 | COMPLETED |  | 2015-11-18 10:27 | 2015-11-18 23:41 | 2015-11-18 23:43 | -123.965 | 46.1813
5A15 | 1632965 | CPCC | CPCC1020705 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2016 | Before | 2016-01-21 09:24 | 2016-01-21 09:27 | 0 | 0 | 1823 | 4648.65 | 1 | Y | N | N | Y | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Problem at BPA Tillamook Sub | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2016-01-21 09:30 | 2016-03-03 15:14 | 2016-01-21 15:59 | -123.9097 | 46.1509
5A15 | 1612804 | CPCC | CPCC999020 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_165504_1580286052 | 2015 | Before | 2015-11-16 18:14 | 2015-11-16 19:16 | 33 | 2047.1 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - TRIMMABLE |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman removed a tree branch from the line and replaced a blown fuse @ F/P165504 | DISTRIBUTION | DEVICE | AUTO | 2015-11-16 21:45 | COMPLETED |  | 2015-11-16 18:38 | 2015-11-17 06:28 | 2015-11-17 06:30 | -123.9287 | 46.1777
5A15 | 1616858 | CPCC | CPCC1001431 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_089904_1580312224 | 2015 | Before | 2015-11-23 08:42 | 2015-11-23 09:16 | 0 | 0 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: associate to outage 01001429; crew to repair broken jumper | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-11-23 11:45 | COMPLETED |  | 2015-11-23 08:35 | 2015-12-02 08:39 | 2015-12-02 08:43 | -123.9425 | 46.1976
5A15 | 1641273 | CPCC | CPCC1026503 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_079904_825180484 | 2016 | Before | 2016-02-24 06:15 | 2016-02-24 09:20 | 4 | 664.933 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Crew found b/o ug; reports the only xfmr off is 079880. | DISTRIBUTION | DEVICE | MANUAL | 2016-02-24 14:00 | COMPLETED |  | 2016-02-24 06:15 | 2016-02-24 16:14 | 2016-02-24 16:17 | -123.9626 | 46.1979
5A15 | 1646481 | CPCC | CPCC1032754 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_216406_626300595 | 2016 | Before | 2016-03-15 18:10 | 2016-03-15 18:37 | 4 | 104.533 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | SOURCE: Serviceman repaired connections on transformers at F/P 216406 | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2016-03-15 18:10 | 2016-03-16 07:34 | 2016-03-16 07:37 | -123.9259 | 46.1619
5A15 | 1652282 | CPCC | CPCC1036470 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_088802_825180426 | 2016 | Before | 2016-04-09 20:10 | 2016-04-09 21:28 | 256 | 19955.2 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman found fuse open at 088802, patrolled for cause, no cause found, re-fused and holding. Outages were reported on all 3 phases, Serviceman only found 1 fuse open, he verified all the other phases were energized and that customers had power. | DISTRIBUTION | DEVICE | AUTO | 2016-04-10 00:15 | COMPLETED |  | 2016-04-09 21:10 | 2016-04-11 09:25 | 2016-04-09 22:41 | -123.9439 | 46.197
5A15 | 1645478 | CPCC | CPCC1031225 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_165503_543460369 | 2016 | Before | 2016-03-12 10:52 | 2016-03-12 14:32 | 39 | 8585.85 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER PADMOUNT/SUBMERSIBLE UG |  |  |  | SOURCE: Crew made temp repairs to transformer at FP 164580, restored all customers. District will schedule to replace transformer | DISTRIBUTION | DEVICE | AUTO | 2016-03-12 14:00 | COMPLETED |  | 2016-03-12 10:52 | 2016-03-12 17:01 | 2016-03-12 17:02 | -123.9296 | 46.1778
5A15 | 1644970 | CPCC | CPCC1030577 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2016 | Before | 2016-03-10 03:38 | 2016-03-10 16:35 | 397 | 308528.55 | 0 | 0 | 1 | Y | N | N | N | Y | OR Coast Plus 03-09-2016 | WEATHER | WIND |  |  | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | SOURCE: wire down in chute/4 broken xarms/access issues | DISTRIBUTION | DEVICE | MANUAL | 2016-03-10 16:00 | COMPLETED |  | 2016-03-10 03:38 | 2016-03-10 16:45 | 2016-03-10 16:50 | -123.9098 | 46.1511
5A15 | 1645187 | CPCC | CPCC1029833 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_217602_626300369 | 2016 | Before | 2016-03-09 17:19 | 2016-03-10 16:35 | 335 | 467632.195 | 0 | 0 | 1 | Y | N | N | N | Y | OR Coast Plus 03-09-2016 | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: wire down in chute/4 broken xarms/access issues PROSPER: changed to first OUT time 03/09/2016 17:19:05, was 03/09/2016 17:09:50 | DISTRIBUTION | DEVICE | MANUAL | 2016-03-09 16:00 | COMPLETED |  | 2016-03-09 17:29 | 2016-03-17 10:47 | 2016-03-11 11:37 | -123.9241 | 46.1647
5A15 | 1645235 | CPCC | CPCC1029907 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2016 | Before | 2016-03-09 18:01 | 2016-03-10 16:35 | 1 | 1354.15 | 0 | 0 | 1 | Y | N | N | N | Y | OR Coast Plus 03-09-2016 | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: see outage 1030059. | DISTRIBUTION | DEVICE | AUTO | 2016-03-09 21:00 | COMPLETED |  | 2016-03-09 18:01 | 2016-03-11 13:06 | 2016-03-11 13:08 | -123.9098 | 46.1511
5A15 | 1652346 | CPCC | CPCC1036076 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_079904_825180484 | 2016 | Before | 2016-04-09 00:01 | 2016-04-09 08:15 | 4 | 1977.4 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Crew isolated bad underground section | DISTRIBUTION | DEVICE | MANUAL | 2016-04-09 09:00 | COMPLETED |  | 2016-04-09 00:01 | 2016-04-10 04:54 | 2016-04-10 04:57 | -123.9626 | 46.1979
5A15 | 1646880 | CPCC | CPCC1032988 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2016 | Before | 2016-03-18 00:28 | 2016-03-18 00:32 | 0 | 0 | 1832 | 7999.733 | 1 | Y | N | N | Y | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Loss of 115 kV Astoria - BPA Tillamook line. Sectionalized outage and restored customers. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2016-03-18 00:30 | 2016-03-29 14:11 | 2016-03-18 01:13 | -123.9097 | 46.151
5A15 | 1645736 | CPCC | CPCC1031558 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2016 | Before | 2016-03-13 10:51 | 2016-03-13 11:31 | 1830 | 74023.5 | 0 | 0 | 1 | Y | N | N | Y | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Astoria CB 2A6 & BPA B1093 locked open due to high wind storm. response dispatched for switching and troubleshooting for fault location. loss of Warrenton, Seaside,Cannon Beach | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2016-03-13 10:56 | 2016-03-29 11:15 | 2016-03-13 21:22 | -123.9097 | 46.151
5A15 | 1641272 | CPCC | CPCC1026540 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_082801_1580003246 | 2016 | Before | 2016-02-24 14:07 | 2016-02-24 15:40 | 13 | 1207.267 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: due bad connectivity in cadops, there are 6 additional custs on FP080785; | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2016-02-24 14:07 | 2016-02-24 16:13 | 2016-02-24 16:17 | -123.9551 | 46.1962
5A15 | 1644971 | CPCC | CPCC1030059 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | Line Cut-100436 | 2016 | Before | 2016-03-09 17:43 | 2016-03-10 16:35 | 1489 | 1738252.133 | 0 | 0 | 2 | Y | N | N | N | Y | OR Coast Plus 03-09-2016 | WEATHER | WIND |  |  | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | SOURCE: Multiple wire down and equipment damage in multiple areas, crews are working to restore; wire down in chute/4 broken xarms/access issues | DISTRIBUTION | DEVICE | MANUAL | 2016-03-10 16:00 | COMPLETED |  | 2016-03-09 18:37 | 2016-03-10 16:45 | 2016-03-10 16:50 | -123.9097 | 46.1509
5A15 | 1651496 | CPCC | CPCC1035743 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_222701_626300659 | 2016 | Before | 2016-04-06 09:27 | 2016-04-06 11:57 | 5 | 750.75 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: outage started at 9:27 completed @ 1000 Lineman reports bad leads at transformer | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2016-04-06 09:37 | 2016-04-06 14:44 | 2016-04-06 13:23 | -123.9133 | 46.166
5A15 | 1638349 | CPCC | CPCC1024825 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_090802_1580312156 | 2016 | Before | 2016-02-16 13:11 | 2016-02-16 13:30 | 14 | 273.933 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | DETERIORATION OR ROTTING | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Took emergency outage at pole 090802 so they could repair rotted wire | DISTRIBUTION | DEVICE | MANUAL | 2016-02-16 14:16 | COMPLETED |  | 2016-02-16 13:11 | 2016-02-16 13:51 | 2016-02-16 13:52 | -123.9407 | 46.1963
5A15 | 1645186 | CPCC | CPCC1030885 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_165380_543460397 | 2016 | Before | 2016-03-10 19:37 | 2016-03-11 09:33 | 1 | 835.367 | 0 | 0 | 1 | Y | N | N | N | Y | OR Coast Plus 03-09-2016 | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | SOURCE: serviceman reports that there is possible bad underground primary, will investigate for cause, UG has been switched, so local crew needed to make repairs and investigate, repairs completed , all customers restored | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2016-03-11 12:00 | COMPLETED |  | 2016-03-10 19:37 | 2016-03-11 11:30 | 2016-03-11 11:32 | -123.9283 | 46.1745
5A15 | 1669709 | CPCC | CPCC1047737 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2016 | Before | 2016-06-02 02:45 | 2016-06-02 02:45 | 0 | 0 | 1844 | 860.533 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: car pole, opened feeder to open solid blades on pole 244501 for safe working clearance to replace pole | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2016-06-02 02:45 | 2016-06-02 04:46 | 2016-06-02 04:49 | -123.9098 | 46.1511
5A15 | 1669706 | CPCC | CPCC1047738 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | SB_224501_1580532736 | 2016 | Before | 2016-06-02 02:46 | 2016-06-02 04:43 | 1827 | 213698.1 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: opened solid blades on pole 244501 to facilitate safe work space | DISTRIBUTION | DEVICE | AUTO | 2016-06-02 05:45 | COMPLETED |  | 2016-06-02 02:46 | 2016-06-02 04:43 | 2016-06-02 04:48 | -123.9105 | 46.1633
5A15 | 1704952 | CPCC | CPCC1071113 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_165608_543460213 | 2016 | Before | 2016-09-25 08:36 | 2016-09-25 09:31 | 9 | 494.85 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: Jumper wire came loose from cutout, serviceman repaired and restored all customers | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2016-09-25 11:45 | COMPLETED |  | 2016-09-25 08:36 | 2016-09-25 13:14 | 2016-09-25 13:18 | -123.9296 | 46.1793
5A15 | 1701049 | CPCC | CPCC1068906 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2016 | Before | 2016-09-13 15:26 | 2016-09-13 15:33 | 1850 | 12395 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE | EQUIPMENT FAILURE | POLE FIRE | POLE OH |  |  |  | SOURCE: Loss of 115kV transmission line, cause under investigation Pole fire at structure 3/18 with 12kV underbuild CB 5A82 Power restored at 15:32:42 on 09/13/2016 PROSPER: Changed start time to match trans outage and added contrib cause of pole fire. Changed restore time to match comments. | DISTRIBUTION | DEVICE | AUTO | 2016-09-13 18:45 | COMPLETED |  | 2016-09-13 15:30 | 2016-09-19 16:20 | 2016-09-13 19:33 | -123.9097 | 46.151
5A15 | 1724153 | CPCC | CPCC1087180 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_091506_543460307 | 2016 | Before | 2016-12-09 18:04 | 2016-12-09 20:20 | 3 | 409.55 | 0 | 0 | 1 | Y | N | N | N | Y | OR Consolidated 12-09-2016 | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Crew to replaced broken Cut out | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2016-12-09 21:15 | COMPLETED |  | 2016-12-09 18:04 | 2016-12-09 20:42 | 2016-12-09 20:44 | -123.937 | 46.1927
5A15 | 1710684 | CPCC | CPCC1075272 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_222500_626300669 | 2016 | Before | 2016-10-13 20:54 | 2016-10-14 19:47 | 1 | 1372.983 | 0 | 0 | 1 | Y | N | N | N | Y | OR CoastPlus 10-13-2016 | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: tree pulled sservice from transformer, will send serviceman to make repairs, crew complete, customer back in service | DISTRIBUTION | CUSTOMER | MANUAL | 2016-10-14 08:00 | COMPLETED |  | 2016-10-13 20:54 | 2016-10-14 19:58 | 2016-10-14 19:58 | -123.9144 | 46.1634
5A15 | 1710091 | CPCC | CPCC1075303 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_082681_825180464 | 2016 | Before | 2016-10-13 21:12 | 2016-10-14 05:38 | 1 | 506.583 | 0 | 0 | 1 | Y | N | N | N | Y | OR CoastPlus 10-13-2016 | INTERFERENCE | VEHICLE ACCIDENT |  |  | TRANSFORMER PADMOUNT/SUBMERSIBLE UG |  |  |  | SOURCE: Transformer was hit , crew put back in place | DISTRIBUTION | CUSTOMER | MANUAL | 2016-10-14 08:00 | COMPLETED |  | 2016-10-13 21:12 | 2016-10-14 06:43 | 2016-10-14 06:43 | -123.9542 | 46.1938
5A15 | 1710033 | CPCC | CPCC1074954 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2016 | Before | 2016-10-13 19:09 | 2016-10-13 19:27 | 1849 | 33282 | 0 | 0 | 1 | Y | N | N | N | Y | OR CoastPlus 10-13-2016 | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: | DISTRIBUTION | DEVICE | AUTO | 2016-10-13 22:15 | COMPLETED |  | 2016-10-13 19:15 | 2016-10-17 14:44 | 2016-10-14 03:28 | -123.9097 | 46.151
5A15 | 1712555 | CPCC | CPCC1078912 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_214700_626300420 | 2016 | Before | 2016-10-19 06:43 | 2016-10-19 14:44 | 18 | 8645.7 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Found open dip fuse pole 214700;crew to make repairs; extending ETR as crew still working on repairs, may be due to location of where they have to dig why it is taking so long | DISTRIBUTION | DEVICE | MANUAL | 2016-10-19 16:00 | COMPLETED |  | 2016-10-19 06:43 | 2016-10-19 15:15 | 2016-10-19 15:18 | -123.9306 | 46.1661
5A15 | 1714850 | CPCC | CPCC1080432 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_216801_626300449 | 2016 | Before | 2016-10-29 10:33 | 2016-10-29 12:10 | 1 | 96.867 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: Serviceman ended up replacing service conductors and B/O Connectors at weatherhead and transformer, restored customer | DISTRIBUTION | CUSTOMER | AUTO |  | COMPLETED |  | 2016-10-29 10:33 | 2016-10-29 17:26 | 2016-10-29 17:28 | -123.9261 | 46.1683
5A15 | 1754203 | CPCC | CPCC1119923 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2017 | Before | 2017-03-10 00:06 | 2017-03-10 00:41 | 1857 | 64406.95 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Loss of Transmission. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2017-03-10 00:14 | 2017-03-10 10:13 | 2017-03-10 04:43 | -123.9097 | 46.1509
5A15 | 1732883 | CPCC | CPCC1099259 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2017 | Before | 2017-01-04 17:21 | 2017-01-04 22:10 | 498 | 144129.666 | 0 | 0 | 1 | Y | N | N | N | Y | OR Consolidated 01-02-2017 | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: 1 phase of primary down -- modeling bad in Cad-Ops, calls coming in on all 3 phases -- breaker not open -- 1 phase out past fp# 224500, approx. 498 customers out -- ran Arcos for a crew -- crew will open CB 5A15 to make repairs PROSPER: creating new outage to pick up balance of circuit | DISTRIBUTION | DEVICE | MANUAL | 2017-01-04 23:45 | COMPLETED |  | 2017-01-04 17:48 | 2017-01-05 09:42 | 2017-01-05 01:48 | -123.9098 | 46.1511
5A15 | 1742646 | CPCC | CPCC1109460 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_217406_626300513 | 2017 | Before | 2017-01-29 14:55 | 2017-01-29 15:36 | 12 | 486.2 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: REPLACED TRANSFORMER FUSE | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2017-01-29 18:00 | COMPLETED |  | 2017-01-29 14:56 | 2017-01-29 18:41 | 2017-01-29 18:43 | -123.9241 | 46.1628
5A15 | 1744465 | CPCC | CPCC1111388 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_189840_825180287 | 2017 | Before | 2017-02-05 19:24 | 2017-02-06 08:48 | 4 | 3215.867 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | SNOW, SLEET AND BLIZZARD |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: wire down btwn 189600 & 188601 | DISTRIBUTION | DEVICE | MANUAL | 2017-02-06 11:00 | COMPLETED |  | 2017-02-05 23:39 | 2017-02-06 10:52 | 2017-02-06 10:53 | -123.9616 | 46.1821
5A15 | 1751074 | CPCC | CPCC1117708 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2017 | Before | 2017-03-01 01:14 | 2017-03-01 02:40 | 1857 | 160351.95 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Fault between Switch 2A24 and Astoria substation | DISTRIBUTION | DEVICE | AUTO | 2017-03-01 04:30 | COMPLETED |  | 2017-03-01 01:19 | 2017-03-01 09:07 | 2017-03-01 07:43 | -123.9097 | 46.151
5A15 | 1747499 | CPCC | CPCC1114840 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2017 | Before | 2017-02-15 23:54 | 2017-02-16 00:01 | 1857 | 13153.75 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE | TREES | TREE - NON-PREVENTABLE | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: 115 KV source CB's Astoria CB 2A6- Lewis & Clark CB 2A5 and BPA Tillamook CB B-1097 relayed open, loss to Seaside, Warrenton, Cannon Beach, Nehalem, Mohler, Garibaldi. Isolated tested, restored PPl load 0001, TPUD at 0009. Mohler & Garibaldi remain out. | DISTRIBUTION | DEVICE | AUTO | 2017-02-16 03:00 | COMPLETED |  | 2017-02-15 23:59 | 2017-02-16 09:09 | 2017-02-16 05:43 | -123.9097 | 46.151
5A15 | 1748922 | CPCC | CPCC1116514 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_216705_626300477 | 2017 | Before | 2017-02-20 21:22 | 2017-02-21 01:50 | 1 | 268.467 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: serviceman reports secondary service replaced - customers power restored | DISTRIBUTION | CUSTOMER | MANUAL | 2017-02-21 03:00 | COMPLETED |  | 2017-02-20 21:22 | 2017-02-21 04:46 | 2017-02-21 04:49 | -123.9277 | 46.1662
5A15 | 1730791 | CPCC | CPCC1094165 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_165402_543460379 | 2016 | Before | 2016-12-28 10:28 | 2016-12-28 11:58 | 1 | 90.317 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | SOURCE: Bad connector replaced PROSPER: power out | DISTRIBUTION | CUSTOMER | AUTO |  | COMPLETED |  | 2016-12-28 10:28 | 2016-12-30 10:40 | 2016-12-28 12:23 | -123.9284 | 46.1762
5A15 | 1738878 | CPCC | CPCC1105524 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2017 | Before | 2017-01-18 04:39 | 2017-01-18 04:43 | 0 | 0 | 1855 | 7234.5 | 1 | Y | N | N | N | Y | OR CoastPlus 01-17-2017 | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Outage was do to loss of transmission. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2017-01-18 05:35 | 2017-01-18 09:51 | 2017-01-18 09:23 | -123.9097 | 46.1509
5A15 | 1739313 | CPCC | CPCC1105270 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_216801_626300449 | 2017 | Before | 2017-01-17 15:55 | 2017-01-17 16:28 | 6 | 201.2 | 0 | 0 | 1 | Y | N | N | N | Y | OR CoastPlus 01-17-2017 | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: broken fuse no cause found | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2017-01-17 19:00 | COMPLETED |  | 2017-01-17 15:55 | 2017-01-18 18:28 | 2017-01-18 18:28 | -123.9261 | 46.1683
5A15 | 1751679 | CPCC | CPCC1118060 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_220605_626300672 | 2017 | Before | 2017-03-03 22:01 | 2017-03-03 23:51 | 1 | 109.883 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | SOURCE: replaced multiple bad connections at transformer bank | DISTRIBUTION | CUSTOMER | AUTO | 2017-03-04 01:15 | COMPLETED |  | 2017-03-03 22:01 | 2017-03-04 01:34 | 2017-03-04 01:39 | -123.9188 | 46.1642
5A15 | 1744462 | CPCC | CPCC1111387 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_188600_825180534 | 2017 | Before | 2017-02-05 19:42 | 2017-02-06 08:47 | 3 | 2355.3 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | SNOW, SLEET AND BLIZZARD |  |  | NO DISTRIBUTION DAMAGE |  |  |  |  | DISTRIBUTION | DEVICE | MANUAL | 2017-02-06 11:00 | COMPLETED |  | 2017-02-05 23:39 | 2017-02-06 10:51 | 2017-02-06 10:53 | -123.9657 | 46.1792
5A15 | 1773459 | CPCC | CPCC1139002 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_220401_626300682 | 2017 | Before | 2017-05-10 18:13 | 2017-05-10 19:08 | 1 | 55.4 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: serviceman reports bad order connector at transformer, repairs made and customer back in service | DISTRIBUTION | CUSTOMER | AUTO |  | COMPLETED |  | 2017-05-10 18:13 | 2017-05-10 22:30 | 2017-05-10 22:34 | -123.919 | 46.1615
5A15 | 1777417 | CPCC | CPCC1142167 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_089810_543460273 | 2017 | Before | 2017-05-24 06:15 | 2017-05-24 07:33 | 1 | 78.467 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman replaced B/O Fuse Door at FP 089810, Restored all customers | DISTRIBUTION | CUSTOMER | AUTO | 2017-05-24 09:15 | COMPLETED |  | 2017-05-24 06:15 | 2017-05-24 09:38 | 2017-05-24 09:43 | -123.9413 | 46.1973
5A15 | 1762137 | CPCC | CPCC1129759 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_050105_1580005926 | 2017 | Before | 2017-04-07 10:48 | 2017-04-07 18:04 | 8 | 3490.4 | 0 | 0 | 1 | Y | N | N | N | Y | OR Consolidated 04-06-2017 | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: tree thru lines, cleared and refused line cutout | DISTRIBUTION | DEVICE | AUTO | 2017-04-07 15:00 | COMPLETED |  | 2017-04-07 11:55 | 2017-04-08 03:46 | 2017-04-08 03:48 | -123.9614 | 46.2012
5A15 | 1762146 | CPCC | CPCC1132540 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_053200_825180328 | 2017 | Before | 2017-04-07 22:03 | 2017-04-07 23:00 | 1 | 56.533 | 0 | 0 | 1 | Y | N | N | N | Y | OR Consolidated 04-06-2017 | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Spliced service out mid span | DISTRIBUTION | CUSTOMER | AUTO | 2017-04-08 01:15 | COMPLETED |  | 2017-04-07 22:04 | 2017-04-08 03:53 | 2017-04-08 03:58 | -123.955 | 46.2021
5A15 | 1762145 | CPCC | CPCC1131386 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_082906_825180280 | 2017 | Before | 2017-04-07 15:31 | 2017-04-07 18:24 | 174 | 30015 | 0 | 0 | 1 | Y | N | N | N | Y | OR Consolidated 04-06-2017 | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: cleared trees from primary, repaired conductor and refused tap line | DISTRIBUTION | DEVICE | AUTO | 2017-04-07 19:00 | COMPLETED |  | 2017-04-07 15:39 | 2017-04-08 03:51 | 2017-04-08 03:53 | -123.9551 | 46.1989
5A15 | 1782354 | CPCC | CPCC1145394 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_087901_825180444 | 2017 | Before | 2017-06-09 11:32 | 2017-06-09 13:29 | 11 | 1071.8 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Burnt pole top at FP 086900, open fuse found at FP 087901, jumpers removed going west at FP 087903, all repairs completed and customers restored serviceman reports likely cutout failed and started tracking, temp repairs made PROSPER: hazard | DISTRIBUTION | DEVICE | MANUAL | 2017-06-09 15:00 | COMPLETED |  | 2017-06-09 11:32 | 2017-06-12 09:51 | 2017-06-09 14:18 | -123.9467 | 46.1982
5A15 | 1783563 | CPCC | CPCC1145898 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_223501_626300379 | 2017 | Before | 2017-06-12 18:06 | 2017-06-12 19:31 | 1 | 84.533 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | SOURCE: replaced sec connectors | DISTRIBUTION | CUSTOMER | AUTO | 2017-06-12 21:15 | COMPLETED |  | 2017-06-12 18:06 | 2017-06-12 20:34 | 2017-06-12 20:38 | -123.9112 | 46.1641
5A15 | 1790249 | CPCC | CPCC1149869 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_094200_543460262 | 2017 | Before | 2017-06-30 17:22 | 2017-06-30 20:16 | 3 | 520.85 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | SOURCE: Crew replaced bad connectors at the transformer | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2017-06-30 22:44 | COMPLETED |  | 2017-06-30 17:23 | 2017-07-01 09:48 | 2017-07-01 09:48 | -123.9309 | 46.1875
5A15 | 1803236 | CPCC | CPCC1157995 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2017 | Before | 2017-08-08 22:04 | 2017-08-08 23:29 | 1869 | 158148.55 | 0 | 0 | 1 | Y | N | N | N | Y | OR CoastPlus 08-08-2017 | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Loss of Astoria - Tillamook 115 kV Line due to Pole Fire | DISTRIBUTION | DEVICE | AUTO | 2017-08-09 01:00 | COMPLETED |  | 2017-08-08 22:05 | 2017-08-09 10:32 | 2017-08-09 03:33 | -123.9107 | 46.1509
5A15 | 1822596 | CPCC | CPCC1168727 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_165504_1580286052 | 2017 | Before | 2017-10-18 20:37 | 2017-10-18 22:27 | 33 | 3622.3 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: tree fell and tore down primary neutral, repairs are made | DISTRIBUTION | DEVICE | AUTO | 2017-10-19 01:45 | COMPLETED |  | 2017-10-18 20:39 | 2017-10-18 22:27 | 2017-10-18 22:28 | -123.9287 | 46.1777
5A15 | 1823726 | CPCC | CPCC1169887 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2017 | Before | 2017-10-21 23:15 | 2017-10-21 23:33 | 1868 | 33624 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Loss of Transmission, cause under investigation | DISTRIBUTION | DEVICE | AUTO | 2017-10-22 02:15 | COMPLETED |  | 2017-10-21 23:17 | 2017-10-23 11:36 | 2017-10-22 04:23 | -123.9107 | 46.1509
5A15 | 1828791 | CPCC | CPCC1173630 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_082906_825180280 | 2017 | Before | 2017-11-12 23:56 | 2017-11-13 03:52 | 72 | 16953.6 | 0 | 0 | 1 | Y | N | N | N | Y | OR Coast Plus 11-12-2017 | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Crew onsite, repairs in progress, all repairs completed and all customers restored | DISTRIBUTION | DEVICE | MANUAL | 2017-11-13 07:00 | COMPLETED |  | 2017-11-12 23:56 | 2017-11-13 04:12 | 2017-11-13 04:13 | -123.9551 | 46.1989
5A15 | 1828793 | CPCC | CPCC1173742 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_082906_825180280 | 2017 | Before | 2017-11-13 02:23 | 2017-11-13 03:52 | 102 | 9003.2 | 0 | 0 | 1 | Y | N | N | N | Y | OR Coast Plus 11-12-2017 | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | PLANNED OUTAGE |  |  |  | SOURCE: Crew Opened remaining 2 phases to facilitate repairs on Outage 1173630 | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2017-11-13 02:23 | 2017-11-13 04:12 | 2017-11-13 04:13 | -123.9551 | 46.1989
5A15 | 1828834 | CPCC | CPCC1173878 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2017 | Before | 2017-11-13 04:35 | 2017-11-13 04:42 | 1868 | 14321.333 | 0 | 0 | 1 | Y | N | N | N | Y | OR Coast Plus 11-12-2017 | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: | DISTRIBUTION | DEVICE | AUTO | 2017-11-13 07:30 | COMPLETED |  | 2017-11-13 04:42 | 2017-11-16 16:06 | 2017-11-13 06:25 | -123.9107 | 46.1509
5A15 | 1829220 | CPCC | CPCC1174482 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | WAR_CB5A15 | 2017 | Before | 2017-11-13 15:30 | 2017-11-13 16:16 | 1868 | 87204.467 | 0 | 0 | 1 | Y | N | N | N | Y | OR Coast Plus 11-12-2017 | LOSS OF SUPPLY | LOSS OF FEED FROM SUPPLIER | WEATHER | WIND | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: weather in area | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2017-11-13 15:41 | 2017-11-16 11:32 | 2017-11-14 06:24 | -123.9107 | 46.1509
5A15 | 1830540 | CPCC | CPCC1175495 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_053201_825180326 | 2017 | Before | 2017-11-18 14:48 | 2017-11-18 18:11 | 6 | 1216.6 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Bad UG Primary, ARCOS Callout for crew started, Crew swapped single phase customer to another phase and will make permanent repairs tomorrow | DISTRIBUTION | DEVICE | MANUAL | 2017-11-19 08:00 | COMPLETED |  | 2017-11-18 14:48 | 2017-11-18 18:41 | 2017-11-18 18:43 | -123.955 | 46.2025
5A15 | 1830721 | CPCC | CPCC1175562 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_053201_825180326 | 2017 | Before | 2017-11-19 11:00 | 2017-11-19 16:36 | 6 | 2013.8 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: B/O UG Primary, Crew repairing, all repairs completed | DISTRIBUTION | DEVICE | MANUAL | 2017-11-19 18:00 | COMPLETED |  | 2017-11-19 11:00 | 2017-11-19 18:05 | 2017-11-19 18:08 | -123.955 | 46.2025
5A15 | 1837858 | CPCC | CPCC1179893 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_220981_626300674 | 2017 | Before | 2017-12-22 10:14 | 2017-12-22 14:31 | 1 | 257.233 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | SOURCE: B/O secondary Cable | DISTRIBUTION | CUSTOMER | MANUAL | 2017-12-22 16:59 | COMPLETED |  | 2017-12-22 10:14 | 2017-12-22 16:43 | 2017-12-22 16:44 | -123.9192 | 46.1685
5A15 | 1871214 | CPCC | CPCC1203253 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_222610_1580311775 | 2018 | After | 2018-05-24 06:12 | 2018-05-24 09:30 | 25 | 4962.5 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: serviceman reports two blown fuses and wire down, will get crew to make repairs | DISTRIBUTION | DEVICE | MANUAL | 2018-05-24 10:30 | COMPLETED |  | 2018-05-24 06:12 | 2018-05-24 14:42 | 2018-05-24 14:45 | -123.9143 | 46.1643
5A15 | 1910611 | CPCC | CPCC1235666 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_220603_626300661 | 2018 | After | 2018-10-30 13:12 | 2018-10-30 14:20 | 1 | 67.783 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | OTHER, KNOWN CAUSE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Street light wire cut in clear, city notified to make repairs | DISTRIBUTION | CUSTOMER | AUTO | 2018-10-30 15:30 | COMPLETED |  | 2018-10-30 13:12 | 2018-10-30 14:20 | 2018-10-30 14:25 | -123.9186 | 46.1652
5A15 | 1912676 | CPCC | CPCC1237173 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_220904_1580364535 | 2018 | After | 2018-11-09 23:02 | 2018-11-10 00:57 | 58 | 6714.467 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | OTHER UG (EXPLAIN IN COMMENTS FIELD) |  |  |  | SOURCE: pistol knocked off, crew will de-energize dip and attempt to re-connect the pistol then re-energize dip PROSPER: change from PLANNED NOTICE EXEMPT to EMERGENCY DAMAGE REPAIR | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2018-11-09 23:04 | 2018-11-14 15:42 | 2018-11-10 06:10 | -123.9193 | 46.1696
5A15 | 1933525 | CPCC | CPCC1259668 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | OH_222610_1580311775 | 2019 | After | 2019-02-06 15:11 | 2019-02-06 16:15 | 18 | 1161 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Open line fuse, no issue found. | DISTRIBUTION | DEVICE | AUTO | 2019-02-06 17:15 | COMPLETED |  | 2019-02-06 15:11 | 2019-02-06 16:16 | 2019-02-06 16:20 | -123.9143 | 46.1643
5A15 | 1933603 | CPCC | CPCC1259684 | PP | OR | CLATSOP (ASTORIA) | WARRENTON | TR_222701_626300659 | 2019 | After | 2019-02-06 16:50 | 2019-02-06 20:27 | 5 | 1088.75 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: replaced transformer fuse | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2019-02-06 22:00 | COMPLETED |  | 2019-02-06 16:50 | 2019-02-06 21:23 | 2019-02-06 21:25 | -123.9133 | 46.166
5A93 | 603095 | CPCC | CPCC412307 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_297400_524160601 | 2007 | Before | 2007-04-02 08:19 | 2007-04-02 10:29 | 1 | 130.417 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused tapline fuse at pole# 294301 and it held, the cause is unknown, customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 602760 | CPCC | CPCC397004 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_030201_475940306 | 2007 | Before | 2007-01-30 08:43 | 2007-01-30 10:35 | 1 | 111.5 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: svcman replaced connections on both ends of the service. customer back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 604110 | CPCC | CPCC397177 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_248601_712540487 | 2007 | Before | 2007-01-31 18:35 | 2007-01-31 20:15 | 88 | 8792.667 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Fuse opened on pole 248601. Serviceman patrolled and found no cause, serviceman found possible tree limb brushing the line. Refused and holding. customers back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6117 | 46.1657
5A93 | 604112 | CPCC | CPCC397184 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_259402_524160636 | 2007 | Before | 2007-01-31 20:23 | 2007-02-01 04:04 | 7 | 3227 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: Bad primary u/g. Repaired U/G customers back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.609 | 46.1475
5A93 | 598901 | CPCC | CPCC393448 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_210904_524160489 | 2007 | Before | 2007-01-11 02:22 | 2007-01-11 06:22 | 33 | 7910.65 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Fuse melted out. Serviceman patrolled and found no cause. Customers back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5684 | 46.1705
5A93 | 620698 | CPCC | CPCC421345 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_307600_524160669 | 2007 | Before | 2007-06-08 10:02 | 2007-06-08 11:32 | 14 | 1256.033 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | CONSTRUCTION |  |  | PLANNED OUTAGE |  |  |  | PROSPER: distribution inmprovement | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5922 | 46.1508
5A93 | 619522 | CPCC | CPCC423356 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_206900_524160494 | 2007 | Before | 2007-06-23 10:52 | 2007-06-23 19:24 | 1 | 512.783 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 618441 | CPCC | CPCC418466 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_163200_475940197 | 2007 | Before | 2007-05-21 02:27 | 2007-05-21 05:42 | 3 | 585.65 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: Bad order cut-out | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 621230 | CPCC | CPCC421408 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_352500_237790110 | 2007 | Before | 2007-06-08 19:35 | 2007-06-08 21:46 | 1 | 130.883 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: Burned off connector. Replaced connector and customer back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 611593 | CPCC | CPCC412615 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_302201_524160641 | 2007 | Before | 2007-04-04 02:35 | 2007-04-04 07:05 | 1 | 269.833 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: Bad UG | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6039 | 46.1445
5A93 | 613668 | CPCC | CPCC415909 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2007 | Before | 2007-04-30 10:19 | 2007-04-30 10:22 | 0 | 0 | 900 | 3300 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF FEED FROM SUPPLIER |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Loss of transmission feed from BPA Ospray Nest 18/1 | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1604
5A93 | 612881 | CPCC | CPCC416376 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | LINECUT-23109 | 2007 | Before | 2007-05-02 13:27 | 2007-05-02 13:40 | 900 | 11700 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF FEED FROM SUPPLIER |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: transmission outage, remodeled for accuracy | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6229 | 46.1609
5A93 | 611691 | CPCC | CPCC414656 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_025000_475940269 | 2007 | Before | 2007-04-17 09:15 | 2007-04-17 10:10 | 1 | 55.017 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: svcman reports he made repairs to broken neut on an oh service. per svcman neut broke due to deterioration. customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 614514 | CPCC | CPCC419901 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_130300_475940356 | 2007 | Before | 2007-05-30 14:02 | 2007-05-30 14:56 | 1 | 54.017 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | LIGHTNING ARRESTER OH |  |  |  | PROSPER: svcman reports blown lightning arrestor caused dip fuse to open. svcman isolated the arrestor, replaced the blown dip fuse and customer is back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5073 | 46.1758
5A93 | 613872 | CPCC | CPCC414988 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_023500_475940276 | 2007 | Before | 2007-04-20 10:25 | 2007-04-20 10:57 | 22 | 720.5 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Crew took outage on tapline at pole# 023500 to make repairs to the overhead primary, customers are all back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.52 | 46.2069
5A93 | 613878 | CPCC | CPCC414999 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_307600_524160669 | 2007 | Before | 2007-04-20 12:29 | 2007-04-20 13:19 | 14 | 697.667 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | INSULATOR OH |  |  |  | PROSPER: crew repairing damaged deadend bells. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5922 | 46.1508
5A93 | 615113 | CPCC | CPCC417230 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | LINECUT-23179 | 2007 | Before | 2007-05-09 13:54 | 2007-05-09 14:02 | 6 | 47.1 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | INSULATOR OH |  |  |  | PROSPER: open jumper to re - set pin in arm | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5965 | 46.1488
5A93 | 617197 | CPCC | CPCC416520 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_206700_524160511 | 2007 | Before | 2007-05-03 09:53 | 2007-05-03 10:46 | 12 | 637.6 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: svcman patrolled beyond a blown line fuse. He found no problems. He refused and customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5763 | 46.1668
5A93 | 624152 | CPCC | CPCC424062 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2007 | Before | 2007-06-27 13:45 | 2007-06-27 13:45 | 0 | 0 | 904 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: T & R | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1604
5A93 | 624963 | CPCC | CPCC424083 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_248601_712540487 | 2007 | Before | 2007-06-27 13:45 | 2007-06-27 16:31 | 90 | 14979 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: tree thru line, crew on site to make repairs.. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6117 | 46.1652
5A93 | 628223 | CPCC | CPCC429479 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_210904_524160489 | 2007 | Before | 2007-07-14 19:06 | 2007-07-14 23:22 | 87 | 6421.8 | 0 | 0 | 2 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Line fuse open. Seriveman patrolling. Refused and found line fuse open on pole 169101. Everyone is back on except 7. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5684 | 46.1705
5A93 | 628225 | CPCC | CPCC429483 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_161100_475940204 | 2007 | Before | 2007-07-14 19:21 | 2007-07-14 20:13 | 1 | 51.683 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Asscoiated to outage 429479. Bad connectivity in CADOPS. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 628231 | CPCC | CPCC429503 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_169101_475940214 | 2007 | Before | 2007-07-14 20:07 | 2007-07-14 23:22 | 4 | 778.8 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Asscoiated with outage 429479. 2 phases on the ground. Opened all 3 fuses on pole 169101. Awaiting crew. Tree went through line and took 3 phases down | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5486 | 46.1735
5A93 | 628233 | CPCC | CPCC429505 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_169101_475940214 | 2007 | Before | 2007-07-14 20:16 | 2007-07-14 23:22 | 31 | 5768.583 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Associated to outage 429503. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5486 | 46.1735
5A93 | 625016 | CPCC | CPCC424655 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_201800_524160541 | 2007 | Before | 2007-07-02 11:30 | 2007-07-02 13:08 | 12 | 1158.9 | 0 | 0 | 2 | Y | N | N | N | N |  | OPERATIONAL | CONTACT BY PACIFICORP |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: wire separated while crew was transferring conductors. crew on site making repairs. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5868 | 46.1674
5A93 | 625017 | CPCC | CPCC424656 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_201800_524160541 | 2007 | Before | 2007-07-02 11:36 | 2007-07-02 13:08 | 110 | 10121.833 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: associate to outage #424655. crew opened line fuses to make repairs. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5868 | 46.1674
5A93 | 626750 | CPCC | CPCC426225 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_302201_524160641 | 2007 | Before | 2007-07-09 17:41 | 2007-07-09 22:07 | 1 | 265.617 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: Bad order underground. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6039 | 46.1445
5A93 | 607234 | CPCC | CPCC406016 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_356702_237790106 | 2007 | Before | 2007-02-23 12:05 | 2007-02-23 14:28 | 1 | 142.45 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: refuse transformer cause unknown | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 607683 | CPCC | CPCC410781 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_044602_475940298 | 2007 | Before | 2007-03-17 15:09 | 2007-03-17 17:12 | 1 | 123.083 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: transformer fuse failed | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 607834 | CPCC | CPCC408126 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_190800_467110037 | 2007 | Before | 2007-02-27 10:28 | 2007-02-27 13:33 | 23 | 4252.7 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: tree off of right of way came down thru line. repairs made all cusotmer are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.4859 | 46.1691
5A93 | 607843 | CPCC | CPCC408218 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_248871_475940363 | 2007 | Before | 2007-02-27 10:58 | 2007-02-27 13:34 | 1 | 155.533 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: associate to outage #408126, b/o connectivity in cadops. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 608676 | CPCC | CPCC409213 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_104900_475940320 | 2007 | Before | 2007-03-03 14:56 | 2007-03-03 16:07 | 1 | 70.933 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Open transformer fuse. bad transformer fuse, replaced and customer back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 605119 | CPCC | CPCC396097 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_033703_475940333 | 2007 | Before | 2007-01-22 15:37 | 2007-01-22 23:02 | 1 | 445.517 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | POLE OH |  |  |  | PROSPER: bus hit and broke pole. Replaced pole customers back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 605127 | CPCC | CPCC396116 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_034903_475940334 | 2007 | Before | 2007-01-22 20:54 | 2007-01-22 23:02 | 43 | 5498.983 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | POLE OH |  |  |  | PROSPER: Associated with outage 396097. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.538 | 46.213
5A93 | 610372 | CPCC | CPCC415129 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_022000_475940270 | 2007 | Before | 2007-04-21 16:20 | 2007-04-21 17:47 | 9 | 782.25 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | INTENTIONAL TO CLEAR TROUBLE | TREES | TREE - NON-PREVENTABLE | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: open line fuse tree burning primary neutral down, repair wire | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5213 | 46.2005
5A93 | 649707 | CPCC | CPCC457557 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_030701_475940162 | 2007 | Before | 2007-11-28 07:06 | 2007-11-28 10:09 | 1 | 182.95 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 648145 | CPCC | CPCC453331 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2007 | Before | 2007-11-12 09:32 | 2007-11-12 09:32 | 0 | 0 | 907 | 256.983 | 1 | Y | N | N | N | Y | 685 - 2007-11-12 to 2007-11-12 OR Clatsop/Astoria | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1604
5A93 | 648146 | CPCC | CPCC453333 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2007 | Before | 2007-11-12 09:23 | 2007-11-13 00:59 | 908 | 155758.267 | 0 | 0 | 3 | Y | N | N | N | Y | 685 - 2007-11-12 to 2007-11-12 OR Clatsop/Astoria | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Tree through line, wire down. Made repairs and customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1604
5A93 | 648948 | CPCC | CPCC464165 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_301502_524160634 | 2007 | Before | 2007-12-06 13:51 | 2007-12-07 20:55 | 1 | 1864.4 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 645352 | CPCC | CPCC451689 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_206806_524160492 | 2007 | Before | 2007-11-03 08:34 | 2007-11-03 11:18 | 35 | 5754 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: B/O undergrounds 35 customers off | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.577 | 46.1685
5A93 | 648194 | CPCC | CPCC454399 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_201804_524160515 | 2007 | Before | 2007-11-12 13:06 | 2007-11-12 23:33 | 305 | 191412.917 | 0 | 0 | 1 | Y | N | N | N | Y | 685 - 2007-11-12 to 2007-11-12 OR Clatsop/Astoria | WEATHER | WIND |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: Broken jumper, had to open line fuses on pole 202800. Made reparis and customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5862 | 46.1679
5A93 | 648971 | CPCC | CPCC464265 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_191604_524160459 | 2007 | Before | 2007-12-06 18:33 | 2007-12-07 20:56 | 2 | 3165.233 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 648974 | CPCC | CPCC464270 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_205980_524160493 | 2007 | Before | 2007-12-06 18:57 | 2007-12-07 20:56 | 1 | 1559.067 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 648977 | CPCC | CPCC464273 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_179000_524160299 | 2007 | Before | 2007-12-06 19:19 | 2007-12-07 20:56 | 1 | 1536.95 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 648980 | CPCC | CPCC464277 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_172803_524160343 | 2007 | Before | 2007-12-06 19:41 | 2007-12-07 21:03 | 1 | 1522.117 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 646582 | CPCC | CPCC447905 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_169101_475940214 | 2007 | Before | 2007-10-18 09:34 | 2007-10-18 10:57 | 7 | 582.867 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: svcman patrolled beyond an open line fuse and found no problems. he replaced the blown line fuse and all customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5486 | 46.1735
5A93 | 645806 | CPCC | CPCC449146 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_109502_1580128764 | 2007 | Before | 2007-10-19 15:25 | 2007-10-19 18:17 | 14 | 2410.333 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: tree thru primary, crew enroute. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5282 | 46.1925
5A93 | 647874 | CPCC | CPCC453195 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2007 | Before | 2007-11-12 09:04 | 2007-11-12 09:04 | 0 | 0 | 909 | 75.75 | 1 | Y | N | N | N | Y | 685 - 2007-11-12 to 2007-11-12 OR Clatsop/Astoria | TREES | TREE - NON-PREVENTABLE |  |  | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1604
5A93 | 646246 | CPCC | CPCC450531 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_167301_475940234 | 2007 | Before | 2007-10-27 08:24 | 2007-10-27 09:59 | 2 | 190.367 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman found transformer fuse open, refused same. No cause found. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 647875 | CPCC | CPCC453207 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2007 | Before | 2007-11-12 09:05 | 2007-11-12 09:05 | 0 | 0 | 909 | 75.75 | 1 | Y | N | N | N | Y | 685 - 2007-11-12 to 2007-11-12 OR Clatsop/Astoria | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1604
5A93 | 647911 | CPCC | CPCC454144 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_290802_524160665 | 2007 | Before | 2007-11-12 15:21 | 2007-11-12 22:12 | 1 | 411.117 | 0 | 0 | 1 | Y | N | N | N | Y | 685 - 2007-11-12 to 2007-11-12 OR Clatsop/Astoria | WEATHER | WIND | WEATHER | WIND | SECONDARY CONDUCTOR OH |  |  |  |  | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 648736 | CPCC | CPCC453845 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_191603_524160455 | 2007 | Before | 2007-11-12 12:56 | 2007-11-13 00:06 | 1 | 670.05 | 0 | 0 | 1 | Y | N | N | N | Y | 685 - 2007-11-12 to 2007-11-12 OR Clatsop/Astoria | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Serviceman patrolled lien and removed several limbs for line. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 648739 | CPCC | CPCC454043 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_033700_475940332 | 2007 | Before | 2007-11-12 12:14 | 2007-11-13 04:50 | 63 | 61528.95 | 0 | 0 | 2 | Y | N | N | N | Y | 685 - 2007-11-12 to 2007-11-12 OR Clatsop/Astoria | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Line down. Isolated at pole 356700. All customers on except 1 transformer. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5396 | 46.2104
5A93 | 649170 | CPCC | CPCC461255 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2007 | Before | 2007-12-03 00:02 | 2007-12-03 00:02 | 0 | 0 | 142 | 11.833 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: T and R | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1604
5A93 | 649171 | CPCC | CPCC461256 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2007 | Before | 2007-12-03 00:02 | 2007-12-04 20:55 | 142 | 382406 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | PROSPER: Breaker was locked out due to storm. Closed breaker and picked up some customers. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1604
5A93 | 649576 | CPCC | CPCC454466 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_142180_475940867 | 2007 | Before | 2007-11-12 23:46 | 2007-11-13 05:56 | 1 | 370.417 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  |  | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 648473 | CPCC | CPCC454286 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_201000_524160571 | 2007 | Before | 2007-11-12 12:18 | 2007-11-13 09:08 | 4 | 4998.933 | 0 | 0 | 1 | Y | N | N | N | Y | 685 - 2007-11-12 to 2007-11-12 OR Clatsop/Astoria | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Tree through line, wire down. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.587 | 46.1564
5A93 | 649232 | CPCC | CPCC458593 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2007 | Before | 2007-12-02 11:36 | 2007-12-06 08:36 | 910 | 4363004.233 | 0 | 0 | 3 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1604
5A93 | 647696 | CPCC | CPCC448325 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_190800_467110037 | 2007 | Before | 2007-10-18 12:36 | 2007-10-18 13:03 | 24 | 652.4 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: svcman replaced blown line fuse and all customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.4859 | 46.1691
5A93 | 641100 | CPCC | CPCC444731 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_206600_524160510 | 2007 | Before | 2007-10-02 20:11 | 2007-10-02 21:52 | 1 | 101.35 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | B/O EQUIPMENT | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | PROSPER: Service was tore from the pole. Going to talk to customer because we need to de energize the transformer to put it back up. Made repairs and customer is back on. Had a bad chicken catcher. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 656837 | CPCC | CPCC465147 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_190300_524160477 | 2007 | Before | 2007-12-08 14:57 | 2007-12-08 17:53 | 1 | 175.517 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 651770 | CPCC | CPCC464307 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_047300_475940300 | 2007 | Before | 2007-12-06 21:10 | 2007-12-07 21:03 | 1 | 1433.367 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 653463 | CPCC | CPCC464829 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_190300_524160477 | 2007 | Before | 2007-12-08 07:48 | 2007-12-08 13:57 | 1 | 368.967 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  |  | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 654298 | CPCC | CPCC464404 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_173200_524160371 | 2007 | Before | 2007-12-07 07:54 | 2007-12-07 21:03 | 1 | 789.617 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 654304 | CPCC | CPCC464414 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_173180_524160361 | 2007 | Before | 2007-12-07 08:14 | 2007-12-07 21:03 | 5 | 3846.833 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 654315 | CPCC | CPCC464907 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_179000_524160299 | 2007 | Before | 2007-12-08 09:10 | 2007-12-08 13:57 | 1 | 286.55 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  |  | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 652219 | CPCC | CPCC461131 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2007 | Before | 2007-12-02 22:04 | 2007-12-03 | 142 | 16524.067 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Outage due to loss of transmission | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1604
5A93 | 654327 | CPCC | CPCC464925 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_363501_237790133 | 2007 | Before | 2007-12-08 09:18 | 2007-12-08 13:57 | 1 | 278.533 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  |  | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 652306 | CPCC | CPCC463709 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_192702_524160452 | 2007 | Before | 2007-12-05 18:24 | 2007-12-07 20:55 | 1 | 3031.217 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 656540 | CPCC | CPCC464657 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_047300_475940300 | 2007 | Before | 2007-12-07 16:25 | 2007-12-08 15:09 | 1 | 1364.2 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  |  | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 651496 | CPCC | CPCC464278 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_168200_475940229 | 2007 | Before | 2007-12-06 19:41 | 2007-12-07 20:56 | 1 | 1515.433 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 651498 | CPCC | CPCC464280 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_204380_524160314 | 2007 | Before | 2007-12-06 19:38 | 2007-12-07 20:56 | 1 | 1518.533 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 651500 | CPCC | CPCC464282 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_169101_475940214 | 2007 | Before | 2007-12-06 19:47 | 2007-12-07 20:56 | 39 | 58860.75 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5486 | 46.1735
5A93 | 651502 | CPCC | CPCC464287 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_197100_524160487 | 2007 | Before | 2007-12-06 20:01 | 2007-12-07 20:56 | 1 | 1494.933 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 653165 | CPCC | CPCC464237 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_307500_524160661 | 2007 | Before | 2007-12-06 16:43 | 2007-12-07 20:56 | 1 | 1692.967 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 654018 | CPCC | CPCC464377 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_354403_237790119 | 2007 | Before | 2007-12-07 03:02 | 2007-12-07 21:03 | 1 | 1081 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 654022 | CPCC | CPCC464384 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_025000_475940269 | 2007 | Before | 2007-12-07 05:17 | 2007-12-07 21:03 | 1 | 945.667 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 654025 | CPCC | CPCC464387 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_190300_524160477 | 2007 | Before | 2007-12-07 06:01 | 2007-12-07 21:03 | 1 | 902.033 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 654028 | CPCC | CPCC464393 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_178080_524160418 | 2007 | Before | 2007-12-07 07:20 | 2007-12-07 21:03 | 1 | 823.383 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 654029 | CPCC | CPCC464394 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_190681_524160462 | 2007 | Before | 2007-12-07 07:28 | 2007-12-07 21:03 | 2 | 1630.9 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 654450 | CPCC | CPCC468335 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_248602_712540487 | 2007 | Before | 2007-12-27 11:47 | 2007-12-27 13:32 | 87 | 9153.85 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: limb broke and fell into primary line. limb removed and all customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6117 | 46.1652
5A93 | 654856 | CPCC | CPCC464484 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_110802_475940265 | 2007 | Before | 2007-12-07 10:38 | 2007-12-07 21:05 | 1 | 626.733 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 654857 | CPCC | CPCC464489 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_363501_237790133 | 2007 | Before | 2007-12-07 10:57 | 2007-12-07 21:05 | 1 | 607.717 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 655692 | CPCC | CPCC464550 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_113404_475940257 | 2007 | Before | 2007-12-07 13:23 | 2007-12-08 15:09 | 2 | 3091.633 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 655699 | CPCC | CPCC464560 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_355602_237790118 | 2007 | Before | 2007-12-07 13:47 | 2007-12-07 23:21 | 1 | 573.85 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 656572 | CPCC | CPCC466079 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_177000_524160500 | 2007 | Before | 2007-12-13 18:43 | 2007-12-13 20:56 | 1 | 133.2 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Karns reports found blown fuse feeding underground and fuse door melted. Will need crew to replace. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5732 | 46.1705
5A93 | 651083 | CPCC | CPCC458590 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2007 | Before | 2007-12-02 11:36 | 2007-12-02 11:36 | 0 | 0 | 910 | 75.833 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: T & R | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1604
5A93 | 651084 | CPCC | CPCC458591 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2007 | Before | 2007-12-02 11:36 | 2007-12-02 11:36 | 0 | 0 | 910 | 197.167 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: T & R | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1604
5A93 | 651506 | CPCC | CPCC464292 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2007 | Before | 2007-12-06 20:15 | 2007-12-06 20:15 | 0 | 0 | 861 | 243.95 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1604
5A93 | 651509 | CPCC | CPCC464301 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_352701_237790112 | 2007 | Before | 2007-12-06 20:37 | 2007-12-07 21:03 | 1 | 1466.2 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 651943 | CPCC | CPCC460966 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2007 | Before | 2007-12-02 20:46 | 2007-12-02 22:04 | 142 | 11016.833 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Wire down, isolated and closed CB. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1604
5A93 | 656159 | CPCC | CPCC465149 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_192702_524160452 | 2007 | Before | 2007-12-08 15:04 | 2007-12-08 17:50 | 1 | 165.867 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 656591 | CPCC | CPCC464296 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_109502_1580128764 | 2007 | Before | 2007-12-06 20:23 | 2007-12-07 13:03 | 14 | 13996.267 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm. Overlaping transf issue, changed On time from 2102 to 1302. P44577 | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5282 | 46.1925
5A93 | 651546 | CPCC | CPCC455162 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_022000_475940270 | 2007 | Before | 2007-11-16 11:20 | 2007-11-16 13:50 | 9 | 1351.2 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: svcman reports wire down. wind blew tree thru the line. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5213 | 46.2005
5A93 | 652861 | CPCC | CPCC464076 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | Line Cut-26649 | 2007 | Before | 2007-12-06 09:08 | 2007-12-06 20:15 | 747 | 455863.65 | 0 | 0 | 4 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND | WEATHER | WIND | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5986 | 46.1672
5A93 | 652038 | CPCC | CPCC463559 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | Line Cut-26623 | 2007 | Before | 2007-12-05 15:00 | 2007-12-05 17:00 | 142 | 17094.433 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: storm related. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1607
5A93 | 652048 | CPCC | CPCC464331 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_290780_524160664 | 2007 | Before | 2007-12-06 22:18 | 2007-12-07 21:03 | 1 | 1365.067 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 652871 | CPCC | CPCC464186 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_248700_712540486 | 2007 | Before | 2007-12-06 14:38 | 2007-12-07 20:55 | 1 | 1817.25 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 653739 | CPCC | CPCC464844 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_163580_467110110 | 2007 | Before | 2007-12-08 08:21 | 2007-12-08 13:57 | 1 | 335.65 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  |  | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 654569 | CPCC | CPCC464430 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_342300_237790085 | 2007 | Before | 2007-12-07 08:57 | 2007-12-07 21:05 | 1 | 728.167 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 654577 | CPCC | CPCC464441 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_341305_237790083 | 2007 | Before | 2007-12-07 09:31 | 2007-12-07 21:05 | 1 | 694.3 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 656711 | CPCC | CPCC465384 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_192702_524160452 | 2007 | Before | 2007-12-09 14:14 | 2007-12-09 16:30 | 1 | 135.717 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 655414 | CPCC | CPCC464531 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_190300_524160477 | 2007 | Before | 2007-12-07 13:20 | 2007-12-08 15:09 | 1 | 1549.15 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 655419 | CPCC | CPCC464537 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_341305_237790083 | 2007 | Before | 2007-12-07 13:20 | 2007-12-08 15:09 | 1 | 1549.217 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 655427 | CPCC | CPCC464548 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_354403_237790119 | 2007 | Before | 2007-12-07 13:23 | 2007-12-07 23:27 | 1 | 604.05 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 653342 | CPCC | CPCC469081 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_206700_524160511 | 2008 | Before | 2008-01-01 08:08 | 2008-01-01 11:41 | 17 | 3613.633 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: crew put primary wire back up and all customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5763 | 46.1668
5A93 | 655466 | CPCC | CPCC466719 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_300300_524160638 | 2007 | Before | 2007-12-18 15:19 | 2007-12-18 17:50 | 3 | 452.4 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: refused, holding | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 652119 | CPCC | CPCC454511 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_356700_237790114 | 2007 | Before | 2007-11-13 05:01 | 2007-11-13 05:32 | 14 | 430.033 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Tree through line. Down primary. Made repairs and customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5142 | 46.2241
5A93 | 652575 | CPCC | CPCC464012 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_256501_712540524 | 2007 | Before | 2007-12-05 22:40 | 2007-12-07 20:55 | 1 | 2774.85 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 650490 | CPCC | CPCC455970 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_081100_475940337 | 2007 | Before | 2007-11-19 15:04 | 2007-11-19 16:44 | 1 | 99.483 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: svcman made repairs to downed service wire. customer does need to make repairs to their equipment before we can re-enrgize. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 652578 | CPCC | CPCC464018 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_243500_712540463 | 2007 | Before | 2007-12-06 06:17 | 2007-12-07 20:55 | 1 | 2317.933 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 652579 | CPCC | CPCC464019 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_191580_524160463 | 2007 | Before | 2007-12-06 06:24 | 2007-12-07 20:55 | 4 | 9244.4 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: wind storm | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 655525 | CPCC | CPCC467678 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2007 | Before | 2007-12-23 17:17 | 2007-12-23 17:17 | 0 | 0 | 910 | 212.333 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: T and R | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1604
5A93 | 655527 | CPCC | CPCC467681 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2007 | Before | 2007-12-23 17:28 | 2007-12-23 17:28 | 0 | 0 | 910 | 212.333 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: T and R | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1604
5A93 | 655528 | CPCC | CPCC467684 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_114400_475940255 | 2007 | Before | 2007-12-23 17:32 | 2007-12-24 00:21 | 1 | 408.933 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: tree took out 3 phase | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 655530 | CPCC | CPCC467689 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_169101_475940214 | 2007 | Before | 2007-12-23 17:29 | 2007-12-24 00:20 | 39 | 16012.75 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: tree took out 3 phase | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5486 | 46.1735
5A93 | 634192 | CPCC | CPCC436499 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_201002_524160572 | 2007 | Before | 2007-08-21 16:12 | 2007-08-21 17:11 | 1 | 58.55 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: exavator tore down service wire. crew made repair and customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 633801 | CPCC | CPCC434832 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_354800_237790104 | 2007 | Before | 2007-08-13 03:14 | 2007-08-13 05:41 | 1 | 146.933 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 632671 | CPCC | CPCC434199 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_206700_524160511 | 2007 | Before | 2007-08-09 08:24 | 2007-08-09 10:32 | 12 | 1544.2 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused tapline fuse at pole# 206700 and it held, the cause is unknown, customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5763 | 46.1668
5A93 | 632044 | CPCC | CPCC432924 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_187000_524160426 | 2007 | Before | 2007-08-03 08:27 | 2007-08-03 09:30 | 4 | 253.4 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: svcman reports he replaced a fuse that pulled apart and customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 670927 | CPCC | CPCC490261 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2008 | Before | 2008-02-27 18:09 | 2008-02-27 18:10 | 0 | 0 | 905 | 905 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: T&R | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1604
5A93 | 675740 | CPCC | CPCC505123 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_170000_524160401 | 2008 | Before | 2008-06-06 10:03 | 2008-06-06 10:38 | 1 | 34.817 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Re-fused ok. Cause due to sparrow. All power restored | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 670991 | CPCC | CPCC493815 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | Line Cut-28408 | 2008 | Before | 2008-03-27 00:26 | 2008-03-27 02:37 | 743 | 96812.9 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: tree in right of way fell onto primary lines open solid blades to make repair | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5869 | 46.1678
5A93 | 671438 | CPCC | CPCC501308 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2008 | Before | 2008-05-14 08:26 | 2008-05-14 08:26 | 0 | 0 | 905 | 30.167 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: t & r | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1604
5A93 | 675927 | CPCC | CPCC503344 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_259402_524160636 | 2008 | Before | 2008-05-23 14:41 | 2008-05-23 20:13 | 8 | 1717.467 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: fp 259402. Cutout feeds primary underground and is blown. 1652 Hankwitz arrived. Made repairs and customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.609 | 46.1475
5A93 | 675234 | CPCC | CPCC499388 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_058001_467110036 | 2008 | Before | 2008-05-10 10:50 | 2008-05-10 16:08 | 11 | 3489.933 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Tree through the primary. Blown line fuse and wire down. Made repairs and customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.4467 | 46.1995
5A93 | 667071 | CPCC | CPCC490554 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_025000_475940269 | 2008 | Before | 2008-03-01 09:59 | 2008-03-01 11:45 | 1 | 106.3 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Burnt neutral and hotleg, bad order secondary . Respliced service and customer is back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 665944 | CPCC | CPCC488945 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_173802_524160344 | 2008 | Before | 2008-02-14 10:18 | 2008-02-14 10:59 | 143 | 5853.467 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | PROSPER: Sleeve failed while straightning pole per Jay Smith | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5816 | 46.1831
5A93 | 677821 | CPCC | CPCC502518 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_163200_475940197 | 2008 | Before | 2008-05-19 12:29 | 2008-05-19 13:31 | 3 | 185.45 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Refused B/O transformer fuse. All power restored | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 680000 | CPCC | CPCC509420 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_163200_475940197 | 2008 | Before | 2008-06-29 19:12 | 2008-06-29 19:17 | 0 | 0 | 1 | 4.95 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Negative duration issue, late call. Changed OFF time from 1919 to 1916 and ON time seconds, from 00 to 31. P44577. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 676857 | CPCC | CPCC504820 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_201901_524160517 | 2008 | Before | 2008-06-03 20:25 | 2008-06-03 22:00 | 1 | 94.567 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 676859 | CPCC | CPCC504822 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_201901_524160517 | 2008 | Before | 2008-06-03 21:15 | 2008-06-03 22:00 | 4 | 181.133 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 657686 | CPCC | CPCC465265 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_169101_475940214 | 2007 | Before | 2007-12-09 05:48 | 2007-12-09 09:39 | 39 | 9008.35 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | PROSPER: Holehouser on site repairs made | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5486 | 46.1735
5A93 | 661559 | CPCC | CPCC482034 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_361602_237790075 | 2008 | Before | 2008-01-24 12:51 | 2008-01-24 14:34 | 1 | 102.75 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | OTHER, KNOWN CAUSE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: svcman reports customer did have low voltage, he tapped the trf and customer is back to 121/242 volts. left message on customers phone recorder notifying them of what was done here. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 657386 | CPCC | CPCC464775 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_023301_475940272 | 2007 | Before | 2007-12-07 22:13 | 2007-12-08 15:09 | 1 | 1015.833 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  |  | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 657388 | CPCC | CPCC464777 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_175200_467110038 | 2007 | Before | 2007-12-07 22:12 | 2007-12-08 15:09 | 1 | 1017.05 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  |  | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 659930 | CPCC | CPCC482502 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_172200_524160298 | 2008 | Before | 2008-01-26 14:30 | 2008-01-26 16:49 | 11 | 1528.633 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Primary wire down. Tree fell down and tore wire down. Made repairs, closed in line fuse and customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5835 | 46.1732
5A93 | 660383 | CPCC | CPCC478964 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2008 | Before | 2008-01-14 13:07 | 2008-01-14 13:07 | 0 | 0 | 911 | 212.567 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: T & R | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1604
5A93 | 660384 | CPCC | CPCC478969 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_169101_475940214 | 2008 | Before | 2008-01-14 13:07 | 2008-01-14 16:50 | 39 | 8713.9 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: trees on line caused wire to burn down. crew enroute to make repairs. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5486 | 46.1735
5A93 | 659178 | CPCC | CPCC477651 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_206302_524160590 | 2008 | Before | 2008-01-08 18:42 | 2008-01-08 21:17 | 1 | 154.933 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - TRIMMABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Found blown fuse feeding U/G dip service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 659188 | CPCC | CPCC477811 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_206403_524160588 | 2008 | Before | 2008-01-08 20:58 | 2008-01-08 21:16 | 2 | 37.367 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - TRIMMABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Tree had pushed hot tap into neutral. removed tree, all good | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5766 | 46.1615
5A93 | 657100 | CPCC | CPCC464725 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_169200_475940217 | 2007 | Before | 2007-12-07 19:10 | 2007-12-08 15:09 | 1 | 1199.417 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  |  | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 657103 | CPCC | CPCC464729 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_206500_524160508 | 2007 | Before | 2007-12-07 19:22 | 2007-12-08 15:09 | 1 | 1187.033 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  |  | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 657106 | CPCC | CPCC464734 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_179000_524160299 | 2007 | Before | 2007-12-07 19:36 | 2007-12-08 15:09 | 1 | 1173.517 | 0 | 0 | 1 | Y | N | N | N | Y | 687 - 2007-12-02 to 2007-12-08 OR Clatsop | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  |  | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 657514 | CPCC | CPCC468165 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_249970_475940366 | 2007 | Before | 2007-12-26 14:05 | 2007-12-26 15:24 | 1 | 79.233 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: svcman replaced a broken trf cutout fuse and customer is back in full service. cause is unknown. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 658009 | CPCC | CPCC474551 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_248502_712540491 | 2008 | Before | 2008-01-05 18:00 | 2008-01-05 19:35 | 2 | 190.767 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: svcman replaced a broken trf cutout fuse and customer is back in full service. cause is unknown. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 701127 | CPCC | CPCC529588 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | Line Cut-31839 | 2008 | Before | 2008-11-03 14:25 | 2008-11-03 14:35 | 911 | 9504.767 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Modeled breaker 5A93 open due to loss of transmission. Breaker 2A2 opened with no cause found. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1607
5A93 | 701907 | CPCC | CPCC531954 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_190300_524160477 | 2008 | Before | 2008-11-17 09:27 | 2008-11-17 10:35 | 3 | 204.6 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Refuse transformer. Power restored | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 697699 | CPCC | CPCC525599 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_111401_475940261 | 2008 | Before | 2008-10-04 12:28 | 2008-10-04 13:16 | 1 | 47.65 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 700947 | CPCC | CPCC527592 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_194703_524160465 | 2008 | Before | 2008-10-19 19:56 | 2008-10-19 23:58 | 1 | 242.617 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | TRANSFORMER OH |  |  |  | PROSPER: replaced transformer | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 692620 | CPCC | CPCC517516 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_206806_524160492 | 2008 | Before | 2008-08-16 19:02 | 2008-08-16 22:03 | 35 | 6321 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER PADMOUNT/SUBMERSIBLE UG |  |  |  | PROSPER: Burnt up pad mount transformer. Replaced and customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.577 | 46.1685
5A93 | 696138 | CPCC | CPCC523343 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_291580_524160331 | 2008 | Before | 2008-09-19 15:35 | 2008-09-19 21:51 | 1 | 376.633 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Tree fell through primary tore it down. Made repairs and customers are back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 695758 | CPCC | CPCC525677 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_058001_467110036 | 2008 | Before | 2008-10-05 07:53 | 2008-10-05 12:21 | 11 | 2941.033 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.4467 | 46.1995
5A93 | 706304 | CPCC | CPCC549983 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2009 | Before | 2009-01-22 13:07 | 2009-01-22 13:09 | 0 | 0 | 914 | 2010.8 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF FEED FROM SUPPLIER |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1604
5A93 | 702738 | CPCC | CPCC534942 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2008 | Before | 2008-12-12 17:46 | 2008-12-12 17:46 | 0 | 0 | 913 | 213.033 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: T & R | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1604
5A93 | 704700 | CPCC | CPCC549319 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_291980_524160617 | 2009 | Before | 2009-01-18 00:17 | 2009-01-18 03:52 | 1 | 215.117 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | PROSPER: fuse blown. Patrolling line. Found bad crimps. Spans long and crew needed to help. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 702741 | CPCC | CPCC534949 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2008 | Before | 2008-12-12 18:05 | 2008-12-12 18:06 | 0 | 0 | 913 | 319.55 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: T & R | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1604
5A93 | 702742 | CPCC | CPCC534957 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | Line Cut-32347 | 2008 | Before | 2008-12-12 17:54 | 2008-12-13 06:52 | 99 | 31086.9 | 0 | 0 | 2 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: 3 phases of wire down. Crew to make repairs. Caution tag 45950 is where line fuses are open. Dick and Gowing and contract crew | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5662 | 46.17
5A93 | 702772 | CPCC | CPCC548098 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_176100_1580001881 | 2009 | Before | 2009-01-08 12:40 | 2009-01-08 15:30 | 11 | 1871.833 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: No cause found. Power restored. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.4532 | 46.1723
5A93 | 708889 | CPCC | CPCC549699 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_208981_524160505 | 2009 | Before | 2009-01-20 11:52 | 2009-01-20 14:54 | 1 | 182.017 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | PROSPER: B/O UG secondary neutral. Installed service saver. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 703279 | CPCC | CPCC535231 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2008 | Before | 2008-12-13 11:20 | 2008-12-13 11:42 | 913 | 19492.55 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF FEED FROM SUPPLIER |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: loss of supply from BPA 1119 to 1122 | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1604
5A93 | 707292 | CPCC | CPCC549577 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | Line Cut-33109 | 2009 | Before | 2009-01-19 09:57 | 2009-01-19 10:05 | 914 | 6915.933 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Loss of transmission | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1607
5A93 | 703715 | CPCC | CPCC554661 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_249202_712540494 | 2009 | Before | 2009-02-26 20:45 | 2009-02-26 21:48 | 2 | 125.1 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused transformer ok. Cause was deteriorated fuse. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 704192 | CPCC | CPCC550300 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2009 | Before | 2009-01-25 03:55 | 2009-01-25 03:56 | 0 | 0 | 914 | 76.167 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: trip and reclose | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1604
5A93 | 704193 | CPCC | CPCC550301 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_307600_524160669 | 2009 | Before | 2009-01-25 04:53 | 2009-01-25 09:40 | 16 | 4586.933 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Line is down, unknown cause at this time. Crew on the way to make repairs. Kinder, Saltmarsh, Karns and Kaplan. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5922 | 46.1508
5A93 | 706602 | CPCC | CPCC553750 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_206700_524160511 | 2009 | Before | 2009-02-20 09:21 | 2009-02-20 10:03 | 12 | 495.2 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | OTHER UTILITY/CONTRACTOR | TREES | TREE - NON-PREVENTABLE | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Loggers fell a tree into lines, slapped two phases together and blew a fuse. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5763 | 46.1668
5A93 | 703808 | CPCC | CPCC535461 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_058001_467110036 | 2008 | Before | 2008-12-14 12:18 | 2008-12-14 15:04 | 11 | 1826.183 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | SNOW, SLEET AND BLIZZARD |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Found blown line fuse. Patrolling for cause. Found wire down pole# 050902. Crew is enroute to make repairs. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.4467 | 46.1995
5A93 | 684349 | CPCC | CPCC509948 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2008 | Before | 2008-07-01 13:58 | 2008-07-01 16:32 | 905 | 139113.583 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF FEED FROM SUPPLIER |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Lost source from BPA - probable tower down. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1604
5A93 | 683563 | CPCC | CPCC510269 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | Line Cut-29878 | 2008 | Before | 2008-07-03 01:44 | 2008-07-03 03:49 | 905 | 113562.417 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Loss of transmission line. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1607
5A93 | 683219 | CPCC | CPCC509386 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2008 | Before | 2008-06-29 19:11 | 2008-06-29 19:20 | 904 | 8136 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  |  | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1604
5A93 | 683223 | CPCC | CPCC509421 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_177380_524161573 | 2008 | Before | 2008-06-29 19:15 | 2008-06-29 19:16 | 0 | 0 | 1 | 0.867 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  |  | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 683224 | CPCC | CPCC509422 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_113404_475940257 | 2008 | Before | 2008-06-29 19:15 | 2008-06-29 19:16 | 0 | 0 | 1 | 0.683 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  |  | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 683225 | CPCC | CPCC509423 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_174280_524160367 | 2008 | Before | 2008-06-29 19:15 | 2008-06-29 19:16 | 0 | 0 | 1 | 0.583 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  |  | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 683228 | CPCC | CPCC509426 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_167200_475940168 | 2008 | Before | 2008-06-29 19:15 | 2008-06-29 19:28 | 1 | 12.433 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  |  | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 683229 | CPCC | CPCC509427 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_259480_712540534 | 2008 | Before | 2008-06-29 19:15 | 2008-06-29 19:16 | 0 | 0 | 1 | 0.883 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  |  | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 686621 | CPCC | CPCC513889 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_080101_475940339 | 2008 | Before | 2008-07-26 17:33 | 2008-07-26 19:38 | 1 | 124.9 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: broken nuetral on secondary | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 726215 | CPCC | CPCC575424 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_191603_524160455 | 2009 | Before | 2009-07-13 18:40 | 2009-07-13 21:00 | 1 | 140.25 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Customer's Neutral conductor was deteriorated. Serviceman replaced customer's secondary service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 725438 | CPCC | CPCC564013 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2009 | Before | 2009-05-05 01:44 | 2009-05-05 01:44 | 0 | 0 | 915 | 320.25 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Breaker tripped and reclosed ok. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1604
5A93 | 725439 | CPCC | CPCC564014 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2009 | Before | 2009-05-05 01:51 | 2009-05-05 01:51 | 0 | 0 | 915 | 213.5 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Breaker tripped and reclosed ok. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1604
5A93 | 725440 | CPCC | CPCC564015 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_169101_475940214 | 2009 | Before | 2009-05-05 01:53 | 2009-05-05 06:35 | 29 | 8191.533 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Crew completed repairs to O/H primary conductor due to tree through line. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5486 | 46.1735
5A93 | 725441 | CPCC | CPCC564016 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_169101_475940214 | 2009 | Before | 2009-05-05 01:59 | 2009-05-05 06:35 | 10 | 2759.833 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Crew completed repairs to O/H primary conductor due to tree through line. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5486 | 46.1735
5A93 | 717599 | CPCC | CPCC541686 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | Line Cut-32674 | 2008 | Before | 2008-12-24 14:48 | 2008-12-24 14:52 | 0 | 0 | 913 | 3058.55 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1607
5A93 | 715981 | CPCC | CPCC540295 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_169101_475940214 | 2008 | Before | 2008-12-22 12:56 | 2008-12-22 16:44 | 39 | 8884.2 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | SNOW, SLEET AND BLIZZARD | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Tree in line blew line fuse. Crew to remove tree. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5486 | 46.1735
5A93 | 716814 | CPCC | CPCC542587 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_176100_1580001881 | 2008 | Before | 2008-12-25 17:29 | 2008-12-25 19:43 | 11 | 1477.117 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | SNOW, SLEET AND BLIZZARD | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Repairs made to line. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.4532 | 46.1723
5A93 | 717301 | CPCC | CPCC545017 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_106200_475940283 | 2009 | Before | 2009-01-01 13:07 | 2009-01-01 14:33 | 3 | 260.1 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Fuse blown. Unknown cause. Refusing. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5355 | 46.1883
5A93 | 719310 | CPCC | CPCC565133 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2009 | Before | 2009-05-14 14:12 | 2009-05-14 14:13 | 0 | 0 | 915 | 76.25 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: T & R | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1604
5A93 | 719311 | CPCC | CPCC565135 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_201800_524160541 | 2009 | Before | 2009-05-14 14:21 | 2009-05-14 15:31 | 83 | 5743.6 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: One phase blown on a set of line cut-outs. Serviceman is patrolling beyond. Serviceman patrolled line, found no cause and refused. All customers back in service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5868 | 46.1674
5A93 | 718970 | CPCC | CPCC532195 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_203900_524160528 | 2008 | Before | 2008-11-20 06:36 | 2008-11-20 08:15 | 1 | 99.467 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Refused transformer. Power restored. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 720655 | CPCC | CPCC565362 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_336100_237790136 | 2009 | Before | 2009-05-16 20:17 | 2009-05-16 21:45 | 1 | 87.317 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: replaced transformer fuse | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 717084 | CPCC | CPCC541549 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_159300_475940191 | 2008 | Before | 2008-12-24 10:47 | 2008-12-24 11:52 | 1 | 65 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | SNOW, SLEET AND BLIZZARD | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5282 | 46.1764
5A93 | 728461 | CPCC | CPCC572265 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_246700_712540483 | 2009 | Before | 2009-06-23 09:11 | 2009-06-23 09:25 | 0 | 0 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: blown xfmr fuse. Serviceman investigating. Deteriorated xfmr fuse. Serviceman replaced. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 728766 | CPCC | CPCC572928 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_069800_467110028 | 2009 | Before | 2009-06-28 16:07 | 2009-06-28 17:53 | 1 | 106.317 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: replaced transformer fuse | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 709454 | CPCC | CPCC542531 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_194601_524160468 | 2008 | Before | 2008-12-25 15:01 | 2008-12-25 15:01 | 0 | 0 | 3 | 1.75 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | ICE | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 709187 | CPCC | CPCC542470 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_194601_524160468 | 2008 | Before | 2008-12-25 11:30 | 2008-12-25 15:00 | 3 | 630.9 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | ICE | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 709189 | CPCC | CPCC542475 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_173802_524160344 | 2008 | Before | 2008-12-25 11:20 | 2008-12-25 14:27 | 51 | 9539.55 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5816 | 46.1831
5A93 | 709192 | CPCC | CPCC542479 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_194703_524160465 | 2008 | Before | 2008-12-25 12:00 | 2008-12-25 15:00 | 1 | 180.35 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | ICE | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 709193 | CPCC | CPCC542489 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_173802_524160344 | 2008 | Before | 2008-12-25 12:39 | 2008-12-25 14:27 | 104 | 11181.733 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | INTENTIONAL TO CLEAR TROUBLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5816 | 46.1831
5A93 | 713231 | CPCC | CPCC546737 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_169500_475940248 | 2009 | Before | 2009-01-03 10:37 | 2009-01-03 11:37 | 14 | 843.733 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | SNOW, SLEET AND BLIZZARD |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: wire diown at pole 104100 | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5494 | 46.1785
5A93 | 714873 | CPCC | CPCC559666 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_172600_524160349 | 2009 | Before | 2009-04-06 21:06 | 2009-04-06 22:24 | 4 | 312.2 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Transformer fuse blew. Fuse was deteriorated. Refused and customers are back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 711360 | CPCC | CPCC546394 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_050902_467110030 | 2009 | Before | 2009-01-02 10:59 | 2009-01-02 14:03 | 1 | 184.567 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | TRANSFORMER OH |  |  |  | PROSPER: Crew repalced damaged transformer. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 712965 | CPCC | CPCC546710 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | Line Cut-32886 | 2009 | Before | 2009-01-03 07:09 | 2009-01-03 11:37 | 4 | 1074.067 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | SNOW, SLEET AND BLIZZARD |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: wire down at pole 104100, see outage 546737 | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5395 | 46.1863
5A93 | 709759 | CPCC | CPCC550646 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2009 | Before | 2009-01-22 14:03 | 2009-01-22 14:04 | 0 | 0 | 914 | 487.467 | 1 | Y | N | N | N | N |  | PLANNED | TRANSMISSION REQUESTED |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: grid de-energized transmission line per BPA request to facilitate switching requirments. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1604
5A93 | 713042 | CPCC | CPCC560723 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_022000_475940270 | 2009 | Before | 2009-04-13 09:19 | 2009-04-13 10:06 | 9 | 416.25 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | INTENTIONAL TO CLEAR TROUBLE | TREES | TREE - NON-PREVENTABLE | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman opened a set of cut-outs so that a tree crew could remove a tree from lines. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5213 | 46.2005
5A93 | 750356 | CPCC | CPCC596904 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_114400_475940255 | 2009 | Before | 2009-11-08 13:09 | 2009-11-08 14:34 | 1 | 84.95 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: B/O cutout fuse | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 753901 | CPCC | CPCC624411 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | Line Cut-41958 | 2010 | Before | 2010-03-29 10:05 | 2010-03-29 10:21 | 920 | 14720 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Loss of x-mission | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1607
5A93 | 750782 | CPCC | CPCC592967 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2009 | Before | 2009-10-14 11:30 | 2009-10-14 11:30 | 0 | 0 | 920 | 76.667 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: T & R. High winds in area. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1604
5A93 | 749211 | CPCC | CPCC601002 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_303200_524160647 | 2009 | Before | 2009-11-22 19:31 | 2009-11-22 19:31 | 0 | 0 | 1 | 0.733 | 1 | Y | N | N | N | Y | 858 - 2009-11-22 to 2009-11-22 OR Clatsop | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: tree on line | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 749214 | CPCC | CPCC601008 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | SB_156303_1580204317 | 2009 | Before | 2009-11-22 20:14 | 2009-11-22 22:59 | 37 | 6109.933 | 0 | 0 | 1 | Y | N | N | N | Y | 858 - 2009-11-22 to 2009-11-22 OR Clatsop | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: cadops server needed to br rebooted by IT , linked to Roseburg area cust reported up by Astoria GF, IT issues | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5342 | 46.1758
5A93 | 749219 | CPCC | CPCC601037 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | Line Cut-39523 | 2009 | Before | 2009-11-22 20:21 | 2009-11-23 01:31 | 56 | 15404.133 | 0 | 0 | 2 | Y | N | N | N | Y | 858 - 2009-11-22 to 2009-11-22 OR Clatsop | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.52 | 46.2068
5A93 | 753166 | CPCC | CPCC598892 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | SW_172800_1580005920 | 2009 | Before | 2009-11-17 11:11 | 2009-11-17 11:13 | 0 | 0 | 29 | 59.45 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | TREES | TREE - NON-PREVENTABLE | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Crew had to open a switch to close a set of fuses on a dead line and pick up load with the switch. Fuses were open because wire that was down due to wind and trees. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5836 | 46.1821
5A93 | 752400 | CPCC | CPCC600346 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | Line Cut-39491 | 2009 | Before | 2009-11-22 06:33 | 2009-11-22 20:19 | 921 | 174046.032 | 0 | 0 | 5 | Y | N | N | N | Y | 858 - 2009-11-22 to 2009-11-22 OR Clatsop | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Manually opened CB 5A93 due to tree laying across primary and we did not want to heat the circuit up when we heated high line up. Other wire down, have been isolating and sectionalizing. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6232 | 46.1605
5A93 | 753179 | CPCC | CPCC600971 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_030701_475940162 | 2009 | Before | 2009-11-22 15:35 | 2009-11-22 20:53 | 1 | 317.883 | 0 | 0 | 1 | Y | N | N | N | Y | 858 - 2009-11-22 to 2009-11-22 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: fuse out -- refused | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 753192 | CPCC | CPCC600993 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_020500_475940329 | 2009 | Before | 2009-11-22 18:19 | 2009-11-23 01:31 | 1 | 431.333 | 0 | 0 | 1 | Y | N | N | N | Y | 858 - 2009-11-22 to 2009-11-22 OR Clatsop | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 753195 | CPCC | CPCC600997 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_342205_237790086 | 2009 | Before | 2009-11-22 18:56 | 2009-11-23 04:10 | 1 | 554.467 | 0 | 0 | 1 | Y | N | N | N | Y | 858 - 2009-11-22 to 2009-11-22 OR Clatsop | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 750091 | CPCC | CPCC596843 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | Line Cut-39066 | 2009 | Before | 2009-11-07 23:10 | 2009-11-08 03:08 | 1 | 237.467 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: removed tree and put wire back up | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5076 | 46.2222
5A93 | 750092 | CPCC | CPCC596865 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | RC_202904_1580471805 | 2009 | Before | 2009-11-07 23:03 | 2009-11-08 01:29 | 273 | 39826.15 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: trere through the line, see outage # 596843 | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5845 | 46.1701
5A93 | 751335 | CPCC | CPCC601196 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | Line Cut-39556 | 2009 | Before | 2009-11-23 14:33 | 2009-11-23 14:36 | 0 | 0 | 921 | 2471.35 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6229 | 46.1609
5A93 | 752487 | CPCC | CPCC598614 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | RC_202904_1580471805 | 2009 | Before | 2009-11-16 22:54 | 2009-11-17 11:13 | 274 | 160241.3 | 0 | 0 | 2 | Y | N | N | N | Y | 855 - 2009-11-16 to 2009-11-16 OR Clatsop | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: recloser trip open. Tree through primary conductor. Crew to make repairs. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5845 | 46.1701
5A93 | 750536 | CPCC | CPCC600302 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | Line Cut-39485 | 2009 | Before | 2009-11-22 05:26 | 2009-11-22 06:33 | 921 | 61707 | 0 | 0 | 1 | Y | N | N | N | Y | 858 - 2009-11-22 to 2009-11-22 OR Clatsop | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE | WEATHER | WIND | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Transmission line tripped open, sectionalized and restored power to the substation | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1608
5A93 | 750545 | CPCC | CPCC601046 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_362600_237790131 | 2009 | Before | 2009-11-23 00:35 | 2009-11-23 01:37 | 1 | 62.2 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | POLE OH |  |  |  | PROSPER: service has been restored | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 750546 | CPCC | CPCC601047 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_360600_237790128 | 2009 | Before | 2009-11-23 01:00 | 2009-11-23 01:35 | 1 | 35.467 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | POLE OH |  |  |  | PROSPER: customer back in power | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 750552 | CPCC | CPCC601061 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_058001_467110036 | 2009 | Before | 2009-11-23 07:59 | 2009-11-23 11:09 | 11 | 2093.3 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman has another call. Tree caused line fuse to blow. Crew removed tree and refused line. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.4467 | 46.1995
5A93 | 752913 | CPCC | CPCC600938 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_303400_524160645 | 2009 | Before | 2009-11-22 13:27 | 2009-11-22 21:08 | 1 | 461.15 | 0 | 0 | 1 | Y | N | N | N | Y | 858 - 2009-11-22 to 2009-11-22 OR Clatsop | WEATHER | WIND |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: svcman has restored power. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 752575 | CPCC | CPCC599936 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_248602_712540487 | 2009 | Before | 2009-11-21 23:53 | 2009-11-22 03:53 | 91 | 21891.567 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6117 | 46.1652
5A93 | 749109 | CPCC | CPCC599774 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2009 | Before | 2009-11-21 23:48 | 2009-11-21 23:48 | 0 | 0 | 921 | 76.75 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE | WEATHER | WIND | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1604
5A93 | 746961 | CPCC | CPCC581932 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_259300_1580247858 | 2009 | Before | 2009-08-11 14:23 | 2009-08-11 19:44 | 41 | 4670.783 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: line fuse blown at pole 259300. Serviceman patrolling. Fuse on dip pole 302201 blew on test. Crew to make repairs. Repairs made and customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6091 | 46.1465
5A93 | 759432 | CPCC | CPCC608170 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_033700_475940332 | 2009 | Before | 2009-12-24 12:35 | 2009-12-24 13:44 | 62 | 4316.233 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Line fuse melted out on cold load pick up. Serviceman refused line and it held. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5396 | 46.2104
5A93 | 757116 | CPCC | CPCC628541 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_083103_475940343 | 2010 | Before | 2010-04-18 18:09 | 2010-04-18 20:11 | 1 | 121.967 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | PROSPER: serviceman found bad secondary neutral connection, repaired, power back to normal. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 754436 | CPCC | CPCC624538 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | Line Cut-41987 | 2010 | Before | 2010-03-29 10:44 | 2010-03-29 10:46 | 0 | 0 | 920 | 1855.333 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Loss of Transmission | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1607
5A93 | 759165 | CPCC | CPCC608100 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | Line Cut-40222 | 2009 | Before | 2009-12-24 10:34 | 2009-12-24 12:30 | 156 | 18137.6 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | INTERFERENCE | VEHICLE ACCIDENT | POLE OH |  |  |  | PROSPER: Crew lifted a set of jumpers to issolate a car hit pole. Crew to repalce pole 173800. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5836 | 46.1826
5A93 | 757311 | CPCC | CPCC624130 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | Line Cut-41942 | 2010 | Before | 2010-03-29 07:18 | 2010-03-29 07:34 | 920 | 14720 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Loss of x-mission | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1607
5A93 | 756136 | CPCC | CPCC619472 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_203801_524160536 | 2010 | Before | 2010-02-25 15:45 | 2010-02-25 17:34 | 3 | 326.75 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman off. District to dispatch this call. Patrolling, fused melted out, refused transformer, power back to normal | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 758909 | CPCC | CPCC610378 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_058001_467110036 | 2010 | Before | 2010-01-01 18:51 | 2010-01-01 20:19 | 11 | 960.667 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: found nothing, refused line fuse, power ok | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.4467 | 46.1995
5A93 | 737659 | CPCC | CPCC588027 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_200801_524160542 | 2009 | Before | 2009-09-19 11:29 | 2009-09-19 14:24 | 1 | 174.967 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 737327 | CPCC | CPCC584971 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_166301_475940230 | 2009 | Before | 2009-08-30 06:01 | 2009-08-30 10:12 | 1 | 250.167 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | PROSPER: Bad transformer | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 738966 | CPCC | CPCC588730 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2009 | Before | 2009-09-22 04:41 | 2009-09-22 04:41 | 0 | 0 | 919 | 76.583 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: T&R | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1604
5A93 | 738968 | CPCC | CPCC588731 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_307600_524160669 | 2009 | Before | 2009-09-22 05:04 | 2009-09-22 07:14 | 6 | 780.3 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: removed tree limb, power ok, refused line fuse, all on | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5922 | 46.1508
5A93 | 737585 | CPCC | CPCC583698 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_170903_524160336 | 2009 | Before | 2009-08-24 16:23 | 2009-08-24 17:49 | 1 | 85.767 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Servicman driving. Will call back for outage info. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 778314 | CPCC | CPCC644072 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_304400_524160653 | 2010 | Before | 2010-07-15 18:36 | 2010-07-15 23:27 | 1 | 291.033 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Riding lawn mowere hit guy wire and damaged o/h secondary service. Crew made repairs | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 775234 | CPCC | CPCC631000 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_354800_237790104 | 2010 | Before | 2010-04-28 15:26 | 2010-04-28 17:34 | 1 | 128.5 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: bad connection at wetherhead and transformer | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 768565 | CPCC | CPCC603279 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_354103_237790122 | 2009 | Before | 2009-12-06 16:04 | 2009-12-06 19:15 | 1 | 190.733 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Replaced bad order xfmr fuse. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 767427 | CPCC | CPCC623342 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_176103_467110042 | 2010 | Before | 2010-03-26 09:51 | 2010-03-26 14:39 | 10 | 2875.667 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | CONSTRUCTION |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: WO# 5402376, moving pole and riser. Crew had planned outage yesterday but job not completed (equipment needed). Crew got equipment and is finishing job today. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.4537 | 46.1722
5A93 | 767469 | CPCC | CPCC615957 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_259800_712540529 | 2010 | Before | 2010-01-25 09:25 | 2010-01-25 10:14 | 1 | 49.45 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: left message on cell. Serviceman found a deteriorated xfmr fuse and replaced it. Customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 772389 | CPCC | CPCC636056 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_245501_712540470 | 2010 | Before | 2010-05-20 18:08 | 2010-05-20 19:17 | 3 | 207.5 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Deteriorated fuse. Refused and customers are back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 769667 | CPCC | CPCC618595 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_243601_712540455 | 2010 | Before | 2010-02-18 13:41 | 2010-02-18 15:45 | 1 | 124.467 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: B/O ug primary between pole# 243601 and padmount# 242780. Crew to make repairs. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6227 | 46.1654
5A93 | 780537 | CPCC | CPCC631032 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_354800_237790104 | 2010 | Before | 2010-04-29 08:56 | 2010-04-29 12:25 | 1 | 209.95 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Serviceman found a deteriorated secondary service. He replaced the service and all connectors. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 785168 | CPCC | CPCC639840 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_206815_524160512 | 2010 | Before | 2010-06-21 07:46 | 2010-06-21 12:15 | 1 | 268.467 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Low three phase service. Log truck had made contact with service while drving through area with a large load. No info on truck or driver. Crew to make repairs to service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 763777 | CPCC | CPCC611419 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_207900_524160504 | 2010 | Before | 2010-01-10 13:31 | 2010-01-10 17:02 | 10 | 2114.833 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: found riser fuse open, called in crew, b/o u.g. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5733 | 46.1693
5A93 | 762992 | CPCC | CPCC617767 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2010 | Before | 2010-02-10 12:16 | 2010-02-10 12:16 | 0 | 0 | 919 | 214.433 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | SPLICE B/O OH |  |  |  | PROSPER: T&R due to down primary wire caused by o/h splice failure. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1604
5A93 | 762995 | CPCC | CPCC617799 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_169101_475940214 | 2010 | Before | 2010-02-10 12:28 | 2010-02-10 15:11 | 7 | 1142.867 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | SPLICE B/O OH |  |  |  | PROSPER: Fuse blown due to down primary wire between pole# 158301 and pole# 159300 (cause: o/h splice failed). Crew made repairs. All customers back in service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5486 | 46.1735
5A93 | 763002 | CPCC | CPCC617831 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_169101_475940214 | 2010 | Before | 2010-02-10 13:49 | 2010-02-10 15:11 | 32 | 2626.133 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | B/O EQUIPMENT | SPLICE B/O OH |  |  |  | PROSPER: Crew opened other 2 fuses to make repairs to down primary wire caused by splice failure. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5486 | 46.1735
5A93 | 761922 | CPCC | CPCC610788 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_160104_475940201 | 2010 | Before | 2010-01-06 06:00 | 2010-01-06 11:01 | 1 | 301.3 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | PROSPER: B/o ug service. Crew installed service saver and will make permanent repairs at a later time. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 761182 | CPCC | CPCC610952 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_206700_524160511 | 2010 | Before | 2010-01-07 00:36 | 2010-01-07 05:21 | 17 | 4849.533 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: refer to outage #610951 for crew response times. Tree came down and tore down primary wire. crew to make repairs. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5763 | 46.1668
5A93 | 766403 | CPCC | CPCC606619 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_200500_524160550 | 2009 | Before | 2009-12-14 18:17 | 2009-12-14 21:12 | 7 | 1225.933 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: replaced cut out | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 762806 | CPCC | CPCC626492 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_176100_1580001881 | 2010 | Before | 2010-04-05 13:20 | 2010-04-05 15:43 | 11 | 1570.433 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Tree through o/h primary wire on pole# 088001. Crew made repairs to o/h primary. Customers back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.4532 | 46.1723
5A93 | 764854 | CPCC | CPCC611112 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | Line Cut-40527 | 2010 | Before | 2010-01-07 23:38 | 2010-01-07 23:51 | 920 | 11960 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: crew enroute to patrol, closed on test and holding | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1607
5A93 | 801205 | CPCC | CPCC665900 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_032205_1580021744 | 2010 | Before | 2010-11-22 16:51 | 2010-11-22 18:46 | 84 | 9709 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Blown fuse due to tree limb on primary. Crew removed branch (no distribution damage). Replaced fuse and it held. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5423 | 46.2033
5A93 | 803541 | CPCC | CPCC665373 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2010 | Before | 2010-11-19 06:01 | 2010-11-19 06:01 | 0 | 0 | 802 | 66.833 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: trip and reclose bad jumper on fuse pole | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1604
5A93 | 803542 | CPCC | CPCC665375 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_167201_475940213 | 2010 | Before | 2010-11-19 06:26 | 2010-11-19 08:00 | 1 | 94.45 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Bad connectivity in cadops. Associate to outage# 665364. Blown line fuse and open jumper due to primary wire down caused by a tree limb. Crew made repairs. All customers back in service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 799676 | CPCC | CPCC668810 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_169101_475940214 | 2010 | Before | 2010-12-08 02:36 | 2010-12-08 06:41 | 39 | 9558.9 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: tree through wire, crew to make repairs | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5486 | 46.1735
5A93 | 800100 | CPCC | CPCC665068 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_300601_524160631 | 2010 | Before | 2010-11-17 12:09 | 2010-11-17 13:27 | 3 | 233.55 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Deteriorated x-fmr fuse. Serviceman replaced fuse and it held. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 802477 | CPCC | CPCC655482 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_192702_524160452 | 2010 | Before | 2010-09-20 10:35 | 2010-09-20 13:10 | 1 | 154.55 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: B/O o/h service neutral. Serviceman made repairs. Customer back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 803288 | CPCC | CPCC665362 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2010 | Before | 2010-11-19 04:04 | 2010-11-19 04:04 | 0 | 0 | 927 | 108.15 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: trip and reclose bad jumper on fuse pole | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1604
5A93 | 803289 | CPCC | CPCC665364 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_201804_524160515 | 2010 | Before | 2010-11-19 04:10 | 2010-11-19 08:37 | 125 | 28911.233 | 0 | 0 | 2 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Blown line fuse and open jumper due to primary wire down caused by a tree limb. Crew made repairs. All customers back in service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5862 | 46.1679
5A93 | 803290 | CPCC | CPCC665365 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_176180_524160326 | 2010 | Before | 2010-11-19 04:22 | 2010-11-19 08:00 | 1 | 217.85 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Bad connectivity in cadops. Associate to outage# 665364. Blown line fuse and open jumper due to primary wire down caused by a tree limb. Crew made repairs. All customers back in service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 803740 | CPCC | CPCC662565 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_022000_475940270 | 2010 | Before | 2010-11-01 10:14 | 2010-11-01 15:22 | 9 | 2773.35 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: crew located and repaired OH Primary Wire due to tree thru line, outage restored | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5213 | 46.2005
5A93 | 803807 | CPCC | CPCC665421 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_174280_524160367 | 2010 | Before | 2010-11-19 11:09 | 2010-11-19 11:47 | 4 | 153 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman replaced blown x-fmr fuse (no cause found). Customers back in service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 798392 | CPCC | CPCC656376 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_109500_475940295 | 2010 | Before | 2010-09-27 12:59 | 2010-09-27 17:16 | 2 | 514.2 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | PROSPER: crew located open transformer fuse, investigating for cause/damage, crew located OH primary wire resting on pole due to failed insulator top tie, crew making repairs(14:14), crew also replacing B/O OH Transformer | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 798401 | CPCC | CPCC656407 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | Line Cut-45669 | 2010 | Before | 2010-09-27 16:19 | 2010-09-27 16:43 | 273 | 6388.2 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | PROSPER: crew had hold on FR# 5A93B, possibly replace B/O OH transformer and tied down floating Primary conductor, FR opened while refusing suspected B/O transformer W/3amp fuse, crew was in the clear, MADS/PPE's observed. no damage or injuries. outage restored | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5846 | 46.1701
5A93 | 794512 | CPCC | CPCC661559 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_355701_237790117 | 2010 | Before | 2010-10-25 08:22 | 2010-10-25 15:20 | 1 | 418.4 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | PROSPER: left message(08:36). serviceman located B/O OH transformer & faulted UG secondary cable, transformer replaced, service saver installed, outage restored, cable to replaced at later date. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 810234 | CPCC | CPCC669845 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_022000_475940270 | 2010 | Before | 2010-12-13 04:00 | 2010-12-13 07:51 | 9 | 2079.6 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Crew made repairs to the overhead primary that was taken down by a tree, customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5213 | 46.2005
5A93 | 811041 | CPCC | CPCC675265 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_206401_524160592 | 2011 | Before | 2011-01-11 17:34 | 2011-01-11 19:01 | 1 | 86.867 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman arrived found open cutout fuse. Investigated and determined deteriorated fuse. Outage restored. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 808449 | CPCC | CPCC697824 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_191703_524160453 | 2011 | Before | 2011-03-23 08:14 | 2011-03-23 09:31 | 2 | 153.367 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman replaced deteriorated x-fmr fuse. Customer back in service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 805802 | CPCC | CPCC671081 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | Line Cut-47096 | 2010 | Before | 2010-12-18 02:00 | 2010-12-18 06:07 | 13 | 3208.4 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Wire down burning on ground. Blown line fuse. Cause was tree limb. Repairs made. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5868 | 46.1673
5A93 | 805804 | CPCC | CPCC671084 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | RC_201800_1580471910 | 2010 | Before | 2010-12-18 02:09 | 2010-12-18 06:07 | 117 | 27826.5 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | TREES | TREE - NON-PREVENTABLE | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Took emergency outage, wire down burning on ground. repaired conductor. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5868 | 46.1674
5A93 | 805812 | CPCC | CPCC671103 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_248602_712540487 | 2010 | Before | 2010-12-18 05:37 | 2010-12-18 08:35 | 91 | 16179.8 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: tree thru line. Crew made repairs | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6117 | 46.1652
5A93 | 805815 | CPCC | CPCC671115 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_023500_475940276 | 2010 | Before | 2010-12-18 01:23 | 2010-12-18 12:07 | 25 | 14138.1 | 0 | 0 | 2 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Crew needed to make repairs to the overhead primary that was taken down by a tree. Customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.52 | 46.2069
5A93 | 787868 | CPCC | CPCC662722 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2010 | Before | 2010-11-02 01:36 | 2010-11-02 01:36 | 0 | 0 | 926 | 216.067 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: T and R. Tree through primary. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1604
5A93 | 787869 | CPCC | CPCC662723 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2010 | Before | 2010-11-02 01:38 | 2010-11-02 01:38 | 0 | 0 | 926 | 246.933 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: T and R. Tree through primary. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1604
5A93 | 787871 | CPCC | CPCC662730 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_173802_524160344 | 2010 | Before | 2010-11-02 01:46 | 2010-11-02 06:21 | 122 | 33543.9 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Blown line fuse. Tree through primary, crew needed. Repairs made and customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5816 | 46.1831
5A93 | 787872 | CPCC | CPCC662735 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_173802_524160344 | 2010 | Before | 2010-11-02 05:00 | 2010-11-02 06:21 | 36 | 2920.8 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | TREES | TREE - NON-PREVENTABLE | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Crew took emergency outage to make repairs. See outage 662730 for the original outage. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5816 | 46.1831
5A93 | 785948 | CPCC | CPCC639927 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_259801_712540528 | 2010 | Before | 2010-06-21 18:49 | 2010-06-21 20:17 | 1 | 87.233 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: bad fuse | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 788406 | CPCC | CPCC662799 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_293701_524160612 | 2010 | Before | 2010-11-02 16:46 | 2010-11-02 18:08 | 1 | 82.283 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: dispatch IVR callback confirms customer has checked breakers, has no power . Replaced deteriorated xfmr fuse | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 789632 | CPCC | CPCC651770 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_109502_1580128764 | 2010 | Before | 2010-08-26 17:19 | 2010-08-26 19:58 | 14 | 2220.867 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Patroled line, no cause found. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5282 | 46.1925
5A93 | 828225 | CPCC | CPCC706269 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_150602_475940249 | 2011 | Before | 2011-05-22 11:03 | 2011-05-22 14:14 | 1 | 190.967 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: bad cut-out to tranformer, cut-out replaced, power restored. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 824888 | CPCC | CPCC709157 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2011 | Before | 2011-06-18 07:16 | 2011-06-18 07:16 | 0 | 0 | 929 | 77.417 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1604
5A93 | 823825 | CPCC | CPCC708869 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_206301_524160593 | 2011 | Before | 2011-06-17 08:27 | 2011-06-17 10:57 | 1 | 150.017 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Serviceman found an secondary service on the ground (cause unknown). Serviceman put service back up. Customer back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 831298 | CPCC | CPCC706579 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | Line Cut-50100 | 2011 | Before | 2011-05-25 17:26 | 2011-05-25 17:33 | 929 | 6642.35 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF FEED FROM SUPPLIER |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Loss of feed from supplier (BPA). Grid switched customers back in service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1607
5A93 | 834203 | CPCC | CPCC716005 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_178080_524160418 | 2011 | Before | 2011-08-03 11:56 | 2011-08-03 13:50 | 1 | 114.15 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: Serviceman on another job, will go here next. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 816738 | CPCC | CPCC670861 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_034903_475940334 | 2010 | Before | 2010-12-16 16:04 | 2010-12-16 22:52 | 28 | 11418.4 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | POLE OH |  |  |  | PROSPER: Car hit pole, pole down and line fuse blown. Repairs made, customer power restored. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.538 | 46.213
5A93 | 816739 | CPCC | CPCC670865 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_032205_1580021744 | 2010 | Before | 2010-12-16 19:04 | 2010-12-16 22:52 | 85 | 19324.75 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | POLE OH |  |  |  | PROSPER: Took emergency outage to make repairs to car hit pole. See outage 670861. Repairs made, customer power restored. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5423 | 46.2033
5A93 | 816493 | CPCC | CPCC679705 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_206806_524160492 | 2011 | Before | 2011-02-13 01:35 | 2011-02-13 09:49 | 35 | 17285.917 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: Crew needed to make repairs to the B/O underground primary. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.577 | 46.1685
5A93 | 811754 | CPCC | CPCC686644 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_167402_475940240 | 2011 | Before | 2011-03-03 05:32 | 2011-03-03 06:43 | 2 | 141.533 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Blown transformer fuse. Bad transformer fuse. Refused and customers are back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5A93 | 815419 | CPCC | CPCC679417 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2011 | Before | 2011-02-12 16:31 | 2011-02-12 16:31 | 0 | 0 | 929 | 77.417 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: feeder operation | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1604
5A93 | 815421 | CPCC | CPCC679430 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_194702_1580489220 | 2011 | Before | 2011-02-12 16:24 | 2011-02-13 00:07 | 760 | 351740.667 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Per GF serviceman located tree thru OH Primary, crew on site making repairs(10:48) Fuse opened at 22:15, remodel in CAAD OPS when outage completed | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.5992 | 46.1671
5A93 | 857993 | CPCC | CPCC729362 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_169101_475940214 | 2011 | Before | 2011-11-11 14:14 | 2011-11-11 16:26 | 39 | 5162.313 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Open line line fuse (no cause found). Serviceman replaced fuse and it held. Serviceman realized afterwards that B phase fuse was blown also (but door didnt open). So please add 5 customers to the total customer count for this outage. | DISTRIBUTION | DEVICE | AUTO | 2011-11-11 18:15 | COMPLETED |  | 2011-11-11 15:07 | 2011-11-28 14:56 | 2011-11-11 17:33 | -123.5486 | 46.1735
5A93 | 860700 | CPCC | CPCC731155 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_248602_712540487 | 2011 | Before | 2011-11-22 04:12 | 2011-11-22 07:12 | 91 | 16375.45 | 0 | 0 | 1 | Y | N | N | N | Y | 2011-11-22 to 2011-11-23 OR Clatsop | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Crew arrived and found open line fuses will patrol and report. Found wire down remainder of the crew enroute. Crew made repairs. All customers back in service. | DISTRIBUTION | DEVICE | AUTO | 2011-11-22 07:15 | COMPLETED |  | 2011-11-22 04:14 | 2011-11-22 07:12 | 2011-11-22 12:31 | -123.6117 | 46.1652
5A93 | 861239 | CPCC | CPCC732551 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_206700_524160511 | 2011 | Before | 2011-11-23 02:15 | 2011-11-23 10:09 | 18 | 8541.6 | 0 | 0 | 1 | Y | N | N | N | Y | 2011-11-22 to 2011-11-23 OR Clatsop | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Crew needed to make repairs to the overhead primary and strighten a pole that was damaged by a tree. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2011-11-23 06:58 | 2011-11-23 10:09 | 2011-11-23 12:16 | -123.5763 | 46.1668
5A93 | 857219 | CPCC | CPCC728888 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_360600_237790128 | 2011 | Before | 2011-11-07 17:18 | 2011-11-07 22:53 | 1 | 334.55 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | SOURCE: Serviceman arrived and found B/o xfrmr, need crew. Made repairs outage restored | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2011-11-07 23:30 | COMPLETED |  | 2011-11-07 17:18 | 2011-11-07 22:53 | 2011-11-08 08:29 | -123.5061 | 46.2218
5A93 | 847464 | CPCC | CPCC724332 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_206700_524160511 | 2011 | Before | 2011-10-04 20:57 | 2011-10-05 00:27 | 13 | 2726.75 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Crew needed, Crew arrived and removed tree from line replaced blown line fuse outage restored. | DISTRIBUTION | DEVICE | AUTO | 2011-10-04 23:30 | COMPLETED |  | 2011-10-04 20:57 | 2011-10-11 11:47 | 2011-10-05 05:09 | -123.5763 | 46.1668
5A93 | 844653 | CPCC | CPCC717999 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_206806_524160492 | 2011 | Before | 2011-08-20 01:04 | 2011-08-20 08:33 | 35 | 15723.167 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: the crew is making repairs to bad order undground cable . Repairs made and customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.577 | 46.1685
5A93 | 851326 | CPCC | CPCC726273 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_293300_524160604 | 2011 | Before | 2011-10-20 09:30 | 2011-10-20 10:29 | 1 | 59.017 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman replaced deteriorated x-fmr fuse. Customer back in service. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2011-10-20 12:30 | COMPLETED |  | 2011-10-20 09:30 | 2011-10-20 10:29 | 2011-10-20 14:54 | -123.5829 | 46.1477
5A93 | 859294 | CPCC | CPCC730284 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_159300_475940191 | 2011 | Before | 2011-11-16 22:57 | 2011-11-17 01:36 | 1 | 158.633 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Tree through primary, crew needed. Repairs made and customer is back on. | DISTRIBUTION | DEVICE | MANUAL | 2011-11-17 03:00 | COMPLETED |  | 2011-11-16 22:57 | 2011-11-17 01:36 | 2011-11-17 01:44 | -123.5282 | 46.1764
5A93 | 858992 | CPCC | CPCC730033 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_244501_712540469 | 2011 | Before | 2011-11-15 09:28 | 2011-11-15 11:57 | 1 | 148.467 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: B/O x-fmr fuse. Crew replaced fuse. Customer back in full service. | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2011-11-15 13:45 | COMPLETED |  | 2011-11-15 09:28 | 2011-11-15 11:57 | 2011-11-15 15:48 | -123.6195 | 46.1636
5A93 | 861129 | CPCC | CPCC731684 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_201900_524160521 | 2011 | Before | 2011-11-22 12:09 | 2011-11-23 04:14 | 19 | 12763.266 | 0 | 0 | 2 | Y | N | N | N | Y | 2011-11-22 to 2011-11-23 OR Clatsop | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Open dip fuse due to b/o ug primary. Crew onsite making repairs. Temp repairs complete, over ground in conduit. | DISTRIBUTION | DEVICE | MANUAL | 2011-11-23 07:15 | COMPLETED |  | 2011-11-22 12:10 | 2011-11-23 04:14 | 2011-11-23 06:06 | -123.5868 | 46.169
5A93 | 861132 | CPCC | CPCC732148 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2011 | Before | 2011-11-22 22:14 | 2011-11-23 00:09 | 923 | 106052.7 | 0 | 0 | 1 | Y | N | N | N | Y | 2011-11-22 to 2011-11-23 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: T&R | DISTRIBUTION | DEVICE | AUTO | 2011-11-23 01:45 | COMPLETED |  | 2011-11-22 22:35 | 2011-11-23 00:10 | 2011-11-23 06:06 | -123.6231 | 46.1604
5A93 | 861230 | CPCC | CPCC732838 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2011 | Before | 2011-11-23 11:35 | 2011-11-23 11:35 | 0 | 0 | 934 | 77.833 | 1 | Y | N | N | N | Y | 2011-11-22 to 2011-11-23 OR Clatsop | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: T & R. Winter storm | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2011-11-23 11:35 | 2011-11-23 11:35 | 2011-11-23 12:12 | -123.6231 | 46.1604
5A93 | 840064 | CPCC | CPCC723432 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_291580_524160331 | 2011 | Before | 2011-09-26 16:21 | 2011-09-26 22:40 | 1 | 379.217 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: crew repaired wire down. Unsure of details, crew did not call in when complete, area manager sent details atf | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-10-12 16:15 | 2011-09-28 10:10
5A93 | 839493 | CPCC | CPCC723332 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | Line Cut-52243 | 2011 | Before | 2011-09-26 10:28 | 2011-09-26 12:49 | 24 | 3373.6 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Blown line fuse due to primary wire down caused by a tree. Crew made repairs. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.4751 | 46.1697
5A93 | 839869 | CPCC | CPCC723409 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | Line Cut-52254 | 2011 | Before | 2011-09-26 14:46 | 2011-09-26 14:47 | 0 | 0 | 929 | 944.483 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Sub de-energized due to loss of transmission. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -123.6231 | 46.1607
5A93 | 880926 | CPCC | CPCC746638 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_195900_1580528843 | 2012 | Before | 2012-02-07 13:51 | 2012-02-07 14:03 | 24 | 304.4 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | TREES | TREE - NON-PREVENTABLE | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Crew took an outage to remove a tree from o/h primary. | DISTRIBUTION | DEVICE | MANUAL | 2012-02-07 14:58 | COMPLETED |  | 2012-02-07 13:51 | 2012-02-08 14:42 | 2012-02-07 16:01 | -123.475 | 46.1698
5A93 | 875268 | CPCC | CPCC740617 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_211901_1580419438 | 2012 | Before | 2012-01-18 05:52 | 2012-01-18 16:59 | 100 | 64061.433 | 0 | 0 | 2 | Y | N | N | N | Y | 2012-01-17 to 2012-01-21 OR CoastPlus | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman found open line fuses. tree thru line, pole leaning. crew made repairs. | DISTRIBUTION | DEVICE | MANUAL | 2012-01-18 18:15 | COMPLETED |  | 2012-01-18 06:09 | 2012-01-18 16:59 | 2012-01-18 19:17 | -123.5662 | 46.1699
5A93 | 875271 | CPCC | CPCC740595 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2012 | Before | 2012-01-18 05:48 | 2012-01-18 05:49 | 0 | 0 | 777 | 258.741 | 1 | Y | N | N | N | Y | 2012-01-17 to 2012-01-21 OR CoastPlus | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: T&R Due to tree through primary PROSPER: customer count reduced due to customers already out on 740667 | DISTRIBUTION | DEVICE | AUTO | 2012-01-18 09:00 | COMPLETED |  | 2012-01-18 05:48 | 2012-01-30 10:56 | 2012-01-18 19:17 | -123.6231 | 46.1604
5A93 | 870545 | CPCC | CPCC737247 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2011 | Before | 2011-12-27 19:23 | 2011-12-27 23:07 | 934 | 171531.767 | 0 | 0 | 3 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Crew patroled line & opened FR's 5A93 a&b, tested from sub, it held for about 3 mins then tripped out again, thats when they found tree branch. Will do a quick patrol behind FR's and cloes them in. | DISTRIBUTION | DEVICE | MANUAL | 2011-12-28 01:00 | COMPLETED |  | 2011-12-27 19:23 | 2011-12-27 23:07 | 2011-12-27 23:22 | -123.6231 | 46.1604
5A93 | 867293 | CPCC | CPCC734806 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_207980_524160502 | 2011 | Before | 2011-12-08 19:20 | 2011-12-08 21:52 | 1 | 151.717 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | SOURCE: created a FLD # 5615538 to fix open secondary neutral tomorrow at customer's request. | DISTRIBUTION | CUSTOMER | AUTO | 2011-12-08 22:30 | COMPLETED |  | 2011-12-08 19:20 | 2011-12-08 21:52 | 2011-12-09 02:32 | -123.5738 | 46.1701
5A93 | 879383 | CPCC | CPCC745452 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_290780_524160664 | 2012 | Before | 2012-01-29 15:25 | 2012-01-29 20:51 | 1 | 325.867 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | SOURCE: bad sec ug, crew to make repairs. repairs complete. | DISTRIBUTION | CUSTOMER | AUTO | 2012-01-29 18:30 | COMPLETED |  | 2012-01-29 15:25 | 2012-01-29 20:51 | 2012-01-29 23:10 | -123.5893 | 46.1524
5A93 | 869286 | CPCC | CPCC736112 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_170000_524160401 | 2011 | Before | 2011-12-19 12:01 | 2011-12-19 15:21 | 1 | 200.033 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | SOURCE: B/O x-fmr. Crew replaced. Customer back in service. | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2011-12-19 17:00 | COMPLETED |  | 2011-12-19 12:01 | 2011-12-19 15:21 | 2011-12-19 15:31 | -123.5881 | 46.1716
5A93 | 870540 | CPCC | CPCC737246 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2011 | Before | 2011-12-27 19:23 | 2011-12-27 19:23 | 0 | 0 | 934 | 77.833 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: T&R | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2011-12-27 19:23 | 2011-12-27 19:23 | 2011-12-27 22:42 | -123.6231 | 46.1604
5A93 | 875269 | CPCC | CPCC740627 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_173802_524160344 | 2012 | Before | 2012-01-18 05:13 | 2012-01-18 13:17 | 35 | 16924.833 | 0 | 0 | 1 | Y | N | N | N | Y | 2012-01-17 to 2012-01-21 OR CoastPlus | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Blown line fuse. Due to tree through primary. | DISTRIBUTION | DEVICE | AUTO | 2012-01-18 09:15 | COMPLETED |  | 2012-01-18 06:16 | 2012-01-18 13:17 | 2012-01-18 19:17 | -123.5816 | 46.1831
5A93 | 871298 | CPCC | CPCC738251 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_109502_1580128764 | 2011 | Before | 2011-12-30 15:10 | 2011-12-30 16:30 | 14 | 1114.167 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman found open line fuse. He is patrolling for cause. Serviceman found some branches that had fallen on the line but had cleared themselves. Serviceman replaced fuse and it held. | DISTRIBUTION | DEVICE | AUTO | 2011-12-30 18:15 | COMPLETED |  | 2011-12-30 15:10 | 2011-12-30 16:30 | 2011-12-30 16:31 | -123.5282 | 46.1925
5A93 | 871638 | CPCC | CPCC738348 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_172002_524160388 | 2011 | Before | 2011-12-31 20:14 | 2011-12-31 21:40 | 1 | 86.233 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Fuse blew due tree limb. Refused and customer is back on. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2011-12-31 23:15 | COMPLETED |  | 2011-12-31 20:14 | 2012-01-05 12:17 | 2011-12-31 21:41 | -123.5836 | 46.1714
5A93 | 871948 | CPCC | CPCC738579 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_203700_524160539 | 2012 | Before | 2012-01-03 07:09 | 2012-01-03 07:31 | 1 | 21.817 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Customer called in a no power to serviceman and he responded. He found blown x-fmr fuse on pole# 203700. Cause was a b/o cut-out. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-01-03 10:15 | COMPLETED |  | 2012-01-03 07:09 | 2012-01-03 07:31 | 2012-01-03 10:41 | -123.583 | 46.1675
5A93 | 866128 | CPCC | CPCC734254 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_343103_237790099 | 2011 | Before | 2011-12-04 14:10 | 2011-12-04 19:27 | 1 | 317.283 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | SOURCE: Bad order transformer, crew needed. | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2011-12-04 20:45 | COMPLETED |  | 2011-12-04 14:10 | 2011-12-04 19:27 | 2011-12-04 19:31 | -123.5399 | 46.2161
5A93 | 881056 | CPCC | CPCC746686 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | Line Cut-57840 | 2012 | Before | 2012-02-08 09:44 | 2012-02-08 10:17 | 935 | 30855 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF FEED FROM SUPPLIER |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Loss of feed from supplier (BPA 115 line) | DISTRIBUTION | DEVICE | AUTO | 2012-02-08 13:00 | COMPLETED |  | 2012-02-08 09:49 | 2012-02-08 10:24 | 2012-02-08 12:56 | -123.6231 | 46.1607
5A93 | 874234 | CPCC | CPCC739851 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_362600_237790131 | 2012 | Before | 2012-01-15 12:53 | 2012-01-15 17:16 | 1 | 263.317 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Tree limb tore down service | DISTRIBUTION | CUSTOMER | AUTO | 2012-01-15 16:00 | COMPLETED |  | 2012-01-15 12:53 | 2012-01-15 17:16 | 2012-01-15 18:51 | -123.5008 | 46.2217
5A93 | 870537 | CPCC | CPCC737262 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2011 | Before | 2011-12-27 22:00 | 2011-12-27 22:32 | 526 | 16630.367 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: T&R tree branch | DISTRIBUTION | DEVICE | AUTO | 2011-12-28 01:00 | COMPLETED |  | 2011-12-27 22:00 | 2011-12-27 22:32 | 2011-12-27 22:42 | -123.6231 | 46.1604
5A93 | 875270 | CPCC | CPCC740667 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_173802_524160344 | 2012 | Before | 2012-01-18 05:34 | 2012-01-18 13:17 | 123 | 56973.5 | 0 | 0 | 2 | Y | N | N | N | Y | 2012-01-17 to 2012-01-21 OR CoastPlus | PLANNED | EMERGENCY DAMAGE REPAIR | TREES | TREE - NON-PREVENTABLE | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Crew opened other two phases (associated to outage# 740627). | DISTRIBUTION | DEVICE | AUTO | 2012-01-18 09:45 | COMPLETED |  | 2012-01-18 06:34 | 2012-01-18 13:17 | 2012-01-18 19:17 | -123.5816 | 46.1831
5A93 | 875272 | CPCC | CPCC740576 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2012 | Before | 2012-01-18 05:03 | 2012-01-18 05:03 | 0 | 0 | 935 | 218.167 | 1 | Y | N | N | N | Y | 2012-01-17 to 2012-01-21 OR CoastPlus | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: T&R Due to tree through primary | DISTRIBUTION | DEVICE | AUTO | 2012-01-18 08:15 | COMPLETED |  | 2012-01-18 05:03 | 2012-01-18 05:03 | 2012-01-18 19:19 | -123.6231 | 46.1604
5A93 | 877554 | CPCC | CPCC744156 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_171500_524160352 | 2012 | Before | 2012-01-22 09:56 | 2012-01-22 10:46 | 2 | 100 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: branch blew transformer fuse | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-01-22 13:00 | COMPLETED |  | 2012-01-22 09:56 | 2012-01-22 10:46 | 2012-01-22 10:50 | -123.5854 | 46.1783
5A93 | 885523 | CPCC | CPCC750046 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_109502_1580128764 | 2012 | Before | 2012-02-25 05:15 | 2012-02-25 08:12 | 14 | 2473.333 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: found stranded point in line made repairs closed on test outage restored. | DISTRIBUTION | DEVICE | AUTO | 2012-02-25 08:45 | COMPLETED |  | 2012-02-25 05:32 | 2012-02-25 08:12 | 2012-02-25 11:30 | -123.5282 | 46.1925
5A93 | 885525 | CPCC | CPCC750064 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_029100_475940163 | 2012 | Before | 2012-02-25 07:30 | 2012-02-25 08:22 | 1 | 52.5 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: tree limb on xfrmr, will clear and close on test.Power restored | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-02-25 10:30 | COMPLETED |  | 2012-02-25 07:30 | 2012-02-25 08:22 | 2012-02-25 11:30 | -123.5083 | 46.2006
5A93 | 905393 | CPCC | CPCC769165 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2012 | Before | 2012-05-11 10:35 | 2012-05-11 10:35 | 0 | 0 | 935 | 77.917 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: T&R | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-05-11 10:35 | 2012-05-11 10:35 | 2012-05-11 11:05 | -123.6231 | 46.1604
5A93 | 888770 | CPCC | CPCC752843 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_168201_475940227 | 2012 | Before | 2012-03-10 07:28 | 2012-03-10 13:58 | 4 | 1003.383 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Serviceman arrived and found blown dip fuse, will test cable and report. isolated bad section and closed fuse to energize the rest of the customers, will make repairs and report. repairs made | DISTRIBUTION | DEVICE | AUTO | 2012-03-10 10:30 | COMPLETED |  | 2012-03-10 07:28 | 2012-03-10 13:58 | 2012-03-10 15:40 | -123.5518 | 46.1747
5A93 | 899305 | CPCC | CPCC765148 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_259300_1580247858 | 2012 | Before | 2012-04-13 14:56 | 2012-04-13 16:18 | 41 | 3332.617 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman found open line fuse. Serviceman patrolled and found no cause. Replaced fuse and it held. | DISTRIBUTION | DEVICE | AUTO | 2012-04-13 18:30 | COMPLETED |  | 2012-04-13 15:27 | 2012-04-13 16:18 | 2012-04-13 16:30 | -123.6091 | 46.1465
5A93 | 900023 | CPCC | CPCC765773 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_146400_475940359 | 2012 | Before | 2012-04-17 14:24 | 2012-04-17 15:51 | 1 | 86.617 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: serviceman states that the cutout door he tried to install did not fit, he talked to the customer and customer is ok with fixing the problem tomorrow, serviceman to repair tomorrow, | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-04-17 17:30 | COMPLETED |  | 2012-04-17 14:24 | 2012-04-17 15:51 | 2012-04-17 17:40 | -123.5147 | 46.1767
5A93 | 888779 | CPCC | CPCC752816 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2012 | Before | 2012-03-10 03:33 | 2012-03-10 03:34 | 0 | 0 | 935 | 358.417 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: TNR , B/O UG | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-03-10 03:33 | 2012-04-02 09:21 | 2012-03-10 15:50 | -123.6231 | 46.1604
5A93 | 911422 | CPCC | CPCC772540 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | Line Cut-63151 | 2012 | Before | 2012-06-04 20:21 | 2012-06-04 20:34 | 937 | 12212.233 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Loss of Transmission. | DISTRIBUTION | DEVICE | AUTO | 2012-06-04 23:30 | COMPLETED |  | 2012-06-04 20:22 | 2012-06-11 13:40 | 2012-06-04 21:12 | -123.6231 | 46.1607
5A93 | 916335 | CPCC | CPCC775058 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_109502_1580128764 | 2012 | Before | 2012-06-23 05:40 | 2012-06-23 10:31 | 14 | 4075.167 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Tree through line, crew needed Crew made repairs and restored power | DISTRIBUTION | DEVICE | AUTO | 2012-06-23 09:00 | COMPLETED |  | 2012-06-23 05:53 | 2012-06-23 10:31 | 2012-06-23 13:46 | -123.5282 | 46.1925
5A93 | 919267 | CPCC | CPCC776576 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_166480_475940238 | 2012 | Before | 2012-07-04 17:09 | 2012-07-04 20:50 | 1 | 220.617 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | SOURCE: bad ug sec, crew installed service saver | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-07-04 20:15 | COMPLETED |  | 2012-07-04 17:09 | 2012-07-04 20:50 | 2012-07-05 00:01 | -123.5567 | 46.1764
5A93 | 914507 | CPCC | CPCC774057 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_174000_467110041 | 2012 | Before | 2012-06-16 14:30 | 2012-06-16 19:32 | 11 | 3323.837 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: crew to make repairs. Bad modeling in cadops. Actual customer count is 11 for total time. | DISTRIBUTION | DEVICE | MANUAL | 2012-06-16 19:45 | COMPLETED |  | 2012-06-16 14:40 | 2012-06-20 16:14 | 2012-06-17 02:03 | -123.4561 | 46.171
5A93 | 1302661 | CPCC | CPCC785063 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_176100_1580001881 | 2012 | Before | 2012-08-19 15:33 | 2012-08-19 19:18 | 11 | 2472.983 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman arrived and found open line fuse will patrol and report. Serviceman found branch on line, needs 2 man crew. Crew arrived. | DISTRIBUTION | DEVICE | MANUAL | 2012-08-19 20:45 | COMPLETED |  | 2012-08-19 15:33 | 2012-08-19 19:18 | 2012-08-19 19:20 | -123.4532 | 46.1723
5A93 | 1295836 | CPCC | CPCC784463 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_167080_475940222 | 2012 | Before | 2012-08-15 12:35 | 2012-08-15 16:19 | 1 | 224.25 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | SOURCE: Crew installed service saver due to the B/O underground secondary service. | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2012-08-15 17:00 | COMPLETED |  | 2012-08-15 12:35 | 2012-08-20 13:54 | 2012-08-15 16:26 | -123.5531 | 46.1714
5A93 | 1325232 | CPCC | CPCC798260 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2012 | Before | 2012-11-19 10:37 | 2012-11-19 13:22 | 935 | 154602.25 | 0 | 0 | 1 | Y | N | N | N | Y | 11-19-2012 to 11-20-2012 OR CoastPlus | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: CB Locked out. tree through primary | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-11-19 10:37 | 2012-11-19 13:22 | 2012-11-19 23:00 | -123.6231 | 46.1604
5A93 | 1325440 | CPCC | CPCC798679 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_169101_475940214 | 2012 | Before | 2012-11-19 13:51 | 2012-11-20 00:58 | 39 | 25986.35 | 0 | 0 | 1 | Y | N | N | N | Y | 11-19-2012 to 11-20-2012 OR CoastPlus | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Blown line fuse due to tree through the line at pole 152001. Repairs made will close on test. Repairs made and customers are back on. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-11-19 13:51 | 2012-11-20 00:58 | 2012-11-20 02:29 | -123.5486 | 46.1735
5A93 | 1325982 | CPCC | CPCC799620 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_022000_475940270 | 2012 | Before | 2012-11-20 07:02 | 2012-11-20 16:56 | 9 | 5348.85 | 0 | 0 | 1 | Y | N | N | N | Y | 11-19-2012 to 11-20-2012 OR CoastPlus | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: crew complete, customers are back inservice | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-11-20 07:02 | 2012-11-26 14:07 | 2012-11-20 18:52 | -123.5213 | 46.2005
5A93 | 1329340 | CPCC | CPCC802801 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_307600_524160669 | 2012 | Before | 2012-12-04 00:27 | 2012-12-04 05:54 | 12 | 3922.6 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman reports down phase, crew made repairs, power restored | DISTRIBUTION | DEVICE | MANUAL | 2012-12-04 07:00 | COMPLETED |  | 2012-12-04 00:27 | 2012-12-06 14:44 | 2012-12-04 06:05 | -123.5922 | 46.1508
5A93 | 1328295 | CPCC | CPCC802038 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_109502_1580128764 | 2012 | Before | 2012-11-30 18:14 | 2012-11-30 20:30 | 14 | 1904.933 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman found line fuse open at pole 109502, patrolled line found no cause, closed for test, it held power restored | DISTRIBUTION | DEVICE | AUTO | 2012-11-30 21:15 | COMPLETED |  | 2012-11-30 18:14 | 2012-12-03 13:29 | 2012-11-30 22:16 | -123.5282 | 46.1925
5A93 | 1324206 | CPCC | CPCC797032 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_173802_524160344 | 2012 | Before | 2012-11-16 17:54 | 2012-11-17 00:45 | 158 | 64964.333 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | POLE OH |  |  |  | SOURCE: Serviceman arrived and found broken pole and wire down, needs 4 man crew and 2 flaggers. Crew made repairs and will close fuses in and report. Fuses in and holding. | DISTRIBUTION | DEVICE | MANUAL | 2012-11-17 03:00 | COMPLETED |  | 2012-11-16 17:58 | 2012-11-17 00:45 | 2012-11-17 02:45 | -123.5816 | 46.1831
5A93 | 1311035 | CPCC | CPCC788970 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_204802_524160532 | 2012 | Before | 2012-09-24 16:50 | 2012-09-24 20:13 | 7 | 1422.633 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Serviceman arrived and found b/o cutout. Replaced cut out and it held | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2012-09-24 22:00 | COMPLETED |  | 2012-09-24 16:50 | 2012-09-24 20:13 | 2012-09-24 20:45 | -123.5811 | 46.1686
5A93 | 1325462 | CPCC | CPCC799106 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_032205_1580021744 | 2012 | Before | 2012-11-19 07:58 | 2012-11-20 03:05 | 28 | 32128.6 | 0 | 0 | 1 | Y | N | N | N | Y | 11-19-2012 to 11-20-2012 OR CoastPlus | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Blown line fuse, wire down. Repairs made and customers are back on. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-11-19 17:28 | 2012-11-20 03:05 | 2012-11-20 03:06 | -123.5423 | 46.2033
5A93 | 1329341 | CPCC | CPCC802800 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2012 | Before | 2012-12-04 00:12 | 2012-12-04 00:12 | 0 | 0 | 940 | 78.333 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: T & R at Substation, phase wire on the ground, crews to repair | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-12-04 00:12 | 2012-12-04 00:12 | 2012-12-04 06:05 | -123.6231 | 46.1604
5A93 | 1332255 | CPCC | CPCC804615 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | Line Cut-70191 | 2012 | Before | 2012-12-16 18:35 | 2012-12-16 22:05 | 56 | 11753.448 | 0 | 0 | 1 | Y | N | N | N | Y | 2012-12-15 to 2012-12-17 OR CoastPlus | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: tree branches on lines | DISTRIBUTION | DEVICE | AUTO | 2012-12-16 22:15 | COMPLETED |  | 2012-12-16 19:10 | 2012-12-18 10:59 | 2012-12-17 00:19 | -123.5868 | 46.1674
5A93 | 1329342 | CPCC | CPCC802849 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_307600_524160669 | 2012 | Before | 2012-12-04 02:21 | 2012-12-04 05:54 | 4 | 853 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman opened fuses at pole 307600 to make repairs | DISTRIBUTION | DEVICE | MANUAL | 2012-12-04 07:30 | COMPLETED |  | 2012-12-04 02:21 | 2012-12-04 05:54 | 2012-12-04 06:05 | -123.5922 | 46.1508
5A93 | 1325223 | CPCC | CPCC797656 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2012 | Before | 2012-11-19 07:12 | 2012-11-19 07:12 | 0 | 0 | 939 | 78.25 | 1 | Y | N | N | N | Y | 11-19-2012 to 11-20-2012 OR CoastPlus | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: T&R due to tree in the line | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-11-19 07:12 | 2012-11-19 07:12 | 2012-11-19 22:58 | -123.6231 | 46.1604
5A93 | 1325534 | CPCC | CPCC799022 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_023500_475940273 | 2012 | Before | 2012-11-19 13:28 | 2012-11-20 05:39 | 31 | 30105.133 | 0 | 0 | 1 | Y | N | N | N | Y | 11-19-2012 to 11-20-2012 OR CoastPlus | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Wire down due to tree. repairs made. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-11-19 17:01 | 2012-11-20 05:39 | 2012-11-20 05:54 | -123.52 | 46.2068
5A93 | 1324210 | CPCC | CPCC797041 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_197100_524160487 | 2012 | Before | 2012-11-16 18:05 | 2012-11-16 19:40 | 1 | 95.35 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman called customer and their power is on. Saw flickering lights from T&R. | DISTRIBUTION | CUSTOMER | AUTO | 2012-11-16 21:15 | COMPLETED |  | 2012-11-16 18:05 | 2012-11-16 19:40 | 2012-11-17 02:45 | -123.5936 | 46.1578
5A93 | 1324212 | CPCC | CPCC797026 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2012 | Before | 2012-11-16 17:52 | 2012-11-16 17:52 | 0 | 0 | 939 | 219.1 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | POLE OH |  |  |  | SOURCE: T and R. from broken pole and wire down from fallin tree | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-11-16 17:52 | 2012-11-16 17:52 | 2012-11-17 02:45 | -123.6231 | 46.1604
5A93 | 1325221 | CPCC | CPCC797658 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2012 | Before | 2012-11-19 07:12 | 2012-11-19 07:12 | 0 | 0 | 939 | 78.25 | 1 | Y | N | N | N | Y | 11-19-2012 to 11-20-2012 OR CoastPlus | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: T&R due to tree in the line | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-11-19 07:12 | 2012-11-19 07:12 | 2012-11-19 22:58 | -123.6231 | 46.1604
5A93 | 1324211 | CPCC | CPCC797029 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2012 | Before | 2012-11-16 17:56 | 2012-11-16 17:57 | 0 | 0 | 781 | 181.973 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | POLE OH |  |  |  | SOURCE: T and R. from broken pole and wire down from fallin tree PROSPER: adjusted for customers already out on cpcc797032 | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-11-16 17:56 | 2012-11-27 13:34 | 2012-11-17 02:45 | -123.6231 | 46.1604
5A93 | 1325222 | CPCC | CPCC798258 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2012 | Before | 2012-11-19 10:37 | 2012-11-19 10:37 | 0 | 0 | 935 | 187 | 1 | Y | N | N | N | Y | 11-19-2012 to 11-20-2012 OR CoastPlus | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: T&R due to tree in the line | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-11-19 10:37 | 2012-11-19 10:37 | 2012-11-19 22:58 | -123.6231 | 46.1604
5A93 | 1325233 | CPCC | CPCC798919 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_206700_524160511 | 2012 | Before | 2012-11-19 14:37 | 2012-11-19 21:46 | 19 | 8164.3 | 0 | 0 | 1 | Y | N | N | N | Y | 11-19-2012 to 11-20-2012 OR CoastPlus | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: wire down | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-11-19 16:20 | 2012-11-19 21:46 | 2012-11-19 23:00 | -123.5763 | 46.1668
5A93 | 1325537 | CPCC | CPCC799562 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_248602_712540487 | 2012 | Before | 2012-11-20 04:18 | 2012-11-20 05:38 | 18 | 1441.8 | 0 | 0 | 1 | Y | N | N | N | Y | 11-19-2012 to 11-20-2012 OR CoastPlus | PLANNED | EMERGENCY DAMAGE REPAIR | TREES | TREE - NON-PREVENTABLE | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Repaired wire down. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-11-20 04:18 | 2012-11-21 09:34 | 2012-11-20 05:54 | -123.6117 | 46.1652
5A93 | 1325217 | CPCC | CPCC797671 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | RC_202904_1580471805 | 2012 | Before | 2012-11-19 07:14 | 2012-11-19 07:57 | 276 | 11909.4 | 0 | 0 | 1 | Y | N | N | N | Y | 11-19-2012 to 11-20-2012 OR CoastPlus | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Field recloser open due to limb on the line. Serviceman removed limb and closed field recloser. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-11-19 07:19 | 2012-11-19 07:57 | 2012-11-19 22:57 | -123.5845 | 46.1701
5A93 | 1325532 | CPCC | CPCC797832 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_110402_475940262 | 2012 | Before | 2012-11-19 08:04 | 2012-11-20 05:40 | 1 | 1296.317 | 0 | 0 | 1 | Y | N | N | N | Y | 11-19-2012 to 11-20-2012 OR CoastPlus | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Part of other call. wire down. repairs made. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2012-11-19 08:04 | 2012-11-20 05:40 | 2012-11-20 05:54 | -123.5253 | 46.1917
5A93 | 1325535 | CPCC | CPCC798916 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | Line Cut-68965 | 2012 | Before | 2012-11-19 09:29 | 2012-11-20 05:38 | 80 | 96773.333 | 0 | 0 | 1 | Y | N | N | N | Y | 11-19-2012 to 11-20-2012 OR CoastPlus | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Wire down, crew restored. See outage 799562. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-11-19 16:19 | 2012-11-21 09:32 | 2012-11-20 05:54 | -123.6085 | 46.1574
5A93 | 1332445 | CPCC | CPCC804455 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2012 | Before | 2012-12-16 18:23 | 2012-12-16 18:23 | 0 | 0 | 941 | 62.733 | 1 | Y | N | N | N | Y | 2012-12-15 to 2012-12-17 OR CoastPlus | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: T and R. Wind, tree through lines. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-12-16 18:23 | 2012-12-16 18:23 | 2012-12-17 04:15 | -123.6231 | 46.1604
5A93 | 1332452 | CPCC | CPCC805986 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | Line Cut-70247 | 2012 | Before | 2012-12-16 23:02 | 2012-12-17 02:39 | 81 | 17502.75 | 0 | 0 | 1 | Y | N | N | N | Y | 2012-12-15 to 2012-12-17 OR CoastPlus | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: T and R. Wind, tree through lines. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-12-16 23:02 | 2012-12-17 02:39 | 2012-12-17 04:16 | -123.5868 | 46.1674
5A93 | 1332450 | CPCC | CPCC806259 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2012 | Before | 2012-12-17 01:54 | 2012-12-17 01:54 | 0 | 0 | 859 | 71.583 | 1 | Y | N | N | N | Y | 2012-12-15 to 2012-12-17 OR CoastPlus | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: T and R. Wind, tree through lines. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-12-17 01:54 | 2012-12-17 01:54 | 2012-12-17 04:16 | -123.6231 | 46.1604
5A93 | 1332901 | CPCC | CPCC806617 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_249202_712540494 | 2012 | Before | 2012-12-17 09:26 | 2012-12-17 10:56 | 1 | 89.75 | 0 | 0 | 1 | Y | N | N | N | Y | 2012-12-15 to 2012-12-17 OR CoastPlus | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: O/H service is down due to tree. Serviceman made repairs. | DISTRIBUTION | CUSTOMER | AUTO | 2012-12-17 12:30 | COMPLETED |  | 2012-12-17 09:26 | 2012-12-17 10:56 | 2012-12-17 14:22 | -123.6105 | 46.1591
5A93 | 1333437 | CPCC | CPCC807211 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_188200_524160425 | 2012 | Before | 2012-12-18 10:05 | 2012-12-18 11:57 | 1 | 111.967 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown x-fmr fuse (no cause found), serviceman replaced fuse and it held. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-12-18 13:15 | COMPLETED |  | 2012-12-18 10:05 | 2012-12-18 11:57 | 2012-12-18 16:01 | -123.5904 | 46.1736
5A93 | 1335278 | CPCC | CPCC813142 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_171401_524160384 | 2012 | Before | 2012-12-23 12:41 | 2012-12-23 13:56 | 1 | 75.2 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown transformer fuse, fuse was bad. Refused and customer is back on. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-12-23 15:45 | COMPLETED |  | 2012-12-23 12:41 | 2012-12-23 13:56 | 2012-12-23 15:17 | -123.5855 | 46.1774
5A93 | 1332465 | CPCC | CPCC806264 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_211901_1580419438 | 2012 | Before | 2012-12-17 01:59 | 2012-12-17 04:46 | 100 | 16701.667 | 0 | 0 | 1 | Y | N | N | N | Y | 2012-12-15 to 2012-12-17 OR CoastPlus | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Blown line fuse, cause wire down. Repairs made and customers are back on. | DISTRIBUTION | DEVICE | AUTO | 2012-12-17 05:00 | COMPLETED |  | 2012-12-17 01:59 | 2012-12-17 04:46 | 2012-12-17 05:30 | -123.5662 | 46.1699
5A93 | 1336078 | CPCC | CPCC813805 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2012 | Before | 2012-12-25 07:19 | 2012-12-25 08:39 | 942 | 74779.1 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: removed tree branch from pole 245600 | DISTRIBUTION | DEVICE | AUTO | 2012-12-25 10:30 | COMPLETED |  | 2012-12-25 07:23 | 2012-12-25 08:39 | 2012-12-25 08:42 | -123.6231 | 46.1604
5A93 | 1336082 | CPCC | CPCC813802 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2012 | Before | 2012-12-25 07:09 | 2012-12-25 07:09 | 0 | 0 | 942 | 298.3 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: tree branch at pole 245600 | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-12-25 07:09 | 2012-12-25 07:09 | 2012-12-25 08:49 | -123.6231 | 46.1604
5A93 | 1332447 | CPCC | CPCC805964 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2012 | Before | 2012-12-16 22:38 | 2012-12-16 22:39 | 0 | 0 | 941 | 78.417 | 1 | Y | N | N | N | Y | 2012-12-15 to 2012-12-17 OR CoastPlus | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: T and R. Wind, tree through lines. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-12-16 22:38 | 2012-12-16 22:39 | 2012-12-17 04:15 | -123.6231 | 46.1604
5A93 | 1336152 | CPCC | CPCC813869 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_246704_712540474 | 2012 | Before | 2012-12-25 10:46 | 2012-12-25 12:40 | 2 | 228.6 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: replaced transformer fuse | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2012-12-25 10:46 | 2012-12-27 15:30 | 2012-12-25 12:46 | -123.6153 | 46.1665
5A93 | 1337978 | CPCC | CPCC815052 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | Line Cut-71677 | 2013 | Before | 2013-01-02 10:56 | 2013-01-02 14:51 | 1 | 235.45 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Tree took primary wire down. Crew to make repairs. | DISTRIBUTION | DEVICE | MANUAL | 2013-01-02 15:30 | COMPLETED |  | 2013-01-02 10:57 | 2013-01-04 11:10 | 2013-01-02 16:05 | -123.5792 | 46.1478
5A93 | 1340695 | CPCC | CPCC817002 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_162201_475940199 | 2013 | Before | 2013-01-15 12:09 | 2013-01-15 15:55 | 1 | 226.083 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | SOURCE: B/O ug service. Crew made temporary repairs. | DISTRIBUTION | CUSTOMER | MANUAL | 2013-01-15 16:45 | COMPLETED |  | 2013-01-15 12:09 | 2013-01-15 15:55 | 2013-01-15 16:00 | -123.564 | 46.173
5A93 | 1347856 | CPCC | CPCC821432 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | SB_156303_1580204317 | 2013 | Before | 2013-02-25 17:26 | 2013-02-25 23:00 | 37 | 11511.533 | 0 | 0 | 2 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | POLE OH |  |  |  | SOURCE: Car hit pole and wire down. Crew making repairs. Repairs made. | DISTRIBUTION | DEVICE | MANUAL | 2013-02-26 01:00 | COMPLETED |  | 2013-02-25 17:26 | 2013-02-25 23:00 | 2013-02-25 23:05 | -123.5342 | 46.1758
5A93 | 1347812 | CPCC | CPCC821407 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2013 | Before | 2013-02-25 16:26 | 2013-02-25 16:26 | 0 | 0 | 942 | 31.4 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | POLE OH |  |  |  |  | DISTRIBUTION | DEVICE | AUTO | 2013-02-25 19:30 | COMPLETED |  | 2013-02-25 16:26 | 2013-02-25 16:26 | 2013-02-25 17:10 | -123.6231 | 46.1604
5A93 | 1361203 | CPCC | CPCC829408 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_248602_712540487 | 2013 | Before | 2013-04-30 11:52 | 2013-04-30 13:59 | 93 | 11773.8 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman reports primary wire down. Serviceman reports wire was old and fatigue and just came down. He will make repairs and report. He has made repairs and customer is back in service. | DISTRIBUTION | DEVICE | AUTO | 2013-04-30 15:00 | COMPLETED |  | 2013-04-30 11:53 | 2013-04-30 13:59 | 2013-04-30 14:31 | -123.6117 | 46.1652
5A93 | 1357832 | CPCC | CPCC827416 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_300300_524160638 | 2013 | Before | 2013-04-14 15:10 | 2013-04-14 16:06 | 2 | 111.7 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: serviceman stated that the fuse was broken, refused the cutout and customers are back in service | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-04-14 18:15 | COMPLETED |  | 2013-04-14 15:10 | 2013-04-14 16:06 | 2013-04-14 17:05 | -123.6083 | 46.1461
5A93 | 1374824 | CPCC | CPCC838225 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2013 | Before | 2013-06-24 01:39 | 2013-06-24 01:39 | 0 | 0 | 942 | 78.5 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: T and R. Outage 838228. Tree through primary. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2013-06-24 01:39 | 2013-06-24 01:39 | 2013-06-24 10:00 | -123.6231 | 46.1604
5A93 | 1374825 | CPCC | CPCC838226 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2013 | Before | 2013-06-24 01:41 | 2013-06-24 01:41 | 0 | 0 | 942 | 78.5 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: T and R. Outage 838228. Tree through primary. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2013-06-24 01:41 | 2013-06-24 01:41 | 2013-06-24 10:00 | -123.6231 | 46.1604
5A93 | 1375018 | CPCC | CPCC838321 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_201600_524160548 | 2013 | Before | 2013-06-24 16:15 | 2013-06-24 17:56 | 1 | 101.6 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: paged response. Transformer fuse pulled apart. Refused and customer is back on. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-06-24 19:15 | COMPLETED |  | 2013-06-24 16:15 | 2013-06-24 17:56 | 2013-06-24 18:00 | -123.5869 | 46.1648
5A93 | 1365176 | CPCC | CPCC832736 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2013 | Before | 2013-05-14 20:28 | 2013-05-14 20:28 | 0 | 0 | 942 | 78.5 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: T and R. Unkown. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2013-05-14 20:28 | 2013-05-14 20:28 | 2013-05-15 06:52 | -123.6231 | 46.1604
5A93 | 1366241 | CPCC | CPCC833114 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_291900_524160618 | 2013 | Before | 2013-05-19 09:43 | 2013-05-19 12:49 | 2 | 372.567 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Burnt up cutout, needs 2 man crew and flaggers due to location. Repairs made and customers are back on. | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2013-05-19 14:30 | COMPLETED |  | 2013-05-19 09:43 | 2013-05-19 12:49 | 2013-05-19 13:05 | -123.5873 | 46.1553
5A93 | 1375447 | CPCC | CPCC838753 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_023500_475940276 | 2013 | Before | 2013-06-25 19:35 | 2013-06-26 02:04 | 24 | 5139.5 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | INSULATOR OH |  |  |  | SOURCE: serviceman states that there is a broken insulator at pole # 355804, will get help to change make repairs. Repairs made. | DISTRIBUTION | DEVICE | MANUAL | 2013-06-26 02:00 | COMPLETED |  | 2013-06-25 19:35 | 2013-06-26 02:04 | 2013-06-26 04:51 | -123.52 | 46.2069
5A93 | 1355486 | CPCC | CPCC826104 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_083101_475940341 | 2013 | Before | 2013-04-04 21:20 | 2013-04-04 22:55 | 4 | 381.2 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown line fuse. Cause was deteriorated fuse. | DISTRIBUTION | DEVICE | AUTO | 2013-04-05 00:30 | COMPLETED |  | 2013-04-04 21:20 | 2013-04-04 22:56 | 2013-04-04 23:15 | -123.582 | 46.1873
5A93 | 1374826 | CPCC | CPCC838228 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_169101_475940214 | 2013 | Before | 2013-06-24 01:51 | 2013-06-24 07:35 | 39 | 12996.266 | 0 | 0 | 2 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Servicman found 40T fuses blown at 169101. Tree through line W/ 3 phases down on Hwy 30. 3 man crew & 2 Flaggers called out | DISTRIBUTION | DEVICE | MANUAL | 2013-06-24 07:45 | COMPLETED |  | 2013-06-24 02:15 | 2013-06-24 07:35 | 2013-06-24 10:00 | -123.5486 | 46.1735
5A93 | 1368778 | CPCC | CPCC834671 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | RC_202904_1580471805 | 2013 | Before | 2013-05-29 08:21 | 2013-05-29 08:23 | 0 | 0 | 276 | 354.2 | 1 | Y | N | N | N | N |  | PLANNED | INTENTIONAL TO CLEAR TROUBLE | TREES | TREE - NON-PREVENTABLE | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Crew opened field recloser to remove limb off of primary line. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2013-05-29 08:21 | 2013-05-29 08:32 | 2013-05-29 16:26 | -123.5845 | 46.1701
5A93 | 1366843 | CPCC | CPCC833450 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_345600_237790094 | 2013 | Before | 2013-05-21 11:47 | 2013-05-21 14:53 | 1 | 186.4 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | SOURCE: B/O x-fmr. Crew replaced. | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2013-05-21 18:00 | COMPLETED |  | 2013-05-21 11:47 | 2013-05-21 14:53 | 2013-05-21 15:56 | -123.5347 | 46.2222
5A93 | 1356559 | CPCC | CPCC826778 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_106400_475940281 | 2013 | Before | 2013-04-09 06:00 | 2013-04-09 06:55 | 1 | 55.133 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: melted fuse | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-04-09 09:00 | COMPLETED |  | 2013-04-09 06:00 | 2013-04-09 06:55 | 2013-04-09 07:06 | -123.5343 | 46.1924
5A93 | 1395631 | CPCC | CPCC847653 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_206401_524160592 | 2013 | Before | 2013-08-21 09:20 | 2013-08-21 09:48 | 2 | 56.4 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Deteriorated x-fmr fuse, Serviceman replaced fuse and it held. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-08-21 12:30 | COMPLETED |  | 2013-08-21 09:20 | 2013-08-21 09:48 | 2013-08-21 16:27 | -123.5765 | 46.1622
5A93 | 1394843 | CPCC | CPCC847177 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_246700_712540479 | 2013 | Before | 2013-08-18 21:32 | 2013-08-18 23:21 | 4 | 436.267 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Dip fuse pulled apart. Refused and customers are back on. | DISTRIBUTION | DEVICE | AUTO | 2013-08-19 00:45 | COMPLETED |  | 2013-08-18 21:32 | 2013-08-18 23:21 | 2013-08-18 23:31 | -123.6147 | 46.1668
5A93 | 1393886 | CPCC | CPCC846621 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_174000_467110041 | 2013 | Before | 2013-08-14 16:51 | 2013-08-14 19:55 | 23 | 4235.833 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - TRIMMABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman on a reconnect. Will dispatch this call when done. Crew patroled line found tree on line removed it and restored power | DISTRIBUTION | DEVICE | MANUAL | 2013-08-14 22:00 | COMPLETED |  | 2013-08-14 16:51 | 2013-08-14 19:55 | 2013-08-14 20:50 | -123.4561 | 46.171
5A93 | 1424644 | CPCC | CPCC867797 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_114600_475940251 | 2013 | Before | 2013-11-26 07:58 | 2013-11-26 11:31 | 1 | 212.717 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | TRANSFORMER OH |  |  |  | SOURCE: Truck driver tore down primary neutral and secondary and damaged xmfr. Crew to make repairs. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-11-26 11:00 | COMPLETED |  | 2013-11-26 07:58 | 2013-11-26 11:31 | 2013-11-26 16:24 | -123.5187 | 46.1944
5A93 | 1408453 | CPCC | CPCC857451 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_172803_524160343 | 2013 | Before | 2013-09-28 16:21 | 2013-09-28 23:20 | 1 | 419.3 | 0 | 0 | 1 | Y | N | N | N | Y | 2013-09-28 to 2013-09-29 OR CoastPlus | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: removed tree branch off service | DISTRIBUTION | CUSTOMER | MANUAL | 2013-09-28 22:30 | COMPLETED |  | 2013-09-28 16:21 | 2013-09-28 23:20 | 2013-09-29 01:41 | -123.585 | 46.1828
5A93 | 1408784 | CPCC | CPCC858522 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_169101_475940214 | 2013 | Before | 2013-09-29 09:59 | 2013-09-29 13:24 | 39 | 8014.5 | 0 | 0 | 1 | Y | N | N | N | Y | 2013-09-28 to 2013-09-29 OR CoastPlus | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Tree took down primary. Crew needed. | DISTRIBUTION | DEVICE | MANUAL | 2013-09-29 17:00 | COMPLETED |  | 2013-09-29 09:59 | 2013-09-29 13:24 | 2013-09-29 14:06 | -123.5486 | 46.1735
5A93 | 1415344 | CPCC | CPCC862472 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_176700_524160334 | 2013 | Before | 2013-10-18 05:55 | 2013-10-18 07:28 | 1 | 92.883 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman arrived and found broken fuse made repairs and restored power | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-10-18 09:00 | COMPLETED |  | 2013-10-18 05:55 | 2013-10-18 07:28 | 2013-10-18 10:09 | -123.5749 | 46.1811
5A93 | 1408348 | CPCC | CPCC857328 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_169101_475940214 | 2013 | Before | 2013-09-28 14:34 | 2013-09-28 21:12 | 39 | 15521.35 | 0 | 0 | 1 | Y | N | N | N | Y | 2013-09-28 to 2013-09-29 OR CoastPlus | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: serviceman patrolled the line and removed a limb from two primary conductors, will refuse and get customers back in service | DISTRIBUTION | DEVICE | MANUAL | 2013-09-28 22:15 | COMPLETED |  | 2013-09-28 14:34 | 2013-09-28 21:12 | 2013-09-28 22:01 | -123.5486 | 46.1735
5A93 | 1420058 | CPCC | CPCC865530 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_169101_475940214 | 2013 | Before | 2013-11-07 06:45 | 2013-11-07 12:21 | 39 | 13081.9 | 0 | 0 | 1 | Y | N | N | N | Y | 2013-11-07 to 2013-11-07 OR Coastplus | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Tree took down primary line and blew line fuses on pole# 169101. Crew to make repairs. | DISTRIBUTION | DEVICE | MANUAL | 2013-11-07 11:00 | COMPLETED |  | 2013-11-07 06:46 | 2013-11-07 12:21 | 2013-11-07 15:18 | -123.5486 | 46.1735
5A93 | 1420069 | CPCC | CPCC865527 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2013 | Before | 2013-11-07 06:40 | 2013-11-07 06:40 | 0 | 0 | 944 | 78.667 | 1 | Y | N | N | N | Y | 2013-11-07 to 2013-11-07 OR Coastplus | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Closed on test, did not hold. Tree on 115kv bus at Vernon was the cause. Associated to Vernon sub outage. PROSPER: Ignore comments. T & R. See outage CPCC865530. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2013-11-07 06:40 | 2013-11-15 15:42 | 2013-11-07 15:28 | -123.6231 | 46.1604
5A93 | 1406000 | CPCC | CPCC856218 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_169500_475940248 | 2013 | Before | 2013-09-21 22:10 | 2013-09-21 22:42 | 19 | 604.517 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | TREES | TREE - NON-PREVENTABLE | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Took emergency outage to remove tree from line. See outage 856204 for original call. Tree removed. Customers are back on. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2013-09-21 22:10 | 2013-09-21 22:42 | 2013-09-21 22:46 | -123.5494 | 46.1785
5A93 | 1420063 | CPCC | CPCC865732 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_169101_475940214 | 2013 | Before | 2013-11-07 12:48 | 2013-11-07 14:04 | 6 | 456.1 | 0 | 0 | 1 | Y | N | N | N | Y | 2013-11-07 to 2013-11-07 OR Coastplus | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Open line fuse. Serviceman patrolled and found no cause. Replaced fuse and it held. | DISTRIBUTION | DEVICE | AUTO | 2013-11-07 16:00 | COMPLETED |  | 2013-11-07 12:48 | 2013-11-07 14:04 | 2013-11-07 15:23 | -123.5486 | 46.1735
5A93 | 1422909 | CPCC | CPCC867310 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_167100_475940209 | 2013 | Before | 2013-11-21 12:06 | 2013-11-21 14:16 | 4 | 520.867 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: B/O cut-out. Crew replaced cut-out, power restored. | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2013-11-21 16:00 | COMPLETED |  | 2013-11-21 12:06 | 2013-11-21 14:16 | 2013-11-21 15:39 | -123.5537 | 46.1731
5A93 | 1407389 | CPCC | CPCC857000 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_166100_475940208 | 2013 | Before | 2013-09-26 19:19 | 2013-09-26 22:20 | 2 | 361.467 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: crew to change cut out | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-09-26 22:30 | COMPLETED |  | 2013-09-26 19:19 | 2013-09-26 22:20 | 2013-09-26 23:07 | -123.5547 | 46.1723
5A93 | 1419113 | CPCC | CPCC865103 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_175200_467110038 | 2013 | Before | 2013-11-03 09:27 | 2013-11-03 11:09 | 2 | 202.833 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Transformer fuse blew, bad order fuse. Refused and customers are back on. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-11-03 12:30 | COMPLETED |  | 2013-11-03 09:27 | 2013-11-03 11:09 | 2013-11-03 11:48 | -123.4546 | 46.1735
5A93 | 1444280 | CPCC | CPCC884787 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2014 | Before | 2014-02-15 16:45 | 2014-02-15 16:45 | 0 | 0 | 945 | 78.75 | 1 | Y | N | N | N | Y | 2014-02-15 OR CoastPlus | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: T and R. Wire down due to tree. Outage 884801. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2014-02-15 16:45 | 2014-02-15 16:45 | 2014-02-16 07:04 | -123.6231 | 46.1604
5A93 | 1442633 | CPCC | CPCC883015 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2014 | Before | 2014-02-12 02:05 | 2014-02-12 02:05 | 0 | 0 | 945 | 78.75 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: T&R | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2014-02-12 02:05 | 2014-02-12 02:05 | 2014-02-12 02:14 | -123.6231 | 46.1604
5A93 | 1439935 | CPCC | CPCC878377 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_172002_524160358 | 2014 | Before | 2014-02-04 08:12 | 2014-02-04 16:35 | 5 | 2516.833 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Blown dip fuse on pole# 172002 due to b/o ug primary. Crew made repairs. | DISTRIBUTION | DEVICE | MANUAL | 2014-02-04 17:00 | COMPLETED |  | 2014-02-04 08:12 | 2014-02-04 16:35 | 2014-02-04 17:18 | -123.5836 | 46.1714
5A93 | 1434865 | CPCC | CPCC874132 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2014 | Before | 2014-01-11 03:35 | 2014-01-11 03:35 | 0 | 0 | 945 | 47.25 | 1 | Y | N | N | N | Y | 2014/01/11 to 2014/01/11 OR CoastPlus | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: T&R due to Trees and wind | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2014-01-11 03:35 | 2014-01-11 03:35 | 2014-01-11 06:09 | -123.6231 | 46.1604
5A93 | 1435085 | CPCC | CPCC874139 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_169101_475940214 | 2014 | Before | 2014-01-11 03:42 | 2014-01-11 14:44 | 39 | 21819 | 0 | 0 | 2 | Y | N | N | N | Y | 2014/01/11 to 2014/01/11 OR CoastPlus | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Tree through primary. Repairs made and customers are back on. | DISTRIBUTION | DEVICE | MANUAL | 2014-01-11 11:45 | COMPLETED |  | 2014-01-11 03:42 | 2014-01-11 14:44 | 2014-01-11 14:49 | -123.5486 | 46.1735
5A93 | 1431819 | CPCC | CPCC872136 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_166280_475940212 | 2013 | Before | 2013-12-24 08:06 | 2013-12-24 11:23 | 1 | 197.067 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: tree limbs were cleared from service and new wire spliced in to restore power | DISTRIBUTION | CUSTOMER | AUTO | 2013-12-24 11:15 | COMPLETED |  | 2013-12-24 08:06 | 2013-12-24 11:23 | 2013-12-24 13:59 | -123.555 | 46.1736
5A93 | 1447631 | CPCC | CPCC887256 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2014 | Before | 2014-03-01 23:23 | 2014-03-01 23:23 | 0 | 0 | 945 | 236.25 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: T&R | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2014-03-01 23:23 | 2014-03-01 23:23 | 2014-03-02 00:14 | -123.6231 | 46.1604
5A93 | 1447635 | CPCC | CPCC887258 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2014 | Before | 2014-03-01 23:24 | 2014-03-02 01:02 | 945 | 92862 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: patrolled, removed tree branch | DISTRIBUTION | DEVICE | AUTO | 2014-03-02 02:30 | COMPLETED |  | 2014-03-01 23:24 | 2014-03-02 01:02 | 2014-03-02 01:07 | -123.6231 | 46.1604
5A93 | 1448158 | CPCC | CPCC887579 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2014 | Before | 2014-03-04 09:04 | 2014-03-04 09:04 | 0 | 0 | 945 | 63 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: T and R. Unknown. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2014-03-04 09:04 | 2014-03-04 09:04 | 2014-03-04 14:19 | -123.6231 | 46.1604
5A93 | 1447636 | CPCC | CPCC887257 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2014 | Before | 2014-03-01 23:23 | 2014-03-01 23:24 | 0 | 0 | 945 | 897.75 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: patrolled & removed tree branch | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2014-03-01 23:23 | 2014-03-01 23:24 | 2014-03-02 01:07 | -123.6231 | 46.1604
5A93 | 1446556 | CPCC | CPCC886766 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2014 | Before | 2014-02-25 13:17 | 2014-02-25 13:17 | 0 | 0 | 945 | 78.75 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: T&R due to limb on the line | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2014-02-25 13:17 | 2014-02-25 13:17 | 2014-02-25 15:08 | -123.6231 | 46.1604
5A93 | 1444278 | CPCC | CPCC884781 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2014 | Before | 2014-02-15 16:42 | 2014-02-15 16:43 | 0 | 0 | 945 | 78.75 | 1 | Y | N | N | N | Y | 2014-02-15 OR CoastPlus | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: T and R. Wire down due to tree. Outage 884801. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2014-02-15 16:42 | 2014-02-15 16:42 | 2014-02-16 07:04 | -123.6231 | 46.1604
5A93 | 1448109 | CPCC | CPCC887583 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_308400_524160659 | 2014 | Before | 2014-03-04 09:15 | 2014-03-04 10:40 | 1 | 84.367 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Broken fuse, refused and customer is back on. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-03-04 12:15 | COMPLETED |  | 2014-03-04 09:15 | 2014-03-04 10:40 | 2014-03-04 11:14 | -123.5916 | 46.1486
5A93 | 1447533 | CPCC | CPCC887212 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_033703_475940333 | 2014 | Before | 2014-03-01 07:49 | 2014-03-01 13:27 | 2 | 675.933 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | SOURCE: Serviceman found bad order 10kva xfmr. 3 man crew & 2 flaggers to be called for repair | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2014-03-01 14:00 | COMPLETED |  | 2014-03-01 07:49 | 2014-03-01 13:28 | 2014-03-01 13:34 | -123.5404 | 46.2099
5A93 | 1433857 | CPCC | CPCC873041 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_259300_1580247858 | 2014 | Before | 2014-01-06 17:14 | 2014-01-06 19:51 | 42 | 6589.1 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: car - pole responder on site on site wire down blown line fuse. Crew made repairs, refused & restored | DISTRIBUTION | DEVICE | AUTO | 2014-01-06 20:30 | COMPLETED |  | 2014-01-06 17:17 | 2014-01-06 19:57 | 2014-01-06 23:04 | -123.6091 | 46.1465
5A93 | 1444571 | CPCC | CPCC885500 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2014 | Before | 2014-02-16 21:15 | 2014-02-16 21:16 | 0 | 0 | 945 | 78.75 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: T&R due to wind and trees | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2014-02-16 21:15 | 2014-02-16 21:15 | 2014-02-17 01:18 | -123.6231 | 46.1604
5A93 | 1442665 | CPCC | CPCC883022 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_211901_1580419438 | 2014 | Before | 2014-02-12 02:35 | 2014-02-12 04:23 | 70 | 7568.167 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: patroled & refused PROSPER: Reversed Direct and Contributory Causes. | DISTRIBUTION | DEVICE | AUTO | 2014-02-12 05:45 | COMPLETED |  | 2014-02-12 02:35 | 2014-02-12 09:24 | 2014-02-12 05:14 | -123.5662 | 46.1699
5A93 | 1442758 | CPCC | CPCC883046 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_023500_475940276 | 2014 | Before | 2014-02-12 03:58 | 2014-02-12 06:36 | 24 | 3794.4 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Wire down, crew to make repairs PROSPER: Reversed Direct and Contributory Causes. | DISTRIBUTION | DEVICE | AUTO | 2014-02-12 07:00 | COMPLETED |  | 2014-02-12 03:58 | 2014-02-12 09:24 | 2014-02-12 06:44 | -123.52 | 46.2069
5A93 | 1442993 | CPCC | CPCC883070 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_169200_475940215 | 2014 | Before | 2014-02-12 04:43 | 2014-02-12 09:48 | 1 | 304.917 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | POLE OH |  |  |  | SOURCE: leaning poles PROSPER: Reversed Direct and Contributory Causes. | DISTRIBUTION | DEVICE | MANUAL | 2014-02-12 08:47 | COMPLETED |  | 2014-02-12 04:43 | 2014-02-13 09:06 | 2014-02-12 14:50 | -123.5496 | 46.174
5A93 | 1448159 | CPCC | CPCC887580 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2014 | Before | 2014-03-04 09:05 | 2014-03-04 09:05 | 0 | 0 | 945 | 78.75 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: T and R. Unknown. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2014-03-04 09:05 | 2014-03-04 09:05 | 2014-03-04 14:19 | -123.6231 | 46.1604
5A93 | 1446562 | CPCC | CPCC886769 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_169101_475940214 | 2014 | Before | 2014-02-25 13:29 | 2014-02-25 14:33 | 10 | 638 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Two blown fuses due to limb across the the phases. Serviceman removed limb and replaced fuses. | DISTRIBUTION | DEVICE | AUTO | 2014-02-25 16:30 | COMPLETED |  | 2014-02-25 13:29 | 2014-02-25 14:33 | 2014-02-25 15:08 | -123.5486 | 46.1735
5A93 | 1444641 | CPCC | CPCC885536 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_169101_475940214 | 2014 | Before | 2014-02-16 21:24 | 2014-02-17 04:15 | 39 | 11431.1 | 0 | 0 | 2 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: crew found blown fuses at pole 169101, crew found wire down at two locations, made repairs to the wire on the main line and closed the cutouts, on tap line still open | DISTRIBUTION | DEVICE | AUTO | 2014-02-17 01:30 | COMPLETED |  | 2014-02-16 22:23 | 2014-02-17 05:13 | 2014-02-17 06:53 | -123.5486 | 46.1735
5A93 | 1433801 | CPCC | CPCC873039 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2014 | Before | 2014-01-06 17:11 | 2014-01-06 17:11 | 0 | 0 | 945 | 78.75 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | POLE OH |  |  |  | SOURCE: trip and reclose reported car - pole | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2014-01-06 17:11 | 2014-01-06 17:11 | 2014-01-06 17:39 | -123.6231 | 46.1604
5A93 | 1439868 | CPCC | CPCC878375 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2014 | Before | 2014-02-04 07:49 | 2014-02-04 07:49 | 0 | 0 | 945 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: T&R due to b/o ug primary. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2014-02-04 07:49 | 2014-02-04 07:51 | 2014-02-04 12:38 | -123.6231 | 46.1604
5A93 | 1444284 | CPCC | CPCC884801 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_201800_1580549254 | 2014 | Before | 2014-02-15 16:51 | 2014-02-15 20:03 | 134 | 25672.167 | 0 | 0 | 1 | Y | N | N | N | Y | 2014-02-15 OR CoastPlus | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Blown line fuses, cause was wire down due to tree. repairs made. | DISTRIBUTION | DEVICE | AUTO | 2014-02-15 20:00 | COMPLETED |  | 2014-02-15 16:52 | 2014-02-15 20:03 | 2014-02-16 07:04 | -123.5868 | 46.1674
5A93 | 1445724 | CPCC | CPCC886345 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_030701_475940162 | 2014 | Before | 2014-02-20 18:30 | 2014-02-20 20:12 | 1 | 102.717 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: page 1834. Broken jumper to transformer. Repairs made and customer is back on. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-02-20 21:30 | COMPLETED |  | 2014-02-20 18:30 | 2014-02-20 20:12 | 2014-02-20 21:49 | -123.5469 | 46.21
5A93 | 1444798 | CPCC | CPCC885666 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_150600_475940166 | 2014 | Before | 2014-02-17 07:51 | 2014-02-17 09:33 | 1 | 102.233 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman refused the tapline fuse at pole# 150600 and it held, the cause was a tree limb, customer is back in full service. | DISTRIBUTION | DEVICE | AUTO | 2014-02-17 11:00 | COMPLETED |  | 2014-02-17 07:51 | 2014-02-17 09:33 | 2014-02-17 13:39 | -123.5471 | 46.1805
5A93 | 1447630 | CPCC | CPCC887255 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2014 | Before | 2014-03-01 23:23 | 2014-03-01 23:23 | 0 | 0 | 945 | 78.75 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: T&R | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2014-03-01 23:23 | 2014-03-01 23:23 | 2014-03-02 00:09 | -123.6231 | 46.1604
5A93 | 1448948 | CPCC | CPCC888270 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_151701_475940184 | 2014 | Before | 2014-03-06 16:28 | 2014-03-06 17:53 | 1 | 84.25 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: limb across xfrmr | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-03-06 19:30 | COMPLETED |  | 2014-03-06 16:28 | 2014-03-06 17:53 | 2014-03-06 21:13 | -123.5463 | 46.1813
5A93 | 1464764 | CPCC | CPCC896703 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | Line Cut-85455 | 2014 | Before | 2014-05-08 21:44 | 2014-05-09 01:39 | 5 | 1172.917 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD NEST (BMTS) | EQUIPMENT FAILURE | POLE FIRE | POLE OH |  |  |  | SOURCE: Serviceman found pole fire, Isolated line and called crew to make repairs and restore power. PROSPER: Per the Astoria district outage 896703 was caused by an Osprey nest. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2014-05-08 21:44 | 2014-05-13 14:03 | 2014-05-09 05:53 | -123.5249 | 46.2292
5A93 | 1465168 | CPCC | CPCC897102 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_033701_475940332 | 2014 | Before | 2014-05-10 17:43 | 2014-05-10 20:26 | 62 | 10135.967 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | INTERFERENCE | VEHICLE ACCIDENT | POLE OH |  |  |  | SOURCE: Pole at 034602 broken & hanging from hit & run. Crew to replace & make repairs. Reported on 897090 (see for enroute & arrive times) | DISTRIBUTION | DEVICE | MANUAL | 2014-05-10 22:00 | COMPLETED |  | 2014-05-10 17:43 | 2014-05-10 20:26 | 2014-05-10 21:23 | -123.5396 | 46.21
5A93 | 1451176 | CPCC | CPCC889946 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_058001_467110036 | 2014 | Before | 2014-03-17 08:09 | 2014-03-17 09:51 | 11 | 1113.2 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown line fuse. Serviceman patrolled and found no cause. Replaced fuse and it held. | DISTRIBUTION | DEVICE | AUTO | 2014-03-17 11:15 | COMPLETED |  | 2014-03-17 08:09 | 2014-03-17 09:51 | 2014-03-17 15:24 | -123.4467 | 46.1995
5A93 | 1461039 | CPCC | CPCC894513 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_242402_712540461 | 2014 | Before | 2014-04-24 06:54 | 2014-04-24 09:00 | 2 | 251.167 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: B/O cut-out on x-fmr bank. Crew to replace cut-out. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-04-24 10:00 | COMPLETED |  | 2014-04-24 06:54 | 2014-04-24 11:33 | 2014-04-24 15:23 | -123.6247 | 46.1631
5A93 | 1463480 | CPCC | CPCC896075 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_176801_524160335 | 2014 | Before | 2014-05-03 10:22 | 2014-05-03 11:40 | 1 | 77.633 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Burned cutout door, will replace and restore power. Outage resolved | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-05-03 13:30 | COMPLETED |  | 2014-05-03 10:22 | 2014-05-03 11:40 | 2014-05-03 16:38 | -123.5754 | 46.1821
5A93 | 1449340 | CPCC | CPCC888801 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_342300_237790085 | 2014 | Before | 2014-03-09 09:04 | 2014-03-09 10:33 | 1 | 89.383 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: replaced transformer fuse | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-03-09 12:15 | COMPLETED |  | 2014-03-09 09:04 | 2014-03-09 10:33 | 2014-03-09 11:43 | -123.5427 | 46.2185
5A93 | 1448849 | CPCC | CPCC888196 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_171201_524160399 | 2014 | Before | 2014-03-06 10:38 | 2014-03-06 12:57 | 2 | 277.267 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: serviceman refused the cutout and customers are back in service | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-03-06 13:45 | COMPLETED |  | 2014-03-06 10:38 | 2014-03-06 12:57 | 2014-03-06 15:58 | -123.5868 | 46.1733
5A93 | 1449436 | CPCC | CPCC888818 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_200980_524160430 | 2014 | Before | 2014-03-09 17:15 | 2014-03-09 20:09 | 1 | 173.917 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | SOURCE: installing service saver, has installed the service saver and customer is back in full service | DISTRIBUTION | CUSTOMER | AUTO | 2014-03-09 20:15 | COMPLETED |  | 2014-03-09 17:15 | 2014-03-09 20:09 | 2014-03-10 00:53 | -123.5889 | 46.17
5A93 | 1485978 | CPCC | CPCC908452 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_169101_475940214 | 2014 | Before | 2014-07-22 13:50 | 2014-07-22 15:36 | 34 | 3586.433 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown line fuse due to tree in the primary . No damage to wire serviceman cleared tree. | DISTRIBUTION | DEVICE | AUTO | 2014-07-22 17:00 | COMPLETED |  | 2014-07-22 13:50 | 2014-07-22 15:36 | 2014-07-23 15:34 | -123.5486 | 46.1735
5A93 | 1476112 | CPCC | CPCC902776 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_172002_524160358 | 2014 | Before | 2014-06-21 07:31 | 2014-06-21 14:25 | 5 | 2069.75 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: bad pri UG crew making repairs | DISTRIBUTION | DEVICE | AUTO | 2014-06-21 10:45 | COMPLETED |  | 2014-06-21 07:31 | 2014-06-21 14:25 | 2014-06-21 14:28 | -123.5836 | 46.1714
5A93 | 1485979 | CPCC | CPCC908446 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2014 | Before | 2014-07-22 13:34 | 2014-07-22 13:34 | 0 | 0 | 938 | 78.167 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: T/R due to tree in line . | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2014-07-22 13:34 | 2014-07-22 13:34 | 2014-07-23 15:34 | -123.6231 | 46.1604
5A93 | 1486179 | CPCC | CPCC908567 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_034903_475940334 | 2014 | Before | 2014-07-23 03:49 | 2014-07-23 07:02 | 36 | 6964.8 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD NEST (BMTS) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: serviceman on site. investigating for cause, found blown fuses on pole 034903 possibly due to a large nest, will get crew to help remove the nest | DISTRIBUTION | DEVICE | AUTO | 2014-07-23 07:00 | COMPLETED |  | 2014-07-23 03:49 | 2014-07-23 07:02 | 2014-07-23 15:41 | -123.538 | 46.213
5A93 | 1481059 | CPCC | CPCC905468 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_249400_712540493 | 2014 | Before | 2014-07-08 09:14 | 2014-07-08 11:25 | 1 | 130.833 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman replaced b/o x-fmr fuse. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-07-08 12:15 | COMPLETED |  | 2014-07-08 09:14 | 2014-07-08 11:25 | 2014-07-08 16:45 | -123.6091 | 46.1622
5A93 | 1517044 | CPCC | CPCC931492 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_201800_1580549254 | 2014 | Before | 2014-11-12 12:47 | 2014-11-12 14:30 | 20 | 2051.66 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman reports limbs on lines | DISTRIBUTION | DEVICE | AUTO | 2014-11-12 16:15 | COMPLETED |  | 2014-11-12 13:01 | 2014-11-13 10:37 | 2014-11-12 16:13 | -123.5868 | 46.1674
5A93 | 1517054 | CPCC | CPCC931458 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2014 | Before | 2014-11-12 11:35 | 2014-11-12 11:35 | 0 | 0 | 940 | 78.333 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: T & R, tree limbs on line | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2014-11-12 11:35 | 2014-11-12 11:35 | 2014-11-12 16:23 | -123.6231 | 46.1604
5A93 | 1517055 | CPCC | CPCC931464 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2014 | Before | 2014-11-12 11:56 | 2014-11-12 11:56 | 0 | 0 | 940 | 78.333 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: T & R, Tree limbs on line | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2014-11-12 11:56 | 2014-11-12 11:56 | 2014-11-12 16:23 | -123.6231 | 46.1604
5A93 | 1502248 | CPCC | CPCC918661 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2014 | Before | 2014-09-14 03:50 | 2014-09-14 10:00 | 938 | 80361.6 | 0 | 0 | 2 | Y | N | N | N | N |  | PLANNED | INTENTIONAL TO CLEAR TROUBLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Clatsop Fire Department request to shut power off fire Hwy 30 and Clifton RD Crew will be needed to make repais wire/ pole down , crew onsite | DISTRIBUTION | DEVICE | MANUAL | 2014-09-14 13:00 | COMPLETED |  | 2014-09-14 03:50 | 2014-09-14 10:53 | 2014-09-14 12:33 | -123.6231 | 46.1604
5A93 | 1504345 | CPCC | CPCC919731 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2014 | Before | 2014-09-22 13:05 | 2014-09-22 13:05 | 0 | 0 | 939 | 78.25 | 1 | Y | N | N | N | N |  | TREES | TREE - TRIMMABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: T&R, Tree fell over in primary lines. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2014-09-22 13:05 | 2014-09-22 13:05 | 2014-09-22 16:33 | -123.6231 | 46.1604
5A93 | 1514069 | CPCC | CPCC928963 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_201506_524160564 | 2014 | Before | 2014-10-31 06:19 | 2014-10-31 07:36 | 2 | 155.667 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: B/O cut-out door. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-10-31 09:30 | COMPLETED |  | 2014-10-31 06:19 | 2014-10-31 07:36 | 2014-10-31 08:54 | -123.586 | 46.1633
5A93 | 1495637 | CPCC | CPCC915322 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_179002_524160421 | 2014 | Before | 2014-08-20 15:56 | 2014-08-20 17:30 | 2 | 189 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: serviceman reports that the fuse had broken, refused the cutout and customers are back in serviice | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-08-20 19:00 | COMPLETED |  | 2014-08-20 15:56 | 2014-08-20 18:29 | 2014-08-20 18:34 | -123.5697 | 46.1713
5A93 | 1504346 | CPCC | CPCC919738 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_169101_475940214 | 2014 | Before | 2014-09-22 13:10 | 2014-09-22 15:55 | 34 | 4777 | 0 | 0 | 2 | Y | N | N | N | N |  | TREES | TREE - TRIMMABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Wire down, due to tree that was marked 'to be removed', but tree crew had not yet removed. | DISTRIBUTION | DEVICE | AUTO | 2014-09-22 16:30 | COMPLETED |  | 2014-09-22 13:24 | 2014-09-22 15:55 | 2014-09-22 16:33 | -123.5486 | 46.1735
5A93 | 1527805 | CPCC | CPCC941745 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_348600_237790076 | 2014 | Before | 2014-12-25 17:36 | 2014-12-25 20:02 | 2 | 292.5 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  |  | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-12-25 23:00 | COMPLETED |  | 2014-12-25 19:52 | 2014-12-25 20:37 | 2014-12-25 20:38 | -123.5291 | 46.2222
5A93 | 1526056 | CPCC | CPCC940037 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_168201_475940227 | 2014 | Before | 2014-12-17 13:39 | 2014-12-17 14:02 | 4 | 89.067 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | B/O EQUIPMENT | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | SOURCE: Crew making emergency repairs to a broken bracket on pole. | DISTRIBUTION | DEVICE | MANUAL | 2014-12-17 15:30 | COMPLETED |  | 2014-12-17 13:39 | 2014-12-17 15:12 | 2014-12-17 15:18 | -123.5518 | 46.1747
5A93 | 1528182 | CPCC | CPCC941985 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_308880_524160668 | 2014 | Before | 2014-12-28 12:49 | 2014-12-28 16:16 | 1 | 206.8 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  |  | DISTRIBUTION | CUSTOMER | AUTO | 2014-12-28 16:00 | COMPLETED |  | 2014-12-28 12:50 | 2014-12-28 16:17 | 2014-12-28 16:18 | -123.591 | 46.154
5A93 | 1526054 | CPCC | CPCC940038 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_168201_475940226 | 2014 | Before | 2014-12-17 13:40 | 2014-12-17 14:02 | 1 | 22.167 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | B/O EQUIPMENT | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | SOURCE: Crew making emergency repairs to a broken bracket on pole. | DISTRIBUTION | DEVICE | MANUAL | 2014-12-17 15:30 | COMPLETED |  | 2014-12-17 13:40 | 2014-12-17 15:12 | 2014-12-17 15:13 | -123.5518 | 46.1747
5A93 | 1532818 | CPCC | CPCC944305 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | Line Cut-93748 | 2015 | Before | 2015-01-18 03:15 | 2015-01-18 08:28 | 3 | 937.8 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  |  | DISTRIBUTION | DEVICE | MANUAL | 2015-01-18 09:00 | COMPLETED |  | 2015-01-18 03:16 | 2015-01-18 08:51 | 2015-01-18 08:53 | -123.588 | 46.1733
5A93 | 1532823 | CPCC | CPCC944312 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_172203_524160398 | 2015 | Before | 2015-01-18 04:51 | 2015-01-18 10:19 | 8 | 2068.283 | 0 | 0 | 4 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman reports more issues found, requested an additional 4 man crew callout. Removed Jumper at FP # 170201, closed fuses and heated up to that point, 3 Customers still out.Repaired, all customers restored | DISTRIBUTION | DEVICE | MANUAL | 2015-01-18 09:00 | COMPLETED |  | 2015-01-18 04:51 | 2015-01-18 10:20 | 2015-01-18 10:23 | -123.5845 | 46.1733
5A93 | 1539560 | CPCC | CPCC951830 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_206700_524160511 | 2015 | Before | 2015-02-17 10:01 | 2015-02-17 10:44 | 19 | 829.35 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | CONSTRUCTION |  |  | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | SOURCE: Crew opened up line fuses on pole # 206700 so they could safely work on equipment. Approx. 30 minute outage | DISTRIBUTION | DEVICE | MANUAL | 2015-02-17 10:30 | COMPLETED |  | 2015-02-17 10:01 | 2015-02-17 12:19 | 2015-02-17 12:23 | -123.5763 | 46.1668
5A93 | 1532767 | CPCC | CPCC944288 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_206700_524160511 | 2015 | Before | 2015-01-17 22:18 | 2015-01-18 01:20 | 19 | 3452.933 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | NO DISTRIBUTION DAMAGE |  |  |  |  | DISTRIBUTION | DEVICE | AUTO | 2015-01-18 04:15 | COMPLETED |  | 2015-01-18 01:02 | 2015-01-18 01:34 | 2015-01-18 01:38 | -123.5763 | 46.1668
5A93 | 1518346 | CPCC | CPCC932777 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_355900_237790105 | 2014 | Before | 2014-11-17 04:58 | 2014-11-17 07:53 | 1 | 175.483 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: replace fuse | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-11-17 08:00 | COMPLETED |  | 2014-11-17 04:58 | 2014-11-17 07:53 | 2014-11-17 14:33 | -123.516 | 46.2263
5A93 | 1521869 | CPCC | CPCC935172 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_168201_475940226 | 2014 | Before | 2014-12-02 14:48 | 2014-12-02 15:05 | 1 | 17.583 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | DETERIORATION OR ROTTING | PRIMARY CABLE UG |  |  |  | SOURCE: Crew de-energized fuse on pole # 168201 (A phase) so they could finish repairs to bad underground on outage #935116 | DISTRIBUTION | DEVICE | MANUAL | 2014-12-02 16:00 | COMPLETED |  | 2014-12-02 14:48 | 2014-12-02 15:07 | 2014-12-02 15:08 | -123.5518 | 46.1747
5A93 | 1526668 | CPCC | CPCC940503 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_169500_475940248 | 2014 | Before | 2014-12-20 22:11 | 2014-12-21 02:30 | 20 | 5186.667 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  |  | DISTRIBUTION | DEVICE | AUTO | 2014-12-21 01:15 | COMPLETED |  | 2014-12-20 22:15 | 2014-12-21 02:32 | 2014-12-21 02:38 | -123.5494 | 46.1785
5A93 | 1529844 | CPCC | CPCC942670 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2015 | Before | 2015-01-02 07:50 | 2015-01-02 11:11 | 940 | 188611 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | OTHER SUB (EXPLAIN IN COMMENTS) |  |  |  | SOURCE: B phase substation transformer fuse blown; Opened circuit breaker at 08:29:33; Substation regulator is bad. Closed circuit breaker at 11:11. | DISTRIBUTION | DEVICE | MANUAL | 2015-01-02 13:15 | COMPLETED |  | 2015-01-02 08:30 | 2015-01-02 16:55 | 2015-01-02 17:03 | -123.6231 | 46.1604
5A93 | 1532790 | CPCC | CPCC944309 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_161205_475940202 | 2015 | Before | 2015-01-18 04:20 | 2015-01-18 06:02 | 2 | 202.5 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  |  | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-01-18 07:30 | COMPLETED |  | 2015-01-18 04:21 | 2015-01-18 06:25 | 2015-01-18 06:28 | -123.5662 | 46.1732
5A93 | 1540658 | CPCC | CPCC952437 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_247701_712540484 | 2015 | Before | 2015-02-23 13:26 | 2015-02-23 14:48 | 1 | 81.55 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-02-23 16:30 | COMPLETED |  | 2015-02-23 13:26 | 2015-02-23 14:48 | 2015-02-23 15:09 | -123.6138 | 46.1664
5A93 | 1521870 | CPCC | CPCC935116 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_168201_475940227 | 2014 | Before | 2014-12-02 06:42 | 2014-12-02 15:05 | 4 | 2012.867 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Crew made repairs to bad underground cable. | DISTRIBUTION | DEVICE | MANUAL | 2014-12-02 16:00 | COMPLETED |  | 2014-12-02 06:42 | 2014-12-02 15:07 | 2014-12-02 15:13 | -123.5518 | 46.1747
5A93 | 1532768 | CPCC | CPCC944276 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2015 | Before | 2015-01-17 22:00 | 2015-01-18 00:35 | 936 | 54326.983 | 0 | 0 | 2 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  |  | DISTRIBUTION | DEVICE | AUTO | 2015-01-18 02:45 | COMPLETED |  | 2015-01-17 23:38 | 2015-01-26 09:34 | 2015-01-18 01:38 | -123.6231 | 46.1604
5A93 | 1532847 | CPCC | CPCC944344 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_200880_524160431 | 2015 | Before | 2015-01-18 10:48 | 2015-01-18 13:02 | 1 | 133.767 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | SOURCE: bad ug sec, installed service saver | DISTRIBUTION | CUSTOMER | AUTO | 2015-01-18 14:00 | COMPLETED |  | 2015-01-18 10:49 | 2015-01-18 14:40 | 2015-01-18 14:43 | -123.589 | 46.1687
5A93 | 1532763 | CPCC | CPCC944275 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2015 | Before | 2015-01-17 23:37 | 2015-01-17 23:38 | 0 | 0 | 902 | 225.5 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: T&R due to tree on the line | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2015-01-17 23:37 | 2015-02-02 09:32 | 2015-01-18 01:38 | -123.6231 | 46.1604
5A93 | 1564345 | CPCC | CPCC966838 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_343000_237790100 | 2015 | Before | 2015-05-31 11:10 | 2015-05-31 15:30 | 2 | 519.5 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | SOURCE: Crew replaced defective transformer. | DISTRIBUTION | DEVICE | AUTO | 2015-05-31 14:15 | COMPLETED |  | 2015-05-31 11:11 | 2015-05-31 17:20 | 2015-05-31 17:23 | -123.5407 | 46.2144
5A93 | 1553909 | CPCC | CPCC960816 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_095801_475940314 | 2015 | Before | 2015-04-19 18:08 | 2015-04-19 19:31 | 1 | 83.233 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Deteriorated xfmr fuse. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-04-19 21:15 | COMPLETED |  | 2015-04-19 18:08 | 2015-04-19 19:35 | 2015-04-19 19:38 | -123.5575 | 46.1975
5A93 | 1559787 | CPCC | CPCC964165 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_176100_1580001881 | 2015 | Before | 2015-05-13 06:17 | 2015-05-13 10:37 | 12 | 3119.2 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Found fuse open due to tree through line; crew repaired primary wire down. | DISTRIBUTION | DEVICE | MANUAL | 2015-05-13 11:30 | COMPLETED |  | 2015-05-13 06:18 | 2015-05-13 10:51 | 2015-05-13 10:53 | -123.4532 | 46.1723
5A93 | 1544153 | CPCC | CPCC954139 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_205980_524160493 | 2015 | Before | 2015-03-10 18:23 | 2015-03-10 18:29 | 34 | 199.467 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | INTENTIONAL TO CLEAR TROUBLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: crew deenergized the transformer to be able to disconnect and idle meter base that has been sparking, will cut the meter base in the clear and re-energize the transformer | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2015-03-10 18:23 | 2015-03-10 18:46 | 2015-03-10 18:48 | -123.5775 | 46.1693
5A93 | 1557332 | CPCC | CPCC962877 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_172406_524160383 | 2015 | Before | 2015-05-03 16:04 | 2015-05-03 20:13 | 4 | 994.133 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | SOURCE: crew to change out transformer. Repairs made, customers are back on. | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2015-05-03 22:30 | COMPLETED |  | 2015-05-03 17:21 | 2015-05-03 22:31 | 2015-05-03 22:33 | -123.5843 | 46.1766
5A93 | 1545099 | CPCC | CPCC954768 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_172203_524160398 | 2015 | Before | 2015-03-15 15:28 | 2015-03-15 22:02 | 11 | 2516.533 | 0 | 0 | 2 | Y | N | N | N | Y | 3/15/2015 Coast Plus | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: serviceman reports wire down. will get a crew to make repairs, wire down due to tree | DISTRIBUTION | DEVICE | AUTO | 2015-03-15 19:00 | COMPLETED |  | 2015-03-15 15:36 | 2015-03-15 22:03 | 2015-03-15 22:08 | -123.5845 | 46.1733
5A93 | 1543710 | CPCC | CPCC953825 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_203502_524160556 | 2015 | Before | 2015-03-08 09:07 | 2015-03-08 10:19 | 2 | 144.067 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: responder reports deteriorated fuse | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2015-03-08 10:17 | 2015-03-08 10:20 | 2015-03-08 10:23 | -123.5825 | 46.164
5A93 | 1559501 | CPCC | CPCC963992 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_203902_524160552 | 2015 | Before | 2015-05-12 07:40 | 2015-05-12 09:26 | 2 | 212.1 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman replaced a broken transformer fuse. Restored customers. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-05-12 10:45 | COMPLETED |  | 2015-05-12 07:40 | 2015-05-12 12:07 | 2015-05-12 12:08 | -123.5838 | 46.1704
5A93 | 1587058 | CPCC | CPCC982518 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_168201_475940227 | 2015 | Before | 2015-08-06 12:26 | 2015-08-06 17:40 | 4 | 1255.133 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Serviceman found dip fuse blown on pole 168201; Crew repaired primary cable | DISTRIBUTION | DEVICE | MANUAL | 2015-08-06 19:15 | COMPLETED |  | 2015-08-06 12:26 | 2015-08-06 17:46 | 2015-08-06 17:48 | -123.5518 | 46.1747
5A93 | 1585795 | CPCC | CPCC981257 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_352602_237790111 | 2015 | Before | 2015-08-03 08:37 | 2015-08-03 11:10 | 1 | 152.383 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman found transformer fuse open; unknown cause as this service has not been used for a long time. Re-fused and it held. | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2015-08-03 11:45 | COMPLETED |  | 2015-08-03 08:38 | 2015-08-03 13:24 | 2015-08-03 13:28 | -123.522 | 46.2228
5A93 | 1571577 | CPCC | CPCC970686 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_203400_524160565 | 2015 | Before | 2015-06-23 08:13 | 2015-06-23 10:06 | 2 | 226 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Deteriorated fuse on transformer | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-06-23 11:15 | COMPLETED |  | 2015-06-23 08:13 | 2015-06-23 12:07 | 2015-06-23 12:08 | -123.5825 | 46.1625
5A93 | 1587059 | CPCC | CPCC982541 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_168201_475940226 | 2015 | Before | 2015-08-06 16:14 | 2015-08-06 17:39 | 1 | 84.867 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | DETERIORATION OR ROTTING | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Related to outage 982518 | DISTRIBUTION | DEVICE | AUTO | 2015-08-06 19:15 | COMPLETED |  | 2015-08-06 16:14 | 2015-08-06 17:47 | 2015-08-06 17:48 | -123.5518 | 46.1747
5A93 | 1581353 | CPCC | CPCC978531 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_307600_524160669 | 2015 | Before | 2015-07-19 06:58 | 2015-07-19 09:02 | 11 | 1366.2 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: serviceman reports two blown line fuses, will patrol for cause, serviceman patrolled the line and found no cause, refused the cutouts and customers are back in service | DISTRIBUTION | DEVICE | AUTO | 2015-07-19 10:15 | COMPLETED |  | 2015-07-19 06:58 | 2015-07-19 10:35 | 2015-07-19 10:38 | -123.5922 | 46.1508
5A93 | 1577392 | CPCC | CPCC974785 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_307600_524160669 | 2015 | Before | 2015-07-07 19:39 | 2015-07-08 01:00 | 14 | 4504.5 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Crew removed a tree from the line and repaired the conductors | DISTRIBUTION | DEVICE | MANUAL | 2015-07-08 02:27 | COMPLETED |  | 2015-07-07 19:48 | 2015-07-08 07:06 | 2015-07-08 07:08 | -123.5922 | 46.1508
5A93 | 1610918 | CPCC | CPCC997942 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_354403_237790119 | 2015 | Before | 2015-11-09 09:52 | 2015-11-09 10:38 | 1 | 46.2 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman found a deteriorated transformer fuse open; re-fused and it held. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-11-09 13:00 | COMPLETED |  | 2015-11-09 09:52 | 2015-11-09 11:19 | 2015-11-09 11:24 | -123.5175 | 46.22
5A93 | 1594701 | CPCC | CPCC987369 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_168201_475940227 | 2015 | Before | 2015-08-31 16:35 | 2015-08-31 22:16 | 4 | 1360.767 | 0 | 0 | 2 | Y | N | N | N | Y | 2015-08-29 OR CoastPlus | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Crew stood off B/O Underground in Cabinet at FP 168181, all other customers restored, Spoke with Water District and they are ok without power overnight, crew will fix during daylight hours | DISTRIBUTION | DEVICE | MANUAL | 2015-08-31 21:45 | COMPLETED |  | 2015-08-31 16:35 | 2015-09-01 02:12 | 2015-09-01 02:13 | -123.5518 | 46.1747
5A93 | 1611398 | CPCC | CPCC998158 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_032500_475940328 | 2015 | Before | 2015-11-10 18:45 | 2015-11-10 20:07 | 1 | 82.7 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Deteriorated fuse barrel on switch -- serviceman replaced barrel | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-11-10 21:45 | COMPLETED |  | 2015-11-10 18:45 | 2015-11-11 00:12 | 2015-11-11 00:14 | -123.5432 | 46.2072
5A93 | 1607455 | CPCC | CPCC995972 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_201804_524160515 | 2015 | Before | 2015-10-25 17:25 | 2015-10-25 20:18 | 164 | 28500.467 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: | DISTRIBUTION | DEVICE | MANUAL | 2015-10-25 22:45 | COMPLETED |  | 2015-10-25 17:38 | 2015-10-26 00:12 | 2015-10-26 00:14 | -123.5862 | 46.1679
5A93 | 1593813 | CPCC | CPCC986298 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2015 | Before | 2015-08-29 09:29 | 2015-08-29 13:53 | 944 | 249404.8 | 0 | 0 | 1 | Y | N | N | N | Y | 2015-08-29 OR CoastPlus | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: circuit breaker locked open; patrolling, wire down | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2015-08-29 10:07 | 2015-09-01 14:46 | 2015-08-29 20:03 | -123.6231 | 46.1604
5A93 | 1594931 | CPCC | CPCC987466 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | Line Cut-97817 | 2015 | Before | 2015-09-01 10:25 | 2015-09-01 11:56 | 49 | 4458.183 | 0 | 0 | 1 | Y | N | N | N | Y | 2015-08-29 OR CoastPlus | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | DETERIORATION OR ROTTING | OTHER UG (EXPLAIN IN COMMENTS FIELD) |  |  |  | SOURCE: Crew reports north side dip on pole 168201 out since last night, now opening south side of dip so they can finish repairs, digging in a ditch. | DISTRIBUTION | DEVICE | MANUAL | 2015-09-01 12:00 | COMPLETED |  | 2015-09-01 10:25 | 2015-09-01 16:21 | 2015-09-01 16:23 | -123.5524 | 46.1745
5A93 | 1589351 | CPCC | CPCC983585 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_307600_524160669 | 2015 | Before | 2015-08-13 21:58 | 2015-08-14 04:48 | 11 | 4512.2 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Crew repaired broken overhead conductor | DISTRIBUTION | DEVICE | AUTO | 2015-08-14 05:00 | COMPLETED |  | 2015-08-13 22:01 | 2015-08-14 06:57 | 2015-08-14 06:58 | -123.5922 | 46.1508
5A93 | 1604215 | CPCC | CPCC993580 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_106200_475940283 | 2015 | Before | 2015-10-10 12:32 | 2015-10-10 15:11 | 3 | 476.75 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Tree Limb Removed, Line Fuse replaced, all customers restored | DISTRIBUTION | DEVICE | AUTO | 2015-10-10 15:45 | COMPLETED |  | 2015-10-10 12:41 | 2015-10-10 15:34 | 2015-10-10 15:38 | -123.5355 | 46.1883
5A93 | 1608828 | CPCC | CPCC996686 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_169101_475940214 | 2015 | Before | 2015-10-31 11:19 | 2015-10-31 15:58 | 37 | 10306.35 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - TRIMMABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Tree took down primary conductor. Crew repaired power line | DISTRIBUTION | DEVICE | AUTO | 2015-10-31 16:00 | COMPLETED |  | 2015-10-31 11:20 | 2015-10-31 19:09 | 2015-10-31 19:14 | -123.5486 | 46.1735
5A93 | 1607391 | CPCC | CPCC995850 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2015 | Before | 2015-10-25 12:00 | 2015-10-25 17:15 | 915 | 288423.555 | 0 | 0 | 2 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: | DISTRIBUTION | DEVICE | MANUAL | 2015-10-25 17:30 | COMPLETED |  | 2015-10-25 12:18 | 2015-10-28 10:34 | 2015-10-25 17:20 | -123.6231 | 46.1604
5A93 | 1607457 | CPCC | CPCC995981 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_301200_524160639 | 2015 | Before | 2015-10-25 18:07 | 2015-10-25 23:20 | 1 | 313.433 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Trees Inc Crew removed tree from line, Customer restored | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2015-10-25 22:15 | COMPLETED |  | 2015-10-25 18:07 | 2015-10-26 00:13 | 2015-10-26 00:14 | -123.606 | 46.1453
5A93 | 1604513 | CPCC | CPCC993981 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_306600_524160658 | 2015 | Before | 2015-10-11 16:14 | 2015-10-11 17:14 | 1 | 60.1 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman arrived, found service low and damaged, replaced service and restored customer | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-10-11 19:15 | COMPLETED |  | 2015-10-11 16:14 | 2015-10-11 18:02 | 2015-10-11 18:03 | -123.5941 | 46.1509
5A93 | 1607456 | CPCC | CPCC995977 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_172504_524160355 | 2015 | Before | 2015-10-25 18:03 | 2015-10-25 21:04 | 1 | 180.517 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman repaired bad Secondary conductor damaged by tree limbs, all customers restored | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2015-10-25 22:15 | COMPLETED |  | 2015-10-25 18:03 | 2015-10-26 00:12 | 2015-10-26 00:14 | -123.5832 | 46.1778
5A93 | 1627833 | CPCC | CPCC1016575 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_297400_524160601 | 2015 | Before | 2015-12-29 07:57 | 2015-12-29 10:12 | 1 | 134.117 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Tree fell and brought down service, serviceman cleared tree and reinstalled service conductor, restored all customers | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-12-29 11:00 | COMPLETED |  | 2015-12-29 07:59 | 2015-12-29 11:01 | 2015-12-29 11:04 | -123.5727 | 46.1481
5A93 | 1613779 | CPCC | CPCC1000887 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_023301_475940272 | 2015 | Before | 2015-11-18 14:37 | 2015-11-18 16:06 | 1 | 88.733 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: open neutral due to trees | DISTRIBUTION | CUSTOMER | AUTO | 2015-11-18 17:45 | COMPLETED |  | 2015-11-18 14:38 | 2015-11-19 03:26 | 2015-11-19 03:28 | -123.5197 | 46.2045
5A93 | 1613857 | CPCC | CPCC999737 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_201800_1580549254 | 2015 | Before | 2015-11-17 13:53 | 2015-11-17 22:06 | 130 | 53879.667 | 0 | 0 | 2 | Y | N | N | N | Y | OR Coast Plus 11-17-2015 | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman isolated at pole 200100; found wire down; will re-fuse shortly | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2015-11-17 17:17 | 2015-11-19 03:47 | 2015-11-19 03:48 | -123.5868 | 46.1674
5A93 | 1625968 | CPCC | CPCC1014368 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_169101_475940214 | 2015 | Before | 2015-12-21 13:01 | 2015-12-21 21:53 | 31 | 16512.677 | 0 | 0 | 1 | Y | N | N | N | Y | OR Coast Plus 12-21-2015 | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Tree thru the line; found open fuse on 169101 PROSPER: added 1 from CPCC1014621, bad connectivity in cadops | DISTRIBUTION | DEVICE | AUTO | 2015-12-21 16:15 | COMPLETED |  | 2015-12-21 13:17 | 2016-01-05 16:00 | 2015-12-22 10:58 | -123.5486 | 46.1735
5A93 | 1634444 | CPCC | CPCC1021811 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_211901_1580419438 | 2016 | Before | 2016-01-28 04:16 | 2016-01-28 16:55 | 98 | 60566.6 | 0 | 0 | 2 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: 2 broken poles and wire down, pole 169200 & 169101; have tree crewe falling trees and continuing to replace broken poles | DISTRIBUTION | DEVICE | MANUAL | 2016-01-28 17:00 | COMPLETED |  | 2016-01-28 04:17 | 2016-01-28 18:16 | 2016-01-28 18:19 | -123.5662 | 46.1699
5A93 | 1613598 | CPCC | CPCC999218 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_169101_475940214 | 2015 | Before | 2015-11-17 12:19 | 2015-11-17 18:59 | 37 | 14805.55 | 0 | 0 | 1 | Y | N | N | N | Y | OR Coast Plus 11-17-2015 | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: wire down; crew repaired | DISTRIBUTION | DEVICE | AUTO | 2015-11-17 16:15 | COMPLETED |  | 2015-11-17 12:54 | 2015-11-18 16:24 | 2015-11-18 16:28 | -123.5486 | 46.1735
5A93 | 1619037 | CPCC | CPCC1005557 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_172200_524160298 | 2015 | Before | 2015-12-09 02:17 | 2015-12-09 10:54 | 11 | 5678.383 | 0 | 0 | 1 | Y | N | N | N | Y | OR Coast Plus 12-08-2015 | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Wire down due to tree. Tree trimmers need to cut in trail to make repairs. | DISTRIBUTION | DEVICE | MANUAL | 2015-12-09 12:00 | COMPLETED |  | 2015-12-09 05:34 | 2015-12-09 10:59 | 2015-12-09 11:04 | -123.5835 | 46.1732
5A93 | 1619667 | CPCC | CPCC1006647 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2015 | Before | 2015-12-10 08:32 | 2015-12-10 08:32 | 0 | 0 | 908 | 45.4 | 1 | Y | N | N | N | Y | OR Coast Plus 12-08-2015 | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: T&R unknown | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2015-12-10 08:32 | 2015-12-10 17:11 | 2015-12-10 17:14 | -123.6231 | 46.1604
5A93 | 1626762 | CPCC | CPCC1015759 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_116400_475940253 | 2015 | Before | 2015-12-23 18:32 | 2015-12-23 19:59 | 1 | 86.65 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman found open transformer fuse, no cause found found, re-fused and holding, all customers restored | DISTRIBUTION | CUSTOMER | AUTO | 2015-12-23 21:45 | COMPLETED |  | 2015-12-23 18:32 | 2015-12-24 03:37 | 2015-12-24 03:39 | -123.5143 | 46.1919
5A93 | 1619674 | CPCC | CPCC1006619 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_169101_475940214 | 2015 | Before | 2015-12-10 07:58 | 2015-12-10 12:51 | 38 | 11117.533 | 0 | 0 | 1 | Y | N | N | N | Y | OR Coast Plus 12-08-2015 | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: found open fuses on pole 169101; crew made repairs to wire down | DISTRIBUTION | DEVICE | MANUAL | 2015-12-10 13:00 | COMPLETED |  | 2015-12-10 08:05 | 2015-12-10 17:16 | 2015-12-10 17:19 | -123.5486 | 46.1735
5A93 | 1625975 | CPCC | CPCC1014798 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_343103_237790099 | 2015 | Before | 2015-12-21 17:26 | 2015-12-21 20:42 | 1 | 196.25 | 0 | 0 | 1 | Y | N | N | N | Y | OR Coast Plus 12-21-2015 | WEATHER | WIND |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: repaired jumper | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-12-21 20:30 | COMPLETED |  | 2015-12-21 17:26 | 2015-12-22 11:01 | 2015-12-22 11:03 | -123.5399 | 46.2161
5A93 | 1613312 | CPCC | CPCC999948 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_353901_237790113 | 2015 | Before | 2015-11-17 18:39 | 2015-11-18 02:31 | 1 | 472.217 | 0 | 0 | 1 | Y | N | N | N | Y | OR Coast Plus 11-17-2015 | TREES | TREE - TRIMMABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Crew repaired primary conductor down due to wind and trees | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2015-11-17 18:41 | 2015-11-18 10:34 | 2015-11-18 06:38 | -123.5192 | 46.2266
5A93 | 1613596 | CPCC | CPCC999150 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_173802_524160344 | 2015 | Before | 2015-11-17 10:35 | 2015-11-17 16:00 | 156 | 50718.2 | 0 | 0 | 1 | Y | N | N | N | Y | OR Coast Plus 11-17-2015 | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: per svcmn: tree through all three phases, line down at fp: 090700. c/o's open at 173801. Crew to make repairs. | DISTRIBUTION | DEVICE | AUTO | 2015-11-17 14:00 | COMPLETED |  | 2015-11-17 10:38 | 2015-11-18 16:19 | 2015-11-18 16:23 | -123.5816 | 46.1831
5A93 | 1613838 | CPCC | CPCC999331 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_248602_712540487 | 2015 | Before | 2015-11-17 14:12 | 2015-11-17 20:00 | 90 | 28201.35 | 0 | 0 | 2 | Y | N | N | N | Y | OR Coast Plus 11-17-2015 | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Crew needed to make repairs to the overhead primary | DISTRIBUTION | DEVICE | MANUAL | 2015-11-18 08:00 | COMPLETED |  | 2015-11-17 14:58 | 2015-11-19 03:43 | 2015-11-19 03:43 | -123.6117 | 46.1652
5A93 | 1620136 | CPCC | CPCC1007185 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_172002_524160388 | 2015 | Before | 2015-12-11 10:30 | 2015-12-11 11:55 | 1 | 85.1 | 0 | 0 | 1 | Y | N | N | N | Y | OR Coast Plus 12-08-2015 | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman removed a tree limb which blew fuse on pole 172002; removed limb and then re-fused and it held. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-12-11 13:30 | COMPLETED |  | 2015-12-11 10:30 | 2015-12-11 14:40 | 2015-12-11 14:42 | -123.5836 | 46.1714
5A93 | 1628684 | CPCC | CPCC1017132 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_169101_475940214 | 2016 | Before | 2016-01-01 17:02 | 2016-01-01 22:37 | 38 | 12730 | 0 | 0 | 1 | Y | N | N | N | Y | OR Coast Plus 1-1-2016 | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Crew removed tree branch from the line and repaired conductors | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2016-01-01 17:02 | 2016-01-02 07:14 | 2016-01-02 07:18 | -123.5486 | 46.1735
5A93 | 1634362 | CPCC | CPCC1021845 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_210903_475940346 | 2016 | Before | 2016-01-28 09:41 | 2016-01-28 10:58 | 10 | 769.5 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: burnt off jumper at pole 210903 | DISTRIBUTION | DEVICE | AUTO | 2016-01-28 12:45 | COMPLETED |  | 2016-01-28 09:45 | 2016-01-28 14:05 | 2016-01-28 14:09 | -123.5676 | 46.1704
5A93 | 1619979 | CPCC | CPCC1007050 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_210903_475940346 | 2015 | Before | 2015-12-10 17:26 | 2015-12-10 22:24 | 24 | 7166.8 | 0 | 0 | 1 | Y | N | N | N | Y | OR Coast Plus 12-08-2015 | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: wire down, crew made repairs | DISTRIBUTION | DEVICE | MANUAL | 2015-12-10 23:58 | COMPLETED |  | 2015-12-10 17:34 | 2015-12-11 04:54 | 2015-12-11 04:59 | -123.5676 | 46.1704
5A93 | 1613249 | CPCC | CPCC999507 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_193701_524160436 | 2015 | Before | 2015-11-17 15:26 | 2015-11-18 05:12 | 18 | 14865.9 | 0 | 0 | 1 | Y | N | N | N | Y | OR Coast Plus 11-17-2015 | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | POLE OH |  |  |  | SOURCE: Crew needed to replace a pole that was broken by a tree, Pole replaced and all customers restored | DISTRIBUTION | DEVICE | MANUAL | 2015-11-18 08:00 | COMPLETED |  | 2015-11-17 15:52 | 2015-11-18 05:38 | 2015-11-18 05:38 | -123.6003 | 46.1671
5A93 | 1613313 | CPCC | CPCC999955 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_023500_475940276 | 2015 | Before | 2015-11-17 18:42 | 2015-11-18 02:30 | 24 | 11226.4 | 0 | 0 | 1 | Y | N | N | N | Y | OR Coast Plus 11-17-2015 | TREES | TREE - TRIMMABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Crew repaired Primary conductor down due to trees and wind | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2015-11-17 18:43 | 2015-11-18 10:34 | 2015-11-18 06:38 | -123.52 | 46.2069
5A93 | 1614604 | CPCC | CPCC1001343 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_306600_524160658 | 2015 | Before | 2015-11-21 19:41 | 2015-11-21 21:52 | 1 | 131.333 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | CONNECTOR OH |  |  |  | SOURCE: broken secondary neutral connector at pole | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-11-21 22:45 | COMPLETED |  | 2015-11-21 19:41 | 2015-11-22 05:38 | 2015-11-22 05:39 | -123.5941 | 46.1509
5A93 | 1618549 | CPCC | CPCC1004847 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | RC_202904_1580471805 | 2015 | Before | 2015-12-07 13:05 | 2015-12-07 17:09 | 276 | 67431.4 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: recloser open; 2 spans of wire down | DISTRIBUTION | DEVICE | AUTO | 2015-12-07 16:30 | COMPLETED |  | 2015-12-07 13:18 | 2015-12-08 07:09 | 2015-12-08 07:14 | -123.5845 | 46.1701
5A93 | 1613820 | CPCC | CPCC1000263 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_201800_1580549254 | 2015 | Before | 2015-11-17 20:13 | 2015-11-17 22:06 | 85 | 9617.75 | 0 | 0 | 1 | Y | N | N | N | Y | OR Coast Plus 11-17-2015 | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: trees thru wire | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2015-11-17 20:19 | 2015-11-19 03:38 | 2015-11-19 03:43 | -123.5868 | 46.1674
5A93 | 1642512 | CPCC | CPCC1027839 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | RC_202904_1580471805 | 2016 | Before | 2016-03-01 13:27 | 2016-03-01 16:33 | 275 | 51218.75 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: trees are falling down in the area due to wind; found span of wire down @ pole 172800; tree on primary; repairs completed | DISTRIBUTION | DEVICE | MANUAL | 2016-03-01 18:00 | COMPLETED |  | 2016-03-01 13:30 | 2016-03-01 16:58 | 2016-03-01 17:03 | -123.5845 | 46.1701
5A93 | 1644913 | CPCC | CPCC1030675 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | RC_202904_1580471805 | 2016 | Before | 2016-03-09 22:55 | 2016-03-10 11:08 | 266 | 195088.833 | 0 | 0 | 1 | Y | N | N | N | Y | OR Coast Plus 03-09-2016 | TREES | TREE - TRIMMABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  |  | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2016-03-10 06:50 | 2016-03-10 15:06 | 2016-03-10 15:07 | -123.5845 | 46.1701
5A93 | 1642648 | CPCC | CPCC1027693 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_169101_475940214 | 2016 | Before | 2016-03-01 12:51 | 2016-03-01 20:54 | 38 | 18360.333 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | POLE OH |  |  |  | SOURCE: Serviceman found fuse open on pole 169101; found broken pole 152000 and wire down; crew en route; possibly unsafe for crew, trees are falling in the area, Pole replaced and all customers restored | DISTRIBUTION | DEVICE | MANUAL | 2016-03-01 17:30 | COMPLETED |  | 2016-03-01 12:51 | 2016-03-02 04:32 | 2016-03-02 04:37 | -123.5486 | 46.1735
5A93 | 1644910 | CPCC | CPCC1030549 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_022000_475940270 | 2016 | Before | 2016-03-10 01:43 | 2016-03-10 12:13 | 9 | 5674.35 | 0 | 0 | 1 | Y | N | N | N | Y | OR Coast Plus 03-09-2016 | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: cutout open @022000 and tree thur line and wire down @026000 per Nate | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2016-03-10 01:43 | 2016-03-10 15:02 | 2016-03-10 15:02 | -123.5213 | 46.2005
5A93 | 1646826 | CPCC | CPCC1032949 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_204802_524160532 | 2016 | Before | 2016-03-17 15:54 | 2016-03-17 16:49 | 6 | 329.4 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman found deterioroated fuse on pole 204802; | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2016-03-17 19:00 | COMPLETED |  | 2016-03-17 15:54 | 2016-03-17 16:56 | 2016-03-17 16:58 | -123.5811 | 46.1686
5A93 | 1644891 | CPCC | CPCC1030615 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_169101_475940214 | 2016 | Before | 2016-03-09 22:23 | 2016-03-10 05:41 | 38 | 16657.933 | 0 | 0 | 1 | Y | N | N | N | Y | OR Coast Plus 03-09-2016 | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Crew removed a tree from the line and repaired conductors | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2016-03-09 22:23 | 2016-03-10 14:27 | 2016-03-10 14:32 | -123.5486 | 46.1735
5A93 | 1644914 | CPCC | CPCC1030424 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | Line Cut-100480 | 2016 | Before | 2016-03-09 22:22 | 2016-03-09 22:23 | 0 | 0 | 912 | 912 | 1 | Y | N | N | N | Y | OR Coast Plus 03-09-2016 | WEATHER | WIND |  |  | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | SOURCE: CB 5A93 Multiple trip and reclose | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2016-03-09 22:33 | 2016-03-10 15:07 | 2016-03-10 15:07 | -123.6231 | 46.1606
5A93 | 1647041 | CPCC | CPCC1033108 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | RC_202904_1580471805 | 2016 | Before | 2016-03-18 11:11 | 2016-03-18 13:08 | 275 | 32156.667 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: @ 1309 FR 5A93B was closed | DISTRIBUTION | DEVICE | AUTO | 2016-03-18 14:30 | COMPLETED |  | 2016-03-18 11:16 | 2016-03-18 16:29 | 2016-03-18 16:33 | -123.5845 | 46.1701
5A93 | 1651432 | CPCC | CPCC1035736 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_206900_524160494 | 2016 | Before | 2016-04-06 08:20 | 2016-04-06 09:48 | 2 | 176.833 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: serviceman reports bad order cutout door | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2016-04-06 11:30 | COMPLETED |  | 2016-04-06 08:20 | 2016-04-06 10:03 | 2016-04-06 10:08 | -123.5761 | 46.1694
5A93 | 1670670 | CPCC | CPCC1048445 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2016 | Before | 2016-06-05 11:50 | 2016-06-05 11:50 | 0 | 0 | 910 | 60.667 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Trip & Close | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2016-06-05 11:50 | 2016-06-05 16:15 | 2016-06-05 16:18 | -123.6231 | 46.1604
5A93 | 1676128 | CPCC | CPCC1052406 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_173802_524160344 | 2016 | Before | 2016-06-21 18:43 | 2016-06-22 00:04 | 154 | 49505.867 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | POLE OH |  |  |  | SOURCE: car hit pole, one fuse open at FP 173802, serviceman had to open other 2 fuses that created outage for 154 customers. Car hit pole on F/P 086401 Crew changed out the pole | DISTRIBUTION | DEVICE | MANUAL | 2016-06-22 02:00 | COMPLETED |  | 2016-06-21 18:43 | 2016-06-22 06:33 | 2016-06-22 06:37 | -123.5816 | 46.1831
5A93 | 1670669 | CPCC | CPCC1048351 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_201800_1580549254 | 2016 | Before | 2016-06-05 05:30 | 2016-06-05 07:07 | 35 | 3364.083 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | PLANNED OUTAGE |  |  |  | SOURCE: Opened to make repairs on Outage 1048319 | DISTRIBUTION | DEVICE | AUTO | 2016-06-05 08:30 | COMPLETED |  | 2016-06-05 05:30 | 2016-06-05 16:14 | 2016-06-05 16:18 | -123.5868 | 46.1674
5A93 | 1670844 | CPCC | CPCC1048442 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_197000_524160484 | 2016 | Before | 2016-06-05 08:15 | 2016-06-05 19:18 | 4 | 2652.267 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER PADMOUNT/SUBMERSIBLE UG |  |  |  | SOURCE: Fuse blown at fp# 197000 -- serviceman investigating | DISTRIBUTION | DEVICE | MANUAL | 2016-06-06 | COMPLETED |  | 2016-06-05 11:12 | 2016-06-06 04:41 | 2016-06-06 04:43 | -123.5926 | 46.1571
5A93 | 1670679 | CPCC | CPCC1048451 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_201800_1580549254 | 2016 | Before | 2016-06-05 12:00 | 2016-06-05 13:25 | 36 | 850.2 | 0 | 0 | 2 | Y | N | N | N | N |  | OPERATIONAL | IMPROPER PROTECTIVE COORDINATION |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Fuse blew due to incorrect fuse coordination @ fp# 290801 | DISTRIBUTION | DEVICE | AUTO | 2016-06-05 15:15 | COMPLETED |  | 2016-06-05 12:03 | 2016-06-05 16:17 | 2016-06-05 16:19 | -123.5868 | 46.1674
5A93 | 1670672 | CPCC | CPCC1048319 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_201800_1580549254 | 2016 | Before | 2016-06-04 23:41 | 2016-06-05 07:07 | 95 | 42328.833 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Made repairs | DISTRIBUTION | DEVICE | MANUAL | 2016-06-05 06:00 | COMPLETED |  | 2016-06-05 00:56 | 2016-06-05 16:16 | 2016-06-05 16:18 | -123.5868 | 46.1674
5A93 | 1680671 | CPCC | CPCC1054926 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | Line Cut-102152 | 2016 | Before | 2016-07-06 07:57 | 2016-07-06 08:04 | 915 | 6054.25 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF FEED FROM SUPPLIER |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2016-07-06 07:59 | 2016-07-07 10:08 | 2016-07-07 00:08 | -123.6231 | 46.1607
5A93 | 1666007 | CPCC | CPCC1045953 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_168201_475940227 | 2016 | Before | 2016-05-19 06:24 | 2016-05-19 13:48 | 3 | 1331.8 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Part of outage# 1045843 -- Fuse blown at term pole -- need crew Patroling through brush;B/O cable; Crew made repairs 1347; | DISTRIBUTION | DEVICE | AUTO | 2016-05-19 09:30 | COMPLETED |  | 2016-05-19 06:24 | 2016-05-19 13:52 | 2016-05-19 13:53 | -123.5518 | 46.1747
5A93 | 1666035 | CPCC | CPCC1045843 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_167080_475940222 | 2016 | Before | 2016-05-19 02:09 | 2016-05-19 13:52 | 1 | 703.483 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Fuse blown at term pole -- need crew; Patroling through brush;B/O cable; Crew made repairs 1347; WIth outage 1045953 | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2016-05-19 13:53 | COMPLETED |  | 2016-05-19 02:09 | 2016-05-19 15:57 | 2016-05-19 15:58 | -123.5531 | 46.1714
5A93 | 1674223 | CPCC | CPCC1051127 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_307600_524160669 | 2016 | Before | 2016-06-15 13:21 | 2016-06-15 16:32 | 13 | 2490.367 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: found tapline fuse open due to tree thru line | DISTRIBUTION | DEVICE | AUTO | 2016-06-15 16:30 | COMPLETED |  | 2016-06-15 13:21 | 2016-06-15 16:38 | 2016-06-15 16:43 | -123.5922 | 46.1508
5A93 | 1676126 | CPCC | CPCC1052425 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_201180_524160577 | 2016 | Before | 2016-06-22 02:46 | 2016-06-22 05:24 | 1 | 158 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTORS UG |  |  |  | SOURCE: Serviceman opened and closed elbow switch on the padmount transformer. The customers power was restored | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2016-06-22 06:00 | COMPLETED |  | 2016-06-22 02:46 | 2016-06-22 06:32 | 2016-06-22 06:37 | -123.5862 | 46.1582
5A93 | 1670671 | CPCC | CPCC1048456 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2016 | Before | 2016-06-05 12:51 | 2016-06-05 12:51 | 0 | 0 | 904 | 45.2 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Trip & Close | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2016-06-05 12:51 | 2016-06-05 16:15 | 2016-06-05 16:18 | -123.6231 | 46.1604
5A93 | 1682888 | CPCC | CPCC1056231 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_168201_475940227 | 2016 | Before | 2016-07-13 03:47 | 2016-07-13 15:03 | 4 | 2705.933 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Dip fuse blown @ fp# 168201 -- crew working on repairs; ug cable does go under hwy 30 | DISTRIBUTION | DEVICE | MANUAL | 2016-07-13 17:00 | COMPLETED |  | 2016-07-13 03:47 | 2016-07-13 15:43 | 2016-07-13 15:48 | -123.5518 | 46.1747
5A93 | 1686411 | CPCC | CPCC1059694 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_176003_524160501 | 2016 | Before | 2016-07-24 16:43 | 2016-07-24 20:45 | 11 | 2666.037 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Open dip fuse at FP 176003 - no details yet on location of bad UG Primary. PROSPER: add 1 from CPCC1059688, miss modeled in Cadops | DISTRIBUTION | DEVICE | AUTO | 2016-07-24 21:00 | COMPLETED |  | 2016-07-24 17:49 | 2016-07-25 15:08 | 2016-07-24 23:28 | -123.5753 | 46.1705
5A93 | 1683611 | CPCC | CPCC1057923 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_167080_475940222 | 2016 | Before | 2016-07-15 17:28 | 2016-07-16 00:20 | 1 | 412.217 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Crew repaired bad primary underground cable Bad Underground between F/P 168181 and 218980 | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2016-07-15 20:30 | COMPLETED |  | 2016-07-15 17:28 | 2016-07-16 09:50 | 2016-07-16 09:53 | -123.5531 | 46.1714
5A93 | 1699909 | CPCC | CPCC1068230 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | UG168181_475940009 | 2016 | Before | 2016-09-08 18:30 | 2016-09-09 04:12 | 1 | 582.767 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Crew repaired B/O Primary Cable, all customers restored | DISTRIBUTION | DEVICE | MANUAL | 2016-09-09 04:30 | COMPLETED |  | 2016-09-08 18:30 | 2016-09-09 04:13 | 2016-09-09 04:18 | -123.5512 | 46.1722
5A93 | 1693845 | CPCC | CPCC1064669 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_290801_524160608 | 2016 | Before | 2016-08-17 02:18 | 2016-08-17 06:24 | 6 | 1475.8 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: OH primary phase came off of insulator -- ran Arcos for a crew | DISTRIBUTION | DEVICE | MANUAL | 2016-08-17 08:15 | COMPLETED |  | 2016-08-17 04:03 | 2016-08-17 06:24 | 2016-08-17 06:28 | -123.5883 | 46.1548
5A93 | 1699908 | CPCC | CPCC1068228 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | UG168181_475940005 | 2016 | Before | 2016-09-08 18:29 | 2016-09-09 04:09 | 1 | 580.667 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Crew opened to facilitate repairs on Outage 1068228 | DISTRIBUTION | DEVICE | MANUAL | 2016-09-09 04:30 | COMPLETED |  | 2016-09-08 18:29 | 2016-09-09 04:11 | 2016-09-09 04:13 | -123.5511 | 46.1722
5A93 | 1699910 | CPCC | CPCC1068245 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | UG168181_475940004 | 2016 | Before | 2016-09-09 01:42 | 2016-09-09 04:10 | 1 | 148.333 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | PLANNED OUTAGE |  |  |  | SOURCE: Crew opened to facilitate repairs on Outage 1068228 | DISTRIBUTION | DEVICE | AUTO | 2016-09-09 04:45 | COMPLETED |  | 2016-09-09 01:42 | 2016-09-09 04:13 | 2016-09-09 04:18 | -123.5511 | 46.1722
5A93 | 1692630 | CPCC | CPCC1063039 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_207200_524160595 | 2016 | Before | 2016-08-12 17:07 | 2016-08-12 23:24 | 1 | 377.667 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: made repairs: bo cable | DISTRIBUTION | DEVICE | AUTO | 2016-08-12 20:15 | COMPLETED |  | 2016-08-12 17:07 | 2016-08-12 23:26 | 2016-08-12 23:28 | -123.5753 | 46.1594
5A93 | 1710599 | CPCC | CPCC1076339 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_023500_475940276 | 2016 | Before | 2016-10-14 12:46 | 2016-10-14 18:48 | 24 | 8694.8 | 0 | 0 | 1 | Y | N | N | N | Y | OR CoastPlus 10-13-2016 | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: crew has made repairs to wire downa nd all customers are back in service | DISTRIBUTION | DEVICE | AUTO | 2016-10-14 18:15 | COMPLETED |  | 2016-10-14 15:03 | 2016-10-14 19:10 | 2016-10-14 19:13 | -123.52 | 46.2069
5A93 | 1710627 | CPCC | CPCC1075903 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_211901_1580419438 | 2016 | Before | 2016-10-14 07:45 | 2016-10-14 13:48 | 99 | 36016.2 | 0 | 0 | 1 | Y | N | N | N | Y | OR CoastPlus 10-13-2016 | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: line patrolled, no cause found | DISTRIBUTION | DEVICE | AUTO | 2016-10-14 12:45 | COMPLETED |  | 2016-10-14 08:46 | 2016-10-14 19:17 | 2016-10-14 19:18 | -123.5662 | 46.1699
5A93 | 1720755 | CPCC | CPCC1084536 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | Line Cut-104212 | 2016 | Before | 2016-11-25 09:17 | 2016-11-25 15:06 | 6 | 2092.1 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Tree fell & Tap fuse blown -- primary down -- need crew | DISTRIBUTION | DEVICE | MANUAL | 2016-11-25 15:15 | COMPLETED |  | 2016-11-25 11:04 | 2016-11-25 17:07 | 2016-11-25 17:08 | -123.5798 | 46.1476
5A93 | 1713689 | CPCC | CPCC1079734 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_307600_524160669 | 2016 | Before | 2016-10-24 13:59 | 2016-10-24 15:56 | 14 | 1636.133 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: all three fuses blown on FP 307600, report of wire down at fish hatchery. crew on site to investigate. upstream 'C' phase fuse blown. response will close at FP 201800 to open fuses 307600 tree caused outage, repairs completed | DISTRIBUTION | DEVICE | AUTO | 2016-10-24 17:15 | COMPLETED |  | 2016-10-24 14:09 | 2016-10-24 16:16 | 2016-10-24 16:18 | -123.5922 | 46.1508
5A93 | 1710598 | CPCC | CPCC1076340 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_023500_475940273 | 2016 | Before | 2016-10-14 13:35 | 2016-10-14 18:49 | 31 | 9726.25 | 0 | 0 | 1 | Y | N | N | N | Y | OR CoastPlus 10-13-2016 | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: crew has made repairs to wire downa nd all customers are back in service PROSPER: change time to first out 10/14/2016 13:34:51, was 10/14/2016 13:15:55 | DISTRIBUTION | DEVICE | AUTO | 2016-10-14 18:15 | COMPLETED |  | 2016-10-14 15:03 | 2016-10-17 14:36 | 2016-10-14 19:13 | -123.52 | 46.2068
5A93 | 1720484 | CPCC | CPCC1084207 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_211901_1580419438 | 2016 | Before | 2016-11-24 08:18 | 2016-11-24 11:24 | 82 | 15264.3 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | SOURCE: fuses opened here to clear tree limb at FP 162000 | DISTRIBUTION | DEVICE | AUTO | 2016-11-24 13:45 | COMPLETED |  | 2016-11-24 10:43 | 2016-11-24 11:26 | 2016-11-24 11:28 | -123.5662 | 46.1699
5A93 | 1721098 | CPCC | CPCC1084760 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_023500_475940276 | 2016 | Before | 2016-11-27 18:57 | 2016-11-27 23:42 | 24 | 4741.583 | 0 | 0 | 2 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman found wire down at FP 359600 on Peterson Lane, isolated at FP 356700, Closed in Line Fuse at FP 023500 to pick up partial customers, Crew repaired down wire due to tree and closed Fuse at FP 356700 to restore all customers | DISTRIBUTION | DEVICE | MANUAL | 2016-11-28 02:15 | COMPLETED |  | 2016-11-27 19:04 | 2016-11-27 23:44 | 2016-11-27 23:48 | -123.52 | 46.2069
5A93 | 1710621 | CPCC | CPCC1076342 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | RC_202904_1580471805 | 2016 | Before | 2016-10-14 11:18 | 2016-10-14 14:50 | 222 | 46982.6 | 0 | 0 | 1 | Y | N | N | N | Y | OR CoastPlus 10-13-2016 | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: crew has found wire down fuses open at pole 023300, will make repairs, recloser was open and crew has closed to open fuses | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2016-10-14 15:04 | 2016-10-14 19:14 | 2016-10-14 19:18 | -123.5845 | 46.1701
5A93 | 1710607 | CPCC | CPCC1076019 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_293300_524160604 | 2016 | Before | 2016-10-14 10:32 | 2016-10-14 15:00 | 1 | 267.733 | 0 | 0 | 1 | Y | N | N | N | Y | OR CoastPlus 10-13-2016 | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: customer was paer of an earlier outage, customer is back in service | DISTRIBUTION | CUSTOMER | AUTO | 2016-10-14 13:45 | COMPLETED |  | 2016-10-14 10:33 | 2016-10-14 19:11 | 2016-10-14 19:13 | -123.5829 | 46.1477
5A93 | 1710416 | CPCC | CPCC1076085 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | FS_248500__3962463 | 2016 | Before | 2016-10-14 09:52 | 2016-10-14 14:59 | 88 | 27007.2 | 0 | 0 | 1 | Y | N | N | N | Y | OR CoastPlus 10-13-2016 | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: CREW MADE REPAIRS | DISTRIBUTION | DEVICE | AUTO | 2016-10-14 15:00 | COMPLETED |  | 2016-10-14 11:47 | 2016-10-14 15:00 | 2016-10-14 15:01 | -123.6117 | 46.1644
5A93 | 1720485 | CPCC | CPCC1084179 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_211901_1580419438 | 2016 | Before | 2016-11-24 08:10 | 2016-11-24 11:24 | 17 | 3293.183 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | SOURCE: serviceman reports center phase fuse open at FP 211901 - patroling - found limb in line at FP 162000 other 2 fuses open at FP 211901 to clear tree limb hazard | DISTRIBUTION | DEVICE | AUTO | 2016-11-24 11:15 | COMPLETED |  | 2016-11-24 08:11 | 2016-11-24 11:27 | 2016-11-24 11:28 | -123.5662 | 46.1699
5A93 | 1714302 | CPCC | CPCC1080157 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_201600_524160548 | 2016 | Before | 2016-10-26 21:16 | 2016-10-26 23:12 | 1 | 116.1 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | SOURCE: Replaced connection at pole | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2016-10-27 00:15 | COMPLETED |  | 2016-10-26 21:16 | 2016-10-27 00:40 | 2016-10-27 00:43 | -123.5869 | 46.1648
5A93 | 1726958 | CPCC | CPCC1092020 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_169101_475940214 | 2016 | Before | 2016-12-15 13:18 | 2016-12-15 14:46 | 6 | 526.6 | 0 | 0 | 1 | Y | N | N | N | Y | OR Consolidated 12-14-2016 | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown line fuse, serviceman is patrolling. Did not find a cause, refused and customers are back on. | DISTRIBUTION | DEVICE | AUTO | 2016-12-15 16:30 | COMPLETED |  | 2016-12-15 13:18 | 2016-12-15 14:53 | 2016-12-15 14:58 | -123.5486 | 46.1735
5A93 | 1710957 | CPCC | CPCC1076538 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_171201_524160399 | 2016 | Before | 2016-10-15 09:39 | 2016-10-15 14:06 | 1 | 266.083 | 0 | 0 | 1 | Y | N | N | N | Y | OR CoastPlus 10-13-2016 | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: outage due to a tree taking down a parlay line, crew enroute to make repairs. repairs have been made customer back in svc | DISTRIBUTION | CUSTOMER | AUTO | 2016-10-15 12:45 | COMPLETED |  | 2016-10-15 09:39 | 2016-10-15 16:55 | 2016-10-15 16:56 | -123.5868 | 46.1733
5A93 | 1710021 | CPCC | CPCC1075265 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_023500_475940276 | 2016 | Before | 2016-10-13 20:04 | 2016-10-14 00:57 | 24 | 7036 | 0 | 0 | 1 | Y | N | N | N | Y | OR CoastPlus 10-13-2016 | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman refused Line Fuse and restored all customers | DISTRIBUTION | DEVICE | MANUAL | 2016-10-14 08:00 | COMPLETED |  | 2016-10-13 20:50 | 2016-10-14 03:22 | 2016-10-14 03:23 | -123.52 | 46.2069
5A93 | 1713137 | CPCC | CPCC1079316 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | RC_202904_1580471805 | 2016 | Before | 2016-10-21 22:33 | 2016-10-22 03:07 | 277 | 53584.483 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman onsite, Field Recloser locked open, patrolling for cause, Serviceman found open line fuse at FP 023500, going back to recloser to close on test and pick up a majority of customers, Serviceman patrolled and found no cause, refused and restored | DISTRIBUTION | DEVICE | MANUAL | 2016-10-22 02:45 | COMPLETED |  | 2016-10-21 22:41 | 2016-10-22 03:08 | 2016-10-22 03:09 | -123.5845 | 46.1701
5A93 | 1718014 | CPCC | CPCC1082185 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_054701_467110034 | 2016 | Before | 2016-11-13 14:23 | 2016-11-13 16:34 | 1 | 131.5 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: serviceman reports secondary conductors were affected. Serviceman disonnected and cleared hazard disconnecting customer. Customer made repairs on their equipment and serviceman was able to reconnect PROSPER: power out | DISTRIBUTION | CUSTOMER | AUTO | 2016-11-13 17:30 | COMPLETED |  | 2016-11-13 14:23 | 2016-11-14 10:39 | 2016-11-13 18:23 | -123.4552 | 46.2081
5A93 | 1710602 | CPCC | CPCC1076293 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_169101_475940214 | 2016 | Before | 2016-10-14 14:03 | 2016-10-14 17:00 | 39 | 6909.5 | 0 | 0 | 1 | Y | N | N | N | Y | OR CoastPlus 10-13-2016 | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: serviceman reported a tree on the line cleared the line and refused the cutout, all cvustomers are back in service | DISTRIBUTION | DEVICE | AUTO | 2016-10-14 17:15 | COMPLETED |  | 2016-10-14 14:05 | 2016-10-14 19:11 | 2016-10-14 19:13 | -123.5486 | 46.1735
5A93 | 1710625 | CPCC | CPCC1075845 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_306980_524160485 | 2016 | Before | 2016-10-14 07:59 | 2016-10-14 15:00 | 1 | 420.683 | 0 | 0 | 1 | Y | N | N | N | Y | OR CoastPlus 10-13-2016 | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: customer was part of an earlier outage | DISTRIBUTION | CUSTOMER | AUTO | 2016-10-14 11:00 | COMPLETED |  | 2016-10-14 08:00 | 2016-10-14 19:15 | 2016-10-14 19:18 | -123.595 | 46.1562
5A93 | 1730181 | CPCC | CPCC1093851 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_355900_237790105 | 2016 | Before | 2016-12-25 15:43 | 2016-12-25 16:58 | 1 | 75.317 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: replaced transformer fuse | DISTRIBUTION | CUSTOMER | AUTO | 2016-12-25 18:45 | COMPLETED |  | 2016-12-25 15:43 | 2016-12-26 02:53 | 2016-12-26 02:58 | -123.516 | 46.2263
5A93 | 1728628 | CPCC | CPCC1092817 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_355900_237790105 | 2016 | Before | 2016-12-19 13:49 | 2016-12-19 17:02 | 1 | 193.483 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman replaced transformer secondary connectors | DISTRIBUTION | CUSTOMER | AUTO | 2016-12-19 18:30 | COMPLETED |  | 2016-12-19 15:27 | 2016-12-19 20:21 | 2016-12-19 20:23 | -123.516 | 46.2263
5A93 | 1734803 | CPCC | CPCC1101675 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2017 | Before | 2017-01-08 12:04 | 2017-01-08 12:14 | 917 | 9429.817 | 0 | 0 | 1 | Y | N | N | N | Y | OR Consolidated 01-02-2017 | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman saw tree limb fall into primary, cleared tree limb and closed CB 5A93 picking up customers. | DISTRIBUTION | DEVICE | AUTO | 2017-01-08 15:15 | COMPLETED |  | 2017-01-08 12:04 | 2017-01-08 15:21 | 2017-01-08 15:24 | -123.6231 | 46.1604
5A93 | 1744459 | CPCC | CPCC1111495 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_190200_524160478 | 2017 | Before | 2017-02-06 07:43 | 2017-02-06 09:01 | 1 | 77.867 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | SNOW, SLEET AND BLIZZARD |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2017-02-06 10:45 | COMPLETED |  | 2017-02-06 07:45 | 2017-02-06 10:47 | 2017-02-06 10:48 | -123.6077 | 46.159
5A93 | 1753510 | CPCC | CPCC1119060 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_346700_237790077 | 2017 | Before | 2017-03-07 13:12 | 2017-03-07 14:56 | 11 | 1144.55 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown line fuse, patrolled. found no cause,, will close on test | DISTRIBUTION | DEVICE | AUTO | 2017-03-07 16:45 | COMPLETED |  | 2017-03-07 13:38 | 2017-03-07 15:03 | 2017-03-07 15:05 | -123.5324 | 46.2238
5A93 | 1744137 | CPCC | CPCC1110979 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_356700_237790114 | 2017 | Before | 2017-02-04 17:18 | 2017-02-04 21:53 | 13 | 3576.083 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Primary & neutral down -- ran Arcos fro a crew, Crew made repairs and restored all customers | DISTRIBUTION | DEVICE | MANUAL | 2017-02-04 23:30 | COMPLETED |  | 2017-02-04 17:18 | 2017-02-05 01:41 | 2017-02-05 01:43 | -123.5142 | 46.2241
5A93 | 1744344 | CPCC | CPCC1111385 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_169101_475940214 | 2017 | Before | 2017-02-05 19:02 | 2017-02-06 02:52 | 39 | 18327.4 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman found open fuses at FP 169101, Patrolled line and knocked off several tree limbs, refused and restored all customers | DISTRIBUTION | DEVICE | MANUAL | 2017-02-06 05:45 | COMPLETED |  | 2017-02-05 23:28 | 2017-02-06 03:09 | 2017-02-06 03:13 | -123.5486 | 46.1735
5A93 | 1744354 | CPCC | CPCC1111246 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_109502_1580128764 | 2017 | Before | 2017-02-05 17:31 | 2017-02-05 23:12 | 12 | 3970.417 | 0 | 0 | 2 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Crew Made repairs to downed wire due to tree thru line | DISTRIBUTION | DEVICE | AUTO | 2017-02-05 20:45 | COMPLETED |  | 2017-02-05 17:31 | 2017-02-06 03:11 | 2017-02-06 03:13 | -123.5282 | 46.1925
5A93 | 1744902 | CPCC | CPCC1112947 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_169101_475940214 | 2017 | Before | 2017-02-07 10:16 | 2017-02-07 11:41 | 39 | 3333.2 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | WEATHER | SNOW, SLEET AND BLIZZARD | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: crew took emergency to make repairs to OH conductor hanging below communications | DISTRIBUTION | DEVICE | MANUAL | 2017-02-07 11:30 | COMPLETED |  | 2017-02-07 10:16 | 2017-02-07 12:58 | 2017-02-07 13:03 | -123.5486 | 46.1735
5A93 | 1734802 | CPCC | CPCC1101592 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | FS_248500__3962463 | 2017 | Before | 2017-01-08 09:49 | 2017-01-08 11:57 | 89 | 11443.917 | 0 | 0 | 1 | Y | N | N | N | Y | OR Consolidated 01-02-2017 | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: tree on line PROSPER: power out | DISTRIBUTION | DEVICE | AUTO | 2017-01-08 13:00 | COMPLETED |  | 2017-01-08 09:49 | 2017-01-10 15:59 | 2017-01-08 15:23 | -123.6117 | 46.1644
5A93 | 1746862 | CPCC | CPCC1114462 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_106200_475940283 | 2017 | Before | 2017-02-13 14:19 | 2017-02-13 14:48 | 3 | 86.15 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Opened tap fuse to make emergency conductor repair | DISTRIBUTION | DEVICE | MANUAL | 2017-02-13 16:30 | COMPLETED |  | 2017-02-13 14:19 | 2017-02-13 14:53 | 2017-02-13 14:58 | -123.5355 | 46.1883
5A93 | 1734730 | CPCC | CPCC1101614 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2017 | Before | 2017-01-08 10:21 | 2017-01-08 11:33 | 828 | 59947.2 | 0 | 0 | 1 | Y | N | N | N | Y | OR Consolidated 01-02-2017 | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: CB 5A93 locked open at Sub. Serviceman arrived and is patrolling. tree removed from line. | DISTRIBUTION | DEVICE | AUTO | 2017-01-08 13:30 | COMPLETED |  | 2017-01-08 10:21 | 2017-01-10 10:48 | 2017-01-08 12:58 | -123.6231 | 46.1604
5A93 | 1745703 | CPCC | CPCC1113750 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_102005_475940289 | 2017 | Before | 2017-02-09 10:56 | 2017-02-09 12:03 | 1 | 67.15 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown transformer fuse, cause was deteriorated fuse. Refused and customer is back on. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2017-02-09 14:00 | COMPLETED |  | 2017-02-09 10:56 | 2017-02-09 12:17 | 2017-02-09 12:18 | -123.5424 | 46.1864
5A93 | 1734932 | CPCC | CPCC1101711 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | Line Cut-104971 | 2017 | Before | 2017-01-08 13:54 | 2017-01-08 15:33 | 3 | 296.3 | 0 | 0 | 1 | Y | N | N | N | Y | OR Consolidated 01-02-2017 | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Tree limb got caught in the primary. | DISTRIBUTION | DEVICE | AUTO | 2017-01-08 17:00 | COMPLETED |  | 2017-01-08 13:54 | 2017-01-08 18:12 | 2017-01-08 18:13 | -123.6087 | 46.1597
5A93 | 1744719 | CPCC | CPCC1111500 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_176100_1580001881 | 2017 | Before | 2017-02-06 08:10 | 2017-02-06 18:19 | 10 | 6092.167 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | SNOW, SLEET AND BLIZZARD | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: found fuse open on pole 176100; will patrol line PROSPER: Tree; Snow contrib | DISTRIBUTION | DEVICE | MANUAL | 2017-02-06 19:30 | COMPLETED |  | 2017-02-06 08:10 | 2017-02-16 11:40 | 2017-02-06 23:08 | -123.4532 | 46.1723
5A93 | 1755340 | CPCC | CPCC1121192 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_170902_524160337 | 2017 | Before | 2017-03-15 09:16 | 2017-03-15 11:13 | 2 | 232.8 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: replaced transformer fuse | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2017-03-15 12:30 | COMPLETED |  | 2017-03-15 09:17 | 2017-03-15 12:12 | 2017-03-15 12:13 | -123.5877 | 46.184
5A93 | 1762190 | CPCC | CPCC1132480 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_172200_524160298 | 2017 | Before | 2017-04-07 20:33 | 2017-04-07 21:36 | 8 | 498 | 0 | 0 | 1 | Y | N | N | N | Y | OR Consolidated 04-06-2017 | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: wire down, crew made repairs. | DISTRIBUTION | DEVICE | MANUAL | 2017-04-07 23:30 | COMPLETED |  | 2017-04-07 20:33 | 2017-04-08 04:32 | 2017-04-08 04:34 | -123.5835 | 46.1732
5A93 | 1762242 | CPCC | CPCC1129955 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_173802_524160344 | 2017 | Before | 2017-04-07 11:20 | 2017-04-07 14:04 | 155 | 25520.75 | 0 | 0 | 1 | Y | N | N | N | Y | OR Consolidated 04-06-2017 | WEATHER | WIND |  |  | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | SOURCE: patrolled, resolved storm related issue, refused and restored | DISTRIBUTION | DEVICE | AUTO | 2017-04-07 15:45 | COMPLETED |  | 2017-04-07 12:43 | 2017-04-08 04:56 | 2017-04-08 05:00 | -123.5816 | 46.1831
5A93 | 1762246 | CPCC | CPCC1130758 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | Line Cut-106557 | 2017 | Before | 2017-04-07 14:16 | 2017-04-07 21:36 | 3 | 1319.55 | 0 | 0 | 1 | Y | N | N | N | Y | OR Consolidated 04-06-2017 | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: wire down at pole 170100 (1ph) | DISTRIBUTION | DEVICE | MANUAL | 2017-04-07 23:30 | COMPLETED |  | 2017-04-07 14:18 | 2017-04-08 05:00 | 2017-04-08 05:03 | -123.588 | 46.1733
5A93 | 1773167 | CPCC | CPCC1138845 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | RC_202904_1580471805 | 2017 | Before | 2017-05-09 19:39 | 2017-05-09 22:00 | 280 | 39666.667 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | SOURCE: Patrolled line to all other fuse taps, no cause found, closed Field recloser 5A93B at FP 202904 at 2200 - tested good customers restored | DISTRIBUTION | DEVICE | AUTO | 2017-05-09 23:00 | COMPLETED |  | 2017-05-09 19:51 | 2017-05-09 23:21 | 2017-05-09 23:23 | -123.5845 | 46.1701
5A93 | 1755947 | CPCC | CPCC1121571 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_022000_475940270 | 2017 | Before | 2017-03-17 12:06 | 2017-03-17 13:58 | 9 | 1007.25 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman found open line fuse at FP 022000, Patrolling for cause, No Cause Found, refused and holding. all customers restored | DISTRIBUTION | DEVICE | AUTO | 2017-03-17 15:30 | COMPLETED |  | 2017-03-17 12:24 | 2017-03-17 15:43 | 2017-03-17 15:48 | -123.5213 | 46.2005
5A93 | 1771764 | CPCC | CPCC1138111 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_058001_467110036 | 2017 | Before | 2017-05-05 12:52 | 2017-05-05 14:31 | 10 | 992 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Wire down at FP 051903 due to tree, wire put back up. trees cleared and restored all customers PROSPER: change time to first out 05/05/2017 12:51:54, was 05/05/2017 12:07:31 | DISTRIBUTION | DEVICE | AUTO | 2017-05-05 16:00 | COMPLETED |  | 2017-05-05 12:52 | 2017-05-19 12:56 | 2017-05-05 15:48 | -123.4467 | 46.1995
5A93 | 1771878 | CPCC | CPCC1138147 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_170800_524160339 | 2017 | Before | 2017-05-05 20:59 | 2017-05-06 00:28 | 4 | 835.467 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: crew replaced cut out | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2017-05-05 20:59 | 2017-05-06 01:11 | 2017-05-06 01:13 | -123.5871 | 46.1833
5A93 | 1784852 | CPCC | CPCC1146500 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_023500_475940273 | 2017 | Before | 2017-06-15 15:26 | 2017-06-15 17:34 | 33 | 4214.65 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman removed a tree limb from the line and repaired a conductor at F/P 021100 | DISTRIBUTION | DEVICE | AUTO | 2017-06-15 19:15 | COMPLETED |  | 2017-06-15 16:03 | 2017-06-15 17:45 | 2017-06-15 17:48 | -123.52 | 46.2068
5A93 | 1787737 | CPCC | CPCC1147824 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_032500_475940328 | 2017 | Before | 2017-06-24 18:00 | 2017-06-24 18:34 | 1 | 33.967 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | SOURCE: Car hit pole earlier today & noked fuse open -- closed fuse on transformer -- no damage to pole | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2017-06-24 21:00 | COMPLETED |  | 2017-06-24 18:00 | 2017-06-24 18:45 | 2017-06-24 18:48 | -123.5432 | 46.2072
5A93 | 1788393 | CPCC | CPCC1148847 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_033703_475940333 | 2017 | Before | 2017-06-26 13:18 | 2017-06-26 14:42 | 3 | 252.05 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: replaced transformer fuse | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2017-06-26 16:30 | COMPLETED |  | 2017-06-26 13:20 | 2017-06-26 16:26 | 2017-06-26 16:28 | -123.5404 | 46.2099
5A93 | 1794880 | CPCC | CPCC1152774 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_201000_524160571 | 2017 | Before | 2017-07-14 22:21 | 2017-07-15 02:22 | 4 | 961.933 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: crew to repair wire down at fp293800 | DISTRIBUTION | DEVICE | MANUAL | 2017-07-15 04:30 | COMPLETED |  | 2017-07-14 22:22 | 2017-07-15 05:24 | 2017-07-15 05:28 | -123.587 | 46.1564
5A93 | 1796573 | CPCC | CPCC1153762 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_259300_1580247858 | 2017 | Before | 2017-07-19 18:26 | 2017-07-19 18:50 | 40 | 949.333 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | LIGHTNING ARRESTER OH |  |  |  | SOURCE: Blown line fuse caused by B/O arrestor | DISTRIBUTION | DEVICE | AUTO | 2017-07-19 21:45 | COMPLETED |  | 2017-07-19 18:26 | 2017-07-19 20:06 | 2017-07-19 20:08 | -123.6091 | 46.1465
5A93 | 1796607 | CPCC | CPCC1153750 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_302201_524160641 | 2017 | Before | 2017-07-19 16:42 | 2017-07-19 21:44 | 1 | 301.85 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | LIGHTNING ARRESTER OH |  |  |  | SOURCE: Blown riser fuse, caused by B/O arrestor | DISTRIBUTION | DEVICE | MANUAL | 2017-07-19 23:45 | COMPLETED |  | 2017-07-19 16:42 | 2017-07-19 21:48 | 2017-07-19 21:53 | -123.6039 | 46.1445
5A93 | 1800533 | CPCC | CPCC1156053 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_176100_1580001881 | 2017 | Before | 2017-07-31 17:05 | 2017-07-31 18:54 | 10 | 1087.5 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman removed tree limb from line and refused, restored all customers | DISTRIBUTION | DEVICE | AUTO | 2017-07-31 20:15 | COMPLETED |  | 2017-07-31 17:05 | 2017-08-01 04:51 | 2017-08-01 04:53 | -123.4532 | 46.1723
5A93 | 1806066 | CPCC | CPCC1159360 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_081102_475940340 | 2017 | Before | 2017-08-17 08:12 | 2017-08-17 10:25 | 3 | 400.7 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: burnt cut out | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2017-08-17 11:00 | COMPLETED |  | 2017-08-17 08:12 | 2017-08-17 16:02 | 2017-08-17 16:03 | -123.5875 | 46.1874
5A93 | 1806721 | CPCC | CPCC1159857 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_058001_467110036 | 2017 | Before | 2017-08-20 03:00 | 2017-08-20 09:21 | 10 | 3810 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: wire down, crew to make repairs | DISTRIBUTION | DEVICE | MANUAL | 2017-08-20 12:00 | COMPLETED |  | 2017-08-20 03:00 | 2017-08-20 13:29 | 2017-08-20 13:33 | -123.4467 | 46.1995
5A93 | 1815390 | CPCC | CPCC1164764 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_259300_1580247858 | 2017 | Before | 2017-09-20 00:35 | 2017-09-20 09:18 | 42 | 7132.383 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Crew repairing bad underground primary cable | DISTRIBUTION | DEVICE | MANUAL | 2017-09-20 09:44 | COMPLETED |  | 2017-09-20 00:36 | 2017-09-20 09:19 | 2017-09-20 09:23 | -123.6091 | 46.1465
5A93 | 1817368 | CPCC | CPCC1165558 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_173080_524160389 | 2017 | Before | 2017-09-27 00:57 | 2017-09-27 07:03 | 5 | 1829.5 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER PADMOUNT/SUBMERSIBLE UG |  |  |  | SOURCE: B/O padmount xfmr. Transformer changed and all customers restored | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2017-09-27 08:30 | COMPLETED |  | 2017-09-27 00:57 | 2017-09-27 19:49 | 2017-09-27 19:54 | -123.583 | 46.1714
5A93 | 1818166 | CPCC | CPCC1166491 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_109502_1580128764 | 2017 | Before | 2017-10-01 14:21 | 2017-10-01 15:36 | 14 | 1050.7 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: NO CAUSE FOUND | DISTRIBUTION | DEVICE | AUTO | 2017-10-01 19:30 | COMPLETED |  | 2017-10-01 14:22 | 2017-10-01 15:37 | 2017-10-01 15:38 | -123.5282 | 46.1925
5A93 | 1818280 | CPCC | CPCC1166527 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | RC_202904_1580471805 | 2017 | Before | 2017-10-02 06:08 | 2017-10-02 08:52 | 280 | 32679.832 | 0 | 0 | 4 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: recloser at FP 202904 open, patrolling; crew sectionalizing to restore customers; still patrolling; no cause found. | DISTRIBUTION | DEVICE | AUTO | 2017-10-02 11:15 | COMPLETED |  | 2017-10-02 06:13 | 2017-10-02 12:48 | 2017-10-02 12:49 | -123.5845 | 46.1701
5A93 | 1820657 | CPCC | CPCC1167552 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_022000_475940270 | 2017 | Before | 2017-10-10 16:49 | 2017-10-10 18:14 | 9 | 764.1 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown line fuse, cause was tree. Serviceman is going to remove and refuse. Refused and customers are back on. | DISTRIBUTION | DEVICE | AUTO | 2017-10-10 19:45 | COMPLETED |  | 2017-10-10 16:49 | 2017-10-11 00:21 | 2017-10-11 00:23 | -123.5213 | 46.2005
5A93 | 1820684 | CPCC | CPCC1167597 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | RC_202904_1580471805 | 2017 | Before | 2017-10-10 23:07 | 2017-10-11 01:25 | 280 | 31957.267 | 0 | 0 | 2 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Field recloser 5A93B locked open -- patrolled line to fused disconnects@ fp# 173802 & opened -- closed recloser 5A93B & finished patrolling line -- step restored -- no cause | DISTRIBUTION | DEVICE | AUTO | 2017-10-11 04:30 | COMPLETED |  | 2017-10-10 23:08 | 2017-10-11 05:18 | 2017-10-11 05:18 | -123.5845 | 46.1701
5A93 | 1821135 | CPCC | CPCC1167884 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_259401_524160635 | 2017 | Before | 2017-10-12 16:13 | 2017-10-12 17:01 | 1 | 48.267 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: replaced transformer fuse | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2017-10-12 21:15 | COMPLETED |  | 2017-10-12 16:13 | 2017-10-13 03:00 | 2017-10-13 03:03 | -123.609 | 46.1486
5A93 | 1823715 | CPCC | CPCC1169687 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_023500_475940276 | 2017 | Before | 2017-10-21 15:36 | 2017-10-21 22:22 | 24 | 9742.8 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Wire down, caused by tree | DISTRIBUTION | DEVICE | MANUAL | 2017-10-21 23:30 | COMPLETED |  | 2017-10-21 15:36 | 2017-10-22 03:45 | 2017-10-22 03:48 | -123.52 | 46.2069
5A93 | 1823716 | CPCC | CPCC1169823 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2017 | Before | 2017-10-21 21:28 | 2017-10-21 21:28 | 0 | 0 | 903 | 60.2 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: T&R | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2017-10-21 21:28 | 2017-10-22 03:45 | 2017-10-22 03:48 | -123.6231 | 46.1605
5A93 | 1823742 | CPCC | CPCC1169857 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | SB_190800_1580640405 | 2017 | Before | 2017-10-21 22:39 | 2017-10-21 23:10 | 23 | 724.117 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Tree through line | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2017-10-21 22:39 | 2017-10-22 04:59 | 2017-10-22 05:03 | -123.4859 | 46.169
5A93 | 1823755 | CPCC | CPCC1170084 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_360600_237790128 | 2017 | Before | 2017-10-22 03:30 | 2017-10-22 04:27 | 1 | 56.65 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | SOURCE: trees and storm, serviceman reports at 0420 customers in this area have been restored | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2017-10-22 08:30 | COMPLETED |  | 2017-10-22 03:31 | 2017-10-22 05:04 | 2017-10-22 05:08 | -123.5061 | 46.2218
5A93 | 1823756 | CPCC | CPCC1170092 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_355900_237790105 | 2017 | Before | 2017-10-22 03:54 | 2017-10-22 04:28 | 1 | 33.917 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | SOURCE: trees and storm, serviceman reports at 0420 customers in this area have been restored PROSPER: power out | DISTRIBUTION | CUSTOMER | AUTO | 2017-10-22 06:45 | COMPLETED |  | 2017-10-22 03:54 | 2017-10-25 08:56 | 2017-10-22 05:08 | -123.516 | 46.2263
5A93 | 1823709 | CPCC | CPCC1169839 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_173802_524160344 | 2017 | Before | 2017-10-21 21:32 | 2017-10-22 00:58 | 49 | 10077.667 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | SOURCE: tree hazard cleared at 2330 | DISTRIBUTION | DEVICE | AUTO | 2017-10-22 03:15 | COMPLETED |  | 2017-10-21 21:52 | 2017-10-22 03:40 | 2017-10-22 03:43 | -123.5816 | 46.1831
5A93 | 1823886 | CPCC | CPCC1170539 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_176100_1580001881 | 2017 | Before | 2017-10-22 12:07 | 2017-10-22 12:49 | 10 | 422.333 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Took emergency outage due to tree in primary burning. Repairs made and customers are back on. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2017-10-22 12:07 | 2017-10-22 14:13 | 2017-10-22 14:18 | -123.4532 | 46.1723
5A93 | 1825737 | CPCC | CPCC1171478 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_202380_524160312 | 2017 | Before | 2017-10-30 14:22 | 2017-10-30 14:55 | 6 | 201.8 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | PLANNED OUTAGE |  |  |  | SOURCE: Serviceman opened transformer to make emergency repairs | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2017-10-30 19:30 | COMPLETED |  | 2017-10-30 14:22 | 2017-10-30 15:05 | 2017-10-30 15:08 | -123.5854 | 46.1617
5A93 | 1827104 | CPCC | CPCC1172104 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_352603_1580298153 | 2017 | Before | 2017-11-05 07:37 | 2017-11-05 09:13 | 3 | 288.1 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: broken transformer sec jumper | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2017-11-05 10:30 | COMPLETED |  | 2017-11-05 07:37 | 2017-11-05 09:29 | 2017-11-05 09:33 | -123.5212 | 46.2225
5A93 | 1827529 | CPCC | CPCC1172305 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_244500_712540433 | 2017 | Before | 2017-11-06 17:36 | 2017-11-06 22:50 | 11 | 3461.333 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Primary & neutral down -- Tap fuses blown @ fp# 244500 -- ran Arcos for a crew | DISTRIBUTION | DEVICE | MANUAL | 2017-11-07 03:45 | COMPLETED |  | 2017-11-06 18:32 | 2017-11-07 04:07 | 2017-11-07 04:13 | -123.6194 | 46.1632
5A93 | 1827605 | CPCC | CPCC1172438 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_243403_712540464 | 2017 | Before | 2017-11-07 06:57 | 2017-11-07 11:04 | 1 | 247.317 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: found at FP 243403 b/o cutout; crew completed repairs | DISTRIBUTION | DEVICE | MANUAL | 2017-11-07 12:00 | COMPLETED |  | 2017-11-07 06:57 | 2017-11-07 12:27 | 2017-11-07 12:28 | -123.6224 | 46.1627
5A93 | 1828025 | CPCC | CPCC1173131 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2017 | Before | 2017-11-08 16:59 | 2017-11-08 17:33 | 927 | 31023.6 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | SOURCE: tree hazard found on line by serviceman, hazard cleared and no damage to conductor. no FP availble or reported | DISTRIBUTION | DEVICE | MANUAL | 2017-11-08 20:00 | COMPLETED |  | 2017-11-08 16:59 | 2017-11-09 11:44 | 2017-11-08 17:48 | -123.6231 | 46.1605
5A93 | 1828599 | CPCC | CPCC1173435 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_106200_475940283 | 2017 | Before | 2017-11-10 18:03 | 2017-11-10 20:00 | 3 | 352.35 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - TRIMMABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Crew removed tree from line and restored all customers | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2017-11-10 18:03 | 2017-11-11 15:50 | 2017-11-11 15:53 | -123.5355 | 46.1883
5A93 | 1828598 | CPCC | CPCC1173401 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_058001_467110036 | 2017 | Before | 2017-11-10 11:54 | 2017-11-10 14:29 | 10 | 1544.833 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Tap fuse blown -- patrolled line -- no trouble found -- re-fused | DISTRIBUTION | DEVICE | AUTO | 2017-11-10 17:00 | COMPLETED |  | 2017-11-10 11:54 | 2017-11-11 15:50 | 2017-11-11 15:53 | -123.4467 | 46.1995
5A93 | 1828792 | CPCC | CPCC1173787 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_173802_524160344 | 2017 | Before | 2017-11-13 00:54 | 2017-11-13 04:10 | 49 | 9639.117 | 0 | 0 | 1 | Y | N | N | N | Y | OR Coast Plus 11-12-2017 | WEATHER | WIND |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Fuse blown due to Wind and Trees, Refused and holding | DISTRIBUTION | DEVICE | AUTO | 2017-11-13 08:15 | COMPLETED |  | 2017-11-13 03:16 | 2017-11-13 04:11 | 2017-11-13 04:13 | -123.5816 | 46.1831
5A93 | 1828871 | CPCC | CPCC1173786 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | Line Cut-109719 | 2017 | Before | 2017-11-13 01:12 | 2017-11-13 07:31 | 57 | 21604.9 | 0 | 0 | 1 | Y | N | N | N | Y | OR Coast Plus 11-12-2017 | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Wire Down, Crew Needed to make repairs | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2017-11-13 03:14 | 2017-11-13 08:05 | 2017-11-13 08:09 | -123.52 | 46.2068
5A93 | 1829068 | CPCC | CPCC1174163 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_173401_524160380 | 2017 | Before | 2017-11-13 12:40 | 2017-11-13 14:58 | 1 | 137.8 | 0 | 0 | 1 | Y | N | N | N | Y | OR Coast Plus 11-12-2017 | WEATHER | WIND |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: replaced svc PROSPER: power out | DISTRIBUTION | CUSTOMER | MANUAL | 2017-11-13 17:30 | COMPLETED |  | 2017-11-13 12:40 | 2017-11-14 10:18 | 2017-11-13 14:59 | -123.5824 | 46.1765
5A93 | 1829138 | CPCC | CPCC1174245 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_032201_475940308 | 2017 | Before | 2017-11-13 14:49 | 2017-11-13 17:27 | 1 | 157.833 | 0 | 0 | 1 | Y | N | N | N | Y | OR Coast Plus 11-12-2017 | WEATHER | WIND |  |  | CONNECTOR OH |  |  |  | SOURCE: svcman replaced house knob. | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2017-11-13 21:00 | COMPLETED |  | 2017-11-13 14:49 | 2017-11-13 17:27 | 2017-11-13 17:29 | -123.5433 | 46.2031
5A93 | 1829250 | CPCC | CPCC1173739 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_169101_475940214 | 2017 | Before | 2017-11-13 02:14 | 2017-11-13 18:55 | 39 | 39043.55 | 0 | 0 | 1 | Y | N | N | N | Y | OR Coast Plus 11-12-2017 | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: tree through line, crew is assigned. crew is making repairs | DISTRIBUTION | DEVICE | MANUAL | 2017-11-13 21:00 | COMPLETED |  | 2017-11-13 02:14 | 2017-11-14 06:31 | 2017-11-14 06:34 | -123.5486 | 46.1735
5A93 | 1832908 | CPCC | CPCC1176876 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | RC_202800_1580536906 | 2017 | Before | 2017-11-28 23:46 | 2017-11-29 00:58 | 299 | 21602.75 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman patrolled the line and could not find a fault. Closed Field recloserRC 5A93A which held | DISTRIBUTION | DEVICE | AUTO | 2017-11-29 05:00 | COMPLETED |  | 2017-11-28 23:50 | 2017-11-29 14:35 | 2017-11-29 14:39 | -123.584 | 46.168
5A93 | 1836004 | CPCC | CPCC1178477 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_080101_1580514256 | 2017 | Before | 2017-12-14 10:09 | 2017-12-14 11:58 | 1 | 108.433 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: tree rubbed through service wire | DISTRIBUTION | CUSTOMER | AUTO | 2017-12-14 13:00 | COMPLETED |  | 2017-12-14 10:09 | 2017-12-14 14:56 | 2017-12-14 14:59 | -123.5883 | 46.1877
5A93 | 1837197 | CPCC | CPCC1179017 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_259300_1580247858 | 2017 | Before | 2017-12-19 09:46 | 2017-12-19 12:49 | 42 | 3044.734 | 0 | 0 | 2 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Tree through the line, will isolate , restore part of the customers, crew to make repairs | DISTRIBUTION | DEVICE | AUTO | 2017-12-19 15:00 | COMPLETED |  | 2017-12-19 09:48 | 2017-12-20 07:26 | 2017-12-20 07:29 | -123.6091 | 46.1465
5A93 | 1839107 | CPCC | CPCC1181472 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2017 | Before | 2017-12-29 18:52 | 2017-12-29 18:52 | 0 | 0 | 927 | 30.9 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: T&R, suspect wind | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2017-12-29 18:52 | 2017-12-29 23:00 | 2017-12-29 23:03 | -123.6231 | 46.1605
5A93 | 1839962 | CPCC | CPCC1182384 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_201000_524160571 | 2018 | Before | 2018-01-02 12:24 | 2018-01-02 12:33 | 4 | 34.467 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Tree on line, cleared will close fuse on test | DISTRIBUTION | DEVICE | AUTO | 2018-01-02 17:30 | COMPLETED |  | 2018-01-02 12:24 | 2018-01-02 12:41 | 2018-01-02 12:43 | -123.587 | 46.1564
5A93 | 1840831 | CPCC | CPCC1182860 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_300300_524160638 | 2018 | Before | 2018-01-07 15:47 | 2018-01-07 17:10 | 2 | 165.867 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | OTHER, KNOWN CAUSE |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: deteriated fuse, tested transformer, refused and holding | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2018-01-07 18:45 | COMPLETED |  | 2018-01-07 15:47 | 2018-01-07 17:40 | 2018-01-07 17:43 | -123.6083 | 46.1461
5A93 | 1846138 | CPCC | CPCC1187338 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_109502_1580128764 | 2018 | Before | 2018-02-04 12:57 | 2018-02-04 14:00 | 14 | 884.567 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman patrolled the line, no cause found. Replaced blown fuse at F/P 109502 | DISTRIBUTION | DEVICE | AUTO | 2018-02-04 18:00 | COMPLETED |  | 2018-02-04 12:59 | 2018-02-04 18:40 | 2018-02-04 18:43 | -123.5282 | 46.1925
5A93 | 1846837 | CPCC | CPCC1187663 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_246601_712540472 | 2018 | Before | 2018-02-07 18:54 | 2018-02-07 21:09 | 1 | 134.683 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Serviceman repaired a bad cut out at F/P 246601 | DISTRIBUTION | CUSTOMER | AUTO | 2018-02-07 21:45 | COMPLETED |  | 2018-02-07 18:54 | 2018-02-08 12:55 | 2018-02-08 12:59 | -123.6151 | 46.1656
5A93 | 1849722 | CPCC | CPCC1189675 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_194710_524160438 | 2018 | Before | 2018-02-20 18:29 | 2018-02-20 20:20 | 3 | 334.15 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: replaced Cut out | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2018-02-20 21:15 | COMPLETED |  | 2018-02-20 18:29 | 2018-02-21 02:07 | 2018-02-21 02:09 | -123.6005 | 46.1673
5A93 | 1850958 | CPCC | CPCC1191185 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_307600_524160669 | 2018 | Before | 2018-02-26 10:20 | 2018-02-26 10:33 | 13 | 166.617 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: crew to make repairs to bad pri conductor. | DISTRIBUTION | DEVICE | MANUAL | 2018-02-26 15:30 | COMPLETED |  | 2018-02-26 10:20 | 2018-02-26 11:18 | 2018-02-26 11:19 | -123.5922 | 46.1508
5A93 | 1855464 | CPCC | CPCC1194314 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | KNA_CB5A93 | 2018 | Before | 2018-03-15 12:28 | 2018-03-15 12:28 | 0 | 0 | 932 | 31.067 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Trip & Close | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2018-03-15 12:28 | 2018-03-15 12:30 | 2018-03-15 12:33 | -123.6231 | 46.1605
5A93 | 1855836 | CPCC | CPCC1194317 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_172002_524160358 | 2018 | Before | 2018-03-15 12:49 | 2018-03-15 18:40 | 5 | 1755.667 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Crew repaired bad underground primary cable | DISTRIBUTION | DEVICE | MANUAL | 2018-03-15 21:24 | COMPLETED |  | 2018-03-15 12:49 | 2018-03-16 14:08 | 2018-03-16 14:13 | -123.5836 | 46.1714
5A93 | 1869291 | CPCC | CPCC1202411 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_206600_524160510 | 2018 | After | 2018-05-14 14:47 | 2018-05-14 16:10 | 3 | 249.7 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Gary de-energized transfome -- wire down | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2018-05-14 17:00 | COMPLETED |  | 2018-05-14 14:47 | 2018-05-15 13:52 | 2018-05-15 13:55 | -123.5764 | 46.1654
5A93 | 1869961 | CPCC | CPCC1202742 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_197000_524160484 | 2018 | After | 2018-05-18 05:48 | 2018-05-18 14:08 | 4 | 1997.133 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: uh oh, open dip fuse, suspect failed ug primary, crew dispatched by district at start of business day, etr is 16:00 to repairs radial feed urd(08:13 r4r), repaired mast, reconnected service outage restored | DISTRIBUTION | DEVICE | MANUAL | 2018-05-18 16:00 | COMPLETED |  | 2018-05-18 05:48 | 2018-05-18 14:39 | 2018-05-18 14:40 | -123.5926 | 46.1571
5A93 | 1870738 | CPCC | CPCC1203097 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_032205_1580021744 | 2018 | After | 2018-05-22 14:58 | 2018-05-22 16:49 | 35 | 3907.75 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Tap fuse blown -- patrolling line -- no trouble found -- re-fused | DISTRIBUTION | DEVICE | MANUAL | 2018-05-22 20:30 | COMPLETED |  | 2018-05-22 15:10 | 2018-05-22 17:22 | 2018-05-22 17:25 | -123.5423 | 46.2033
5A93 | 1871845 | CPCC | CPCC1203989 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_023500_475940276 | 2018 | After | 2018-05-27 17:06 | 2018-05-27 19:15 | 26 | 3361.367 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: patrolled & refused tap | DISTRIBUTION | DEVICE | MANUAL | 2018-05-27 21:00 | COMPLETED |  | 2018-05-27 18:35 | 2018-05-27 19:16 | 2018-05-27 19:20 | -123.52 | 46.2069
5A93 | 1871931 | CPCC | CPCC1203988 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_023500_475940273 | 2018 | After | 2018-05-27 16:55 | 2018-05-27 20:42 | 33 | 7465.7 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: crew put wire back up in the air. | DISTRIBUTION | DEVICE | MANUAL | 2018-05-27 23:45 | COMPLETED |  | 2018-05-27 18:35 | 2018-05-28 06:13 | 2018-05-28 06:15 | -123.52 | 46.2068
5A93 | 1879016 | CPCC | CPCC1211721 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | SB_156303_1580204317 | 2018 | After | 2018-06-24 18:50 | 2018-06-25 01:06 | 37 | 13901.517 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | POLE OH |  |  |  | SOURCE: reported as Car Hit Pole, Serviceman opened solid blades at FP 156503, actually a tree came down and brought wire down on car that stopped to report the wire down | DISTRIBUTION | DEVICE | MANUAL | 2018-06-25 03:45 | COMPLETED |  | 2018-06-24 18:51 | 2018-06-25 06:31 | 2018-06-25 06:35 | -123.5342 | 46.1758
5A93 | 1880602 | CPCC | CPCC1213053 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_034903_475940334 | 2018 | After | 2018-07-01 07:27 | 2018-07-01 09:49 | 29 | 4132.5 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: , Blown Line Fuse, Tree Limbs in primary, Serviceman to clear and refuse | DISTRIBUTION | DEVICE | MANUAL | 2018-07-01 12:15 | COMPLETED |  | 2018-07-01 09:14 | 2018-07-01 16:01 | 2018-07-01 16:05 | -123.538 | 46.213
5A93 | 1883039 | CPCC | CPCC1214406 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_352602_237790111 | 2018 | After | 2018-07-09 14:10 | 2018-07-09 16:29 | 1 | 139.133 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: sec connectors on neutral as well | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2018-07-09 17:00 | COMPLETED |  | 2018-07-09 14:10 | 2018-07-10 08:20 | 2018-07-10 08:25 | -123.522 | 46.2228
5A93 | 1886373 | CPCC | CPCC1216942 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_356700_237790114 | 2018 | After | 2018-07-19 18:10 | 2018-07-19 23:44 | 14 | 1721.3 | 0 | 0 | 2 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Line Fuse Open, Serviceman to patrol, tree fell on Tap Line at FP 360600, Serviceman isolated and refused. | DISTRIBUTION | DEVICE | MANUAL | 2018-07-20 00:30 | COMPLETED |  | 2018-07-19 18:32 | 2018-07-20 06:38 | 2018-07-20 06:40 | -123.5142 | 46.2241
5A93 | 1889348 | CPCC | CPCC1218674 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_201000_524160571 | 2018 | After | 2018-07-30 17:28 | 2018-07-30 21:02 | 4 | 855.4 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Open line fuse at FP#201000. Patrolling the line. Bad Order Cutout. Callout for crew to replace cutout. | DISTRIBUTION | DEVICE | MANUAL | 2018-07-30 22:15 | COMPLETED |  | 2018-07-30 17:30 | 2018-07-31 05:51 | 2018-07-31 05:55 | -123.587 | 46.1564
5A93 | 1890281 | CPCC | CPCC1219214 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_032205_1580021744 | 2018 | After | 2018-08-03 03:56 | 2018-08-03 05:46 | 84 | 9289 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD SUSPECTED, NO MORTALITY |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: patrolled & refused | DISTRIBUTION | DEVICE | AUTO | 2018-08-03 06:00 | COMPLETED |  | 2018-08-03 04:01 | 2018-08-03 05:51 | 2018-08-03 05:55 | -123.5423 | 46.2033
5A93 | 1900198 | CPCC | CPCC1226881 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_058001_467110036 | 2018 | After | 2018-09-12 17:52 | 2018-09-12 19:41 | 10 | 1089.667 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Line Fuse Open, Serviceman patrolled and found no cause, will close fuse on test | DISTRIBUTION | DEVICE | AUTO | 2018-09-12 20:45 | COMPLETED |  | 2018-09-12 17:52 | 2018-09-13 06:58 | 2018-09-13 07:00 | -123.4467 | 46.1995
5A93 | 1902465 | CPCC | CPCC1230424 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | SB_190800_1580640405 | 2018 | After | 2018-09-22 11:04 | 2018-09-22 11:28 | 23 | 545.1 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Opened solid blade SW's to remove tree that fell on line -- no match call report # 2974713 | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2018-09-22 11:04 | 2018-09-22 16:43 | 2018-09-22 16:45 | -123.4859 | 46.169
5A93 | 1906219 | CPCC | CPCC1232822 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_163580_467110110 | 2018 | After | 2018-10-09 13:33 | 2018-10-09 13:57 | 2 | 48.166 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Called by radio and phone 1341 Phill Lutze had to open cut outs at FP 195900 for fire due to tree on the line | DISTRIBUTION | CUSTOMER | AUTO | 2018-10-09 16:00 | COMPLETED |  | 2018-10-09 13:33 | 2018-10-10 09:21 | 2018-10-09 14:10 | -123.4374 | 46.1777
5A93 | 1908774 | CPCC | CPCC1234366 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_022000_475940270 | 2018 | After | 2018-10-21 16:20 | 2018-10-21 16:58 | 9 | 336.15 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | SOURCE: Connector failure, wire re-hung and customers energized | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2018-10-21 16:20 | 2018-10-21 16:59 | 2018-10-21 17:00 | -123.5213 | 46.2005
5A93 | 1909164 | CPCC | CPCC1234535 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_022000_475940270 | 2018 | After | 2018-10-23 10:16 | 2018-10-23 10:46 | 9 | 270.45 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Stranded Primary Conductor, Crew opened fuse to repair | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2018-10-23 10:16 | 2018-10-23 16:23 | 2018-10-23 16:25 | -123.5213 | 46.2005
5A93 | 1910281 | CPCC | CPCC1235400 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_173802_524160344 | 2018 | After | 2018-10-28 16:14 | 2018-10-28 19:05 | 67 | 11475.983 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: Broken jumper at FP 174902, Crew to repair | DISTRIBUTION | DEVICE | MANUAL | 2018-10-28 21:00 | COMPLETED |  | 2018-10-28 16:55 | 2018-10-28 20:22 | 2018-10-28 20:25 | -123.5816 | 46.1831
5A93 | 1910280 | CPCC | CPCC1235414 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_173802_524160344 | 2018 | After | 2018-10-28 17:39 | 2018-10-28 19:03 | 91 | 7647.033 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | PLANNED OUTAGE |  |  |  | SOURCE: Opened last fuse to facilitate repairs on Outage 1235400 | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2018-10-28 17:39 | 2018-10-28 20:22 | 2018-10-28 20:25 | -123.5816 | 46.1831
5A93 | 1911526 | CPCC | CPCC1236500 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | SB_190800_1580640405 | 2018 | After | 2018-11-04 06:11 | 2018-11-04 09:41 | 23 | 4845.717 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | CONNECTOR OH |  |  |  | SOURCE: repaired and rehung | DISTRIBUTION | DEVICE | MANUAL | 2018-11-04 11:00 | COMPLETED |  | 2018-11-04 06:12 | 2018-11-04 11:39 | 2018-11-04 11:45 | -123.4859 | 46.169
5A93 | 1911495 | CPCC | CPCC1236494 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_173802_524160344 | 2018 | After | 2018-11-04 03:53 | 2018-11-04 06:21 | 49 | 7250.367 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Line fuse open, patrolling for cause, No cause found, re-fused and restored | DISTRIBUTION | DEVICE | MANUAL | 2018-11-04 08:30 | COMPLETED |  | 2018-11-04 04:16 | 2018-11-04 06:25 | 2018-11-04 06:30 | -123.5816 | 46.1831
5A93 | 1913065 | CPCC | CPCC1237350 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_201800_1580549254 | 2018 | After | 2018-11-12 06:21 | 2018-11-12 10:07 | 44 | 9954.069 | 0 | 0 | 2 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: found 1 fuse blown. Primary wire down. | DISTRIBUTION | DEVICE | MANUAL | 2018-11-12 11:30 | COMPLETED |  | 2018-11-12 06:21 | 2018-11-13 09:10 | 2018-11-12 14:10 | -123.5868 | 46.1674
5A93 | 1913064 | CPCC | CPCC1237439 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_201800_1580549254 | 2018 | After | 2018-11-12 09:23 | 2018-11-12 10:07 | 92 | 4106.267 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | TREES | TREE - NON-PREVENTABLE | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Associated to outage 1237350. Took outage to make repairs to wire down. | DISTRIBUTION | DEVICE | MANUAL | 2018-11-12 11:30 | COMPLETED |  | 2018-11-12 09:23 | 2018-11-12 14:07 | 2018-11-12 14:10 | -123.5868 | 46.1674
5A93 | 1917189 | CPCC | CPCC1243762 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_157600_475940192 | 2018 | After | 2018-12-01 07:45 | 2018-12-01 09:38 | 1 | 112.417 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: serviceman reports that the fuse had broken, refused the cutout and customer is back in service | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2018-12-01 10:30 | COMPLETED |  | 2018-12-01 07:45 | 2018-12-01 11:53 | 2018-12-01 11:55 | -123.5331 | 46.1795
5A93 | 1917739 | CPCC | CPCC1244077 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_169101_475940214 | 2018 | After | 2018-12-04 06:38 | 2018-12-04 10:55 | 39 | 10019.75 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | POLE OH |  |  |  | SOURCE: Car hit pole - called for crew | DISTRIBUTION | DEVICE | MANUAL | 2018-12-04 12:45 | COMPLETED |  | 2018-12-04 06:38 | 2018-12-04 12:23 | 2018-12-04 12:25 | -123.5486 | 46.1735
5A93 | 1918796 | CPCC | CPCC1244925 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | Line Cut-116011 | 2018 | After | 2018-12-08 21:32 | 2018-12-09 01:19 | 23 | 5224.45 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Tree thru Line, 2 Spans of all 3 Phases down, Crew to repair | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2018-12-08 21:58 | 2018-12-09 05:59 | 2018-12-09 06:00 | -123.4614 | 46.1698
5A93 | 1920135 | CPCC | CPCC1249487 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_354800_237790104 | 2018 | After | 2018-12-14 17:48 | 2018-12-14 19:46 | 1 | 118.217 | 0 | 0 | 1 | Y | N | N | N | Y | OR Consolidated 12-14-2018 | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Burned up meter, serviceman replaced and restored | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2018-12-14 23:45 | COMPLETED |  | 2018-12-14 17:48 | 2018-12-14 20:10 | 2018-12-14 20:10 | -123.5167 | 46.2253
5A93 | 1920252 | CPCC | CPCC1249496 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_173802_524160344 | 2018 | After | 2018-12-14 17:50 | 2018-12-14 21:10 | 34 | 6794.333 | 0 | 0 | 1 | Y | N | N | N | Y | OR Consolidated 12-14-2018 | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Line Fuse open due to trees and wind, Replaced and restored | DISTRIBUTION | DEVICE | MANUAL | 2018-12-14 23:45 | COMPLETED |  | 2018-12-14 17:56 | 2018-12-15 00:01 | 2018-12-15 00:05 | -123.5816 | 46.1831
5A93 | 1921246 | CPCC | CPCC1250357 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_201800_1580549254 | 2018 | After | 2018-12-17 22:35 | 2018-12-18 02:03 | 135 | 28091.25 | 0 | 0 | 1 | Y | N | N | N | Y | OR Consolidated 12-17-2018 | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: All repairs completed, customers restored | DISTRIBUTION | DEVICE | MANUAL | 2018-12-18 03:00 | COMPLETED |  | 2018-12-17 22:43 | 2018-12-18 02:08 | 2018-12-18 02:10 | -123.5868 | 46.1674
5A93 | 1921251 | CPCC | CPCC1250409 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_173802_524160344 | 2018 | After | 2018-12-17 23:08 | 2018-12-18 01:09 | 50 | 6088.333 | 0 | 0 | 1 | Y | N | N | N | Y | OR Consolidated 12-17-2018 | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Line Fuse Open, Serviceman patrolling for cause, no damage, suspect high winds and or tree limb contacting line, closed and restored | DISTRIBUTION | DEVICE | AUTO | 2018-12-18 02:00 | COMPLETED |  | 2018-12-17 23:08 | 2018-12-18 02:08 | 2018-12-18 02:10 | -123.5816 | 46.1831
5A93 | 1921595 | CPCC | CPCC1251074 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_169101_475940214 | 2018 | After | 2018-12-18 12:28 | 2018-12-18 14:56 | 39 | 5804.5 | 0 | 0 | 1 | Y | N | N | N | Y | OR Consolidated 12-17-2018 | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Emergency outage taken to make repairs to conductor | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2018-12-18 12:28 | 2018-12-18 16:34 | 2018-12-18 16:35 | -123.5486 | 46.1735
5A93 | 1922059 | CPCC | CPCC1251482 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_201800_1580549254 | 2018 | After | 2018-12-20 10:04 | 2018-12-20 13:23 | 135 | 26833.5 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Tree through line caused by wind, at pole 200100 | DISTRIBUTION | DEVICE | MANUAL | 2018-12-20 15:00 | COMPLETED |  | 2018-12-20 10:05 | 2018-12-20 13:51 | 2018-12-20 13:55 | -123.5868 | 46.1674
5A93 | 1922082 | CPCC | CPCC1251473 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_173802_524160344 | 2018 | After | 2018-12-20 09:42 | 2018-12-20 14:10 | 158 | 42423 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Tree through line, wire down 084201 | DISTRIBUTION | DEVICE | MANUAL | 2018-12-20 15:00 | COMPLETED |  | 2018-12-20 09:51 | 2018-12-20 15:09 | 2018-12-20 15:10 | -123.5816 | 46.1831
5A93 | 1922107 | CPCC | CPCC1251552 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_342206_237790084 | 2018 | After | 2018-12-20 14:50 | 2018-12-20 17:12 | 10 | 845 | 0 | 0 | 2 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Tree through the line at Pole 137209. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2018-12-20 14:58 | 2018-12-20 17:14 | 2018-12-20 17:15 | -123.5421 | 46.218
5A93 | 1922156 | CPCC | CPCC1251541 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | SB_190800_1580640405 | 2018 | After | 2018-12-20 08:52 | 2018-12-20 19:45 | 23 | 15035.1 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | CONNECTOR OH |  |  |  | SOURCE: Wire down at 173801 | DISTRIBUTION | DEVICE | MANUAL | 2018-12-20 20:30 | COMPLETED |  | 2018-12-20 13:48 | 2018-12-20 19:46 | 2018-12-20 19:50 | -123.4859 | 46.169
5A93 | 1925950 | CPCC | CPCC1254583 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_173802_524160344 | 2019 | After | 2019-01-05 23:50 | 2019-01-06 22:51 | 158 | 218305.967 | 0 | 0 | 1 | Y | N | N | N | Y | OR Consolidated 01-05-2019 | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Wire down near 083102. Fuses open at pole 173801. 12 spans of wire down btwn poles 084201-090801 | DISTRIBUTION | DEVICE | MANUAL | 2019-01-07 01:00 | COMPLETED |  | 2019-01-06 00:05 | 2019-01-06 23:49 | 2019-01-06 23:55 | -123.5816 | 46.1831
5A93 | 1925904 | CPCC | CPCC1254600 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_211901_1580419438 | 2019 | After | 2019-01-05 23:52 | 2019-01-06 12:08 | 103 | 75840.617 | 0 | 0 | 1 | Y | N | N | N | Y | OR Consolidated 01-05-2019 | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: | DISTRIBUTION | DEVICE | MANUAL |  | COMPLETED |  | 2019-01-06 00:22 | 2019-01-06 18:37 | 2019-01-06 18:40 | -123.5662 | 46.1699
5A93 | 1925903 | CPCC | CPCC1254558 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_201800_1580549254 | 2019 | After | 2019-01-05 23:45 | 2019-01-06 12:06 | 135 | 100091.25 | 0 | 0 | 1 | Y | N | N | N | Y | OR Consolidated 01-05-2019 | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: | DISTRIBUTION | DEVICE | MANUAL |  | COMPLETED |  | 2019-01-05 23:45 | 2019-01-06 18:36 | 2019-01-06 18:40 | -123.5868 | 46.1674
5A93 | 1925982 | CPCC | CPCC1254859 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_307600_524160669 | 2019 | After | 2019-01-06 12:08 | 2019-01-07 01:10 | 13 | 10174.883 | 0 | 0 | 1 | Y | N | N | N | Y | OR Consolidated 01-05-2019 | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: 3 spans wire down, crossarm, tree crew just finished | DISTRIBUTION | DEVICE | MANUAL | 2019-01-07 03:00 | COMPLETED |  | 2019-01-06 12:08 | 2019-01-07 15:33 | 2019-01-07 05:30 | -123.5922 | 46.1508
5A93 | 1926023 | CPCC | CPCC1254860 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | SB_190800_1580640405 | 2019 | After | 2019-01-06 12:08 | 2019-01-07 09:35 | 23 | 29585.667 | 0 | 0 | 1 | Y | N | N | N | Y | OR Consolidated 01-05-2019 | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Patroling, tree crew needs to remove tree. | DISTRIBUTION | DEVICE | MANUAL | 2019-01-07 12:00 | COMPLETED |  | 2019-01-06 12:08 | 2019-01-07 15:33 | 2019-01-07 09:40 | -123.4859 | 46.169
5A93 | 1927558 | CPCC | CPCC1256235 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_201000_524160571 | 2019 | After | 2019-01-14 19:00 | 2019-01-15 00:45 | 4 | 1379.067 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Left message on first call, called again 15 minutes later, will wait 15 and start call-out. Gary Dick accepted callout. Tree on line. | DISTRIBUTION | DEVICE | MANUAL | 2019-01-15 03:00 | COMPLETED |  | 2019-01-14 19:00 | 2019-01-15 00:46 | 2019-01-15 00:50 | -123.587 | 46.1564
5A93 | 1927666 | CPCC | CPCC1256287 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_210903_475940346 | 2019 | After | 2019-01-15 11:42 | 2019-01-15 14:50 | 24 | 4504 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: limbs found across conductors pole 162202 | DISTRIBUTION | DEVICE | MANUAL | 2019-01-15 16:00 | COMPLETED |  | 2019-01-15 12:41 | 2019-01-15 14:50 | 2019-01-15 14:55 | -123.5676 | 46.1704
5A93 | 1934962 | CPCC | CPCC1261171 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_058001_467110036 | 2019 | After | 2019-02-12 01:24 | 2019-02-12 06:31 | 10 | 3077.167 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: remove the limb | DISTRIBUTION | DEVICE | MANUAL | 2019-02-12 09:00 | COMPLETED |  | 2019-02-12 01:24 | 2019-02-12 06:38 | 2019-02-12 06:40 | -123.4467 | 46.1995
5A93 | 1936279 | CPCC | CPCC1262629 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | OH_346700_237790077 | 2019 | After | 2019-02-14 18:46 | 2019-02-14 20:46 | 11 | 1324.95 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: 2 open fused @ 346700, patroling, no cause found, replaced and restored | DISTRIBUTION | DEVICE | MANUAL | 2019-02-14 23:00 | COMPLETED |  | 2019-02-14 18:46 | 2019-02-15 03:52 | 2019-02-15 03:55 | -123.5324 | 46.2238
5A93 | 1937689 | CPCC | CPCC1263530 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_176180_524160326 | 2019 | After | 2019-02-20 16:29 | 2019-02-20 19:52 | 1 | 203.583 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | SOURCE: BO Meter | DISTRIBUTION | CUSTOMER | MANUAL | 2019-02-20 21:30 | COMPLETED |  | 2019-02-20 16:29 | 2019-02-20 22:38 | 2019-02-20 22:40 | -123.5751 | 46.1721
5A93 | 1938352 | CPCC | CPCC1263868 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_050902_467110030 | 2019 | After | 2019-02-24 07:28 | 2019-02-24 07:53 | 1 | 24.683 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - TRIMMABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Branch into line, removed and re-fused, customer in service. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2019-02-24 09:45 | COMPLETED |  | 2019-02-24 07:28 | 2019-02-24 08:57 | 2019-02-24 09:00 | -123.4658 | 46.211
5A93 | 1938353 | CPCC | CPCC1263850 | PP | OR | CLATSOP (ASTORIA) | KNAPPA SVENSEN | TR_069900_467110029 | 2019 | After | 2019-02-24 05:55 | 2019-02-24 07:50 | 1 | 114.833 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - TRIMMABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Branch into line, removed and re-fused, customer in service. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2019-02-24 05:56 | 2019-02-24 08:57 | 2019-02-24 09:00 | -123.4678 | 46.2112
5K50 | 597505 | CPCC | CPCC392361 | PP | OR | HOOD RIVER | KENWOOD | RC_292460_278580237 | 2007 | Before | 2007-01-06 01:38 | 2007-01-06 07:52 | 277 | 103667.25 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: crew to remove tree, put wire back up & close field recloser | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.6023 | 45.6261
5K50 | 599405 | CPCC | CPCC392651 | PP | OR | HOOD RIVER | KENWOOD | TR_364600_981200011 | 2007 | Before | 2007-01-07 15:59 | 2007-01-08 01:53 | 1 | 593.4 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: tree took down primary | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 602743 | CPCC | CPCC396609 | PP | OR | HOOD RIVER | KENWOOD | OH_072300_970000038 | 2007 | Before | 2007-01-26 21:04 | 2007-01-26 22:25 | 31 | 2520.3 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: fuses opened on pole to isolate wire down | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.6256 | 45.5835
5K50 | 602744 | CPCC | CPCC396612 | PP | OR | HOOD RIVER | KENWOOD | LINECUT-22103 | 2007 | Before | 2007-01-26 22:25 | 2007-01-27 05:20 | 14 | 5818.867 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | POLE OH |  |  |  | PROSPER: replaced pole & wire | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.6354 | 45.5781
5K50 | 598859 | CPCC | CPCC392560 | PP | OR | HOOD RIVER | KENWOOD | OH_127400_20360153 | 2007 | Before | 2007-01-07 08:38 | 2007-01-07 16:16 | 82 | 15931.7 | 0 | 0 | 2 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Tree through line, fuses on pole 127400 were blown. Cut jumpers on pole 132300. Refused pole 127400. Replace primary wire. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.6367 | 45.5853
5K50 | 598860 | CPCC | CPCC392561 | PP | OR | HOOD RIVER | KENWOOD | TR_061602_970000075 | 2007 | Before | 2007-01-07 09:06 | 2007-01-07 12:20 | 1 | 194.317 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Broken neutral, made repairs customers back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 598861 | CPCC | CPCC392563 | PP | OR | HOOD RIVER | KENWOOD | TR_061401_970000076 | 2007 | Before | 2007-01-07 09:21 | 2007-01-07 12:21 | 1 | 180.1 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Broken neutral, made repairs customers back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 598862 | CPCC | CPCC392565 | PP | OR | HOOD RIVER | KENWOOD | TR_137001_20360121 | 2007 | Before | 2007-01-07 09:25 | 2007-01-07 11:26 | 5 | 604.667 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Associated with outage 392560. Bad connectivity in Cadops. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 598863 | CPCC | CPCC392566 | PP | OR | HOOD RIVER | KENWOOD | TR_128600_20360143 | 2007 | Before | 2007-01-07 09:29 | 2007-01-07 11:26 | 1 | 117.083 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Associated with outage 392560. Bad connectivity in Cadops. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 598868 | CPCC | CPCC392574 | PP | OR | HOOD RIVER | KENWOOD | TR_136900_20360222 | 2007 | Before | 2007-01-07 10:06 | 2007-01-07 11:26 | 1 | 80.45 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Associated with outage 392560. Bad connectivity in Cadops. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 603444 | CPCC | CPCC400038 | PP | OR | HOOD RIVER | KENWOOD | RC_292460_278580237 | 2007 | Before | 2007-02-19 22:30 | 2007-02-20 03:52 | 277 | 89434.067 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Tree through line | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.6023 | 45.6261
5K50 | 620398 | CPCC | CPCC421142 | PP | OR | HOOD RIVER | KENWOOD | TR_176802_278580346 | 2007 | Before | 2007-06-06 16:19 | 2007-06-06 17:29 | 1 | 69.65 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | INTERFERENCE | VEHICLE ACCIDENT | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: dump truck tore down primary neut. crew made repairs. customer is back in full service. Could not model due to the fact cadops did not show any customers on the transformer. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 617383 | CPCC | CPCC419275 | PP | OR | HOOD RIVER | KENWOOD | TR_131800_20360189 | 2007 | Before | 2007-05-24 17:59 | 2007-05-24 18:53 | 1 | 54.7 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Fuse pulled apart. Refused and customer back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 614958 | CPCC | CPCC418866 | PP | OR | HOOD RIVER | KENWOOD | TR_100903_64090349 | 2007 | Before | 2007-05-23 17:14 | 2007-05-23 18:22 | 1 | 68.317 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Refused and customer back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 617405 | CPCC | CPCC419632 | PP | OR | HOOD RIVER | KENWOOD | TR_101800_64090350 | 2007 | Before | 2007-05-27 13:05 | 2007-05-27 14:14 | 1 | 69.517 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman found open cutout, will check and refuse. Pole #101800. one customer off. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 625731 | CPCC | CPCC428297 | PP | OR | HOOD RIVER | KENWOOD | TR_130301_20360179 | 2007 | Before | 2007-07-12 13:38 | 2007-07-12 14:45 | 1 | 66.8 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: squirrel on trf caused the cutout fuse to blow. squirrel cleared, fuse replaced and customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 629032 | CPCC | CPCC428481 | PP | OR | HOOD RIVER | KENWOOD | TR_107511_64090358 | 2007 | Before | 2007-07-13 07:29 | 2007-07-13 07:55 | 3 | 76.2 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Servicman refused transformer# 107511 and it held, the cuase was a squirrel, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 610903 | CPCC | CPCC414839 | PP | OR | HOOD RIVER | KENWOOD | TR_047801_988340552 | 2007 | Before | 2007-04-18 14:56 | 2007-04-18 15:27 | 1 | 30.383 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: associate to outage #414842, b/o connectivity in cadops. tagging installed in cadops. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 610904 | CPCC | CPCC414840 | PP | OR | HOOD RIVER | KENWOOD | TR_090402_64090650 | 2007 | Before | 2007-04-18 14:58 | 2007-04-18 15:25 | 1 | 27.733 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: associate to outage #414842, b/o connectivity in cadops. tagging installed in cadops. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 610905 | CPCC | CPCC414842 | PP | OR | HOOD RIVER | KENWOOD | OH_160501_64090671 | 2007 | Before | 2007-04-18 14:58 | 2007-04-18 15:26 | 64 | 1847.467 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: svcmen making repairs to jumper that melted off at the hot tap. possible that fault current caused this but not confirmed at this time. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.586 | 45.6573
5K50 | 607413 | CPCC | CPCC410539 | PP | OR | HOOD RIVER | KENWOOD | TR_297801_278580254 | 2007 | Before | 2007-03-16 21:04 | 2007-03-17 03:45 | 1 | 401.067 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: bad order underground | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 608228 | CPCC | CPCC410991 | PP | OR | HOOD RIVER | KENWOOD | TR_128600_20360143 | 2007 | Before | 2007-03-20 09:20 | 2007-03-20 10:24 | 1 | 64.583 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: vehicle hit down guy which caused service wire to break and fall to ground. svcman made repairs and customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 610369 | CPCC | CPCC415121 | PP | OR | HOOD RIVER | KENWOOD | TR_203260_278580435 | 2007 | Before | 2007-04-21 15:53 | 2007-04-22 05:20 | 1 | 806.35 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | OTHER UTILITY/CONTRACTOR |  |  | POLE OH |  |  |  | PROSPER: customer toer done pole with back hoe | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 610370 | CPCC | CPCC415122 | PP | OR | HOOD RIVER | KENWOOD | TR_207760_278580428 | 2007 | Before | 2007-04-21 15:57 | 2007-04-22 05:20 | 1 | 803.083 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | OTHER UTILITY/CONTRACTOR |  |  | POLE OH |  |  |  | PROSPER: customer tore done pole with back hoe | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 610371 | CPCC | CPCC415125 | PP | OR | HOOD RIVER | KENWOOD | LINECUT-22973 | 2007 | Before | 2007-04-21 15:58 | 2007-04-22 05:20 | 11 | 8818.7 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | OTHER UTILITY/CONTRACTOR |  |  | POLE OH |  |  |  | PROSPER: customer tore done pole with back hoe | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.591 | 45.6464
5K50 | 649709 | CPCC | CPCC457656 | PP | OR | HOOD RIVER | KENWOOD | TR_291301_278580386 | 2007 | Before | 2007-11-29 01:04 | 2007-11-29 03:04 | 1 | 120.517 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | SNOW, SLEET AND BLIZZARD |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: line down blown fuse | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 649710 | CPCC | CPCC457657 | PP | OR | HOOD RIVER | KENWOOD | Line Cut-26403 | 2007 | Before | 2007-11-29 02:35 | 2007-11-29 07:20 | 18 | 805.716 | 0 | 0 | 2 | Y | N | N | N | N |  | WEATHER | SNOW, SLEET AND BLIZZARD |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Crew made repairs to the overhead primary that burnt down due to wet heavy snow. Customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.6027 | 45.6254
5K50 | 649923 | CPCC | CPCC455819 | PP | OR | HOOD RIVER | KENWOOD | TR_185100_970000046 | 2007 | Before | 2007-11-19 04:18 | 2007-11-19 09:10 | 1 | 291.883 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | SNOW, SLEET AND BLIZZARD |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: associate to 455812, bad connectivity in cadops. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 649931 | CPCC | CPCC455850 | PP | OR | HOOD RIVER | KENWOOD | OH_185401_970000044 | 2007 | Before | 2007-11-19 08:39 | 2007-11-19 13:02 | 13 | 3418.567 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | SNOW, SLEET AND BLIZZARD |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: snow loading on primary conductors. crew patrolling line. crew reports wire down. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.6185 | 45.5697
5K50 | 649984 | CPCC | CPCC457704 | PP | OR | HOOD RIVER | KENWOOD | Line Cut-26413 | 2007 | Before | 2007-11-29 08:49 | 2007-11-29 11:50 | 4 | 721.8 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | SNOW, SLEET AND BLIZZARD |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: crew to put broken primary wire back up. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.5996 | 45.6491
5K50 | 649654 | CPCC | CPCC455803 | PP | OR | HOOD RIVER | KENWOOD | OH_310302_278580242 | 2007 | Before | 2007-11-19 00:42 | 2007-11-19 01:12 | 7 | 205.217 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.6244 | 45.6113
5K50 | 649657 | CPCC | CPCC455812 | PP | OR | HOOD RIVER | KENWOOD | Line Cut-26213 | 2007 | Before | 2007-11-19 02:38 | 2007-11-19 13:02 | 6 | 3741.5 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | SNOW, SLEET AND BLIZZARD |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: tree took down primary | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.6159 | 45.5665
5K50 | 649660 | CPCC | CPCC455816 | PP | OR | HOOD RIVER | KENWOOD | TR_186301_970000058 | 2007 | Before | 2007-11-19 03:50 | 2007-11-19 09:10 | 1 | 319.117 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | SNOW, SLEET AND BLIZZARD |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: associate to 455812, bad connectivity in cadops. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 642263 | CPCC | CPCC442186 | PP | OR | HOOD RIVER | KENWOOD | TR_125001_20360165 | 2007 | Before | 2007-09-13 18:02 | 2007-09-13 19:22 | 5 | 399.75 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Associated to outage 442188. Cadops did not have the line fuses that blew. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 642264 | CPCC | CPCC442188 | PP | OR | HOOD RIVER | KENWOOD | TR_135900_20360217 | 2007 | Before | 2007-09-13 18:00 | 2007-09-13 19:22 | 1 | 81.733 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Line fuse blew, serviceman says wind was blown and there is some tree debree on the ground. Refused and customers are back on.. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 652225 | CPCC | CPCC461166 | PP | OR | HOOD RIVER | KENWOOD | OH_160501_64090671 | 2007 | Before | 2007-12-02 22:36 | 2007-12-03 02:11 | 213 | 45736.45 | 0 | 0 | 2 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Line fuse blown. No cause found. Refused and customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.586 | 45.6573
5K50 | 652775 | CPCC | CPCC459850 | PP | OR | HOOD RIVER | KENWOOD | OH_185401_970000044 | 2007 | Before | 2007-12-02 15:47 | 2007-12-02 22:21 | 19 | 7483.15 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Primary wire down. Crew needed. Repairs have been made, Customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.6185 | 45.5697
5K50 | 652411 | CPCC | CPCC455766 | PP | OR | HOOD RIVER | KENWOOD | TR_364600_981200011 | 2007 | Before | 2007-11-18 20:42 | 2007-11-19 01:11 | 1 | 268.9 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 652416 | CPCC | CPCC455800 | PP | OR | HOOD RIVER | KENWOOD | OH_185401_970000044 | 2007 | Before | 2007-11-18 23:55 | 2007-11-19 02:39 | 19 | 3078.55 | 0 | 0 | 3 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.6185 | 45.5697
5K50 | 665284 | CPCC | CPCC487886 | PP | OR | HOOD RIVER | KENWOOD | TR_168961_64090689 | 2008 | Before | 2008-02-05 20:55 | 2008-02-05 21:59 | 1 | 63.633 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 666641 | CPCC | CPCC486893 | PP | OR | HOOD RIVER | KENWOOD | Line Cut-27598 | 2008 | Before | 2008-02-02 18:07 | 2008-02-02 22:16 | 25 | 6220 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - TRIMMABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: called out crew to rehang primary. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.621 | 45.5748
5K50 | 666647 | CPCC | CPCC486905 | PP | OR | HOOD RIVER | KENWOOD | TR_073001_970000039 | 2008 | Before | 2008-02-02 18:13 | 2008-02-02 22:16 | 1 | 242.917 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - TRIMMABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Associated with outage # 486893. called out crew to rehang primary. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 668271 | CPCC | CPCC494081 | PP | OR | HOOD RIVER | KENWOOD | Line Cut-28420 | 2008 | Before | 2008-03-29 00:01 | 2008-03-29 01:25 | 236 | 20028.533 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | POLE OH |  |  |  | PROSPER: Had a car hit pole, had to take the outage to make repairs to the pole. Repairs have been made and customers are back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.6122 | 45.6187
5K50 | 669082 | CPCC | CPCC491857 | PP | OR | HOOD RIVER | KENWOOD | TR_310203_278580487 | 2008 | Before | 2008-03-10 19:29 | 2008-03-10 20:50 | 2 | 161.9 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Found deteriorated fuse, replaced, power restored | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 680269 | CPCC | CPCC510456 | PP | OR | HOOD RIVER | KENWOOD | TR_179104_278580310 | 2008 | Before | 2008-07-04 03:30 | 2008-07-04 04:06 | 1 | 35.467 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Blown transformer fuse due to lightning. Refused and customers are aback on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 680003 | CPCC | CPCC510447 | PP | OR | HOOD RIVER | KENWOOD | TR_208960_278580419 | 2008 | Before | 2008-07-04 01:02 | 2008-07-04 02:01 | 3 | 174.8 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Transformer fuse blew due to lightning.Refused and customer is back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 679664 | CPCC | CPCC505467 | PP | OR | HOOD RIVER | KENWOOD | TR_137406_20360208 | 2008 | Before | 2008-06-09 21:22 | 2008-06-10 00:01 | 1 | 158.883 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Fuse blown on transformer. Broken fuse. Refused and customer is back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 679675 | CPCC | CPCC505572 | PP | OR | HOOD RIVER | KENWOOD | OH_100001_64090391 | 2008 | Before | 2008-06-10 07:51 | 2008-06-10 07:58 | 27 | 203.85 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: tree removed from oh | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.5651 | 45.664
5K50 | 682951 | CPCC | CPCC509366 | PP | OR | HOOD RIVER | KENWOOD | TR_137406_20360208 | 2008 | Before | 2008-06-29 17:30 | 2008-06-29 19:04 | 7 | 657.767 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD SUSPECTED, NO MORTALITY |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: refused | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 682954 | CPCC | CPCC509369 | PP | OR | HOOD RIVER | KENWOOD | TR_123300_20360158 | 2008 | Before | 2008-06-29 18:11 | 2008-06-29 19:53 | 1 | 102.083 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: refused | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 678973 | CPCC | CPCC502828 | PP | OR | HOOD RIVER | KENWOOD | OH_100001_64090391 | 2008 | Before | 2008-05-20 19:21 | 2008-05-20 22:48 | 38 | 7879.933 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | OTHER, KNOWN CAUSE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: SWAT team request that power be turned off unable to get close to transformer so we had to open line fuse turning off 37 customers | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.5651 | 45.664
5K50 | 679799 | CPCC | CPCC502856 | PP | OR | HOOD RIVER | KENWOOD | TR_185100_970000047 | 2008 | Before | 2008-05-21 08:51 | 2008-05-21 13:12 | 1 | 261.683 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | SECONDARY CABLE UG |  |  |  | PROSPER: Crew repaired B/O underground service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 660655 | CPCC | CPCC479016 | PP | OR | HOOD RIVER | KENWOOD | OH_089403_278580270 | 2008 | Before | 2008-01-14 16:24 | 2008-01-14 17:44 | 38 | 3032.4 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Line down beterrn 082500 # 083401, blew line fuse @ 082500, not found in cad ops, showed by opening at 089403 | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.5864 | 45.6713
5K50 | 662026 | CPCC | CPCC448986 | PP | OR | HOOD RIVER | KENWOOD | LINECUT-25724 | 2007 | Before | 2007-10-19 07:13 | 2007-10-19 09:05 | 3 | 334.55 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: svcmen removed trees from line and all customers are back in full service. per customers we were in here trimming 2 years ago. now need more trimming. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.5905 | 45.6463
5K50 | 662027 | CPCC | CPCC448999 | PP | OR | HOOD RIVER | KENWOOD | TR_207700_278580418 | 2007 | Before | 2007-10-19 07:42 | 2007-10-19 09:04 | 8 | 660.933 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: associate to outage #448973, bad connectivity in cadops. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 661647 | CPCC | CPCC478015 | PP | OR | HOOD RIVER | KENWOOD | OH_185401_970000044 | 2008 | Before | 2008-01-09 10:43 | 2008-01-09 16:10 | 19 | 6222.183 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | SNOW, SLEET AND BLIZZARD | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: crew on site putting primary wire back up. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.6185 | 45.5697
5K50 | 658829 | CPCC | CPCC482091 | PP | OR | HOOD RIVER | KENWOOD | OH_160561_64090670 | 2008 | Before | 2008-01-24 20:48 | 2008-01-24 22:14 | 49 | 4233.6 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: replaced burnt open hot line clamp | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.5859 | 45.6567
5K50 | 660911 | CPCC | CPCC476512 | PP | OR | HOOD RIVER | KENWOOD | TR_136900_20360222 | 2008 | Before | 2008-01-07 13:25 | 2008-01-07 14:13 | 1 | 47.267 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 661755 | CPCC | CPCC448973 | PP | OR | HOOD RIVER | KENWOOD | TR_207760_278580428 | 2007 | Before | 2007-10-19 07:13 | 2007-10-19 09:05 | 1 | 111.333 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: associate to outage #448973, bad connectivity in cadops. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 699940 | CPCC | CPCC531303 | PP | OR | HOOD RIVER | KENWOOD | RC_292460_278580237 | 2008 | Before | 2008-11-12 05:46 | 2008-11-12 08:27 | 278 | 44957.233 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Center phase down at pole 313500. Cause was tree through the line. Made repairs. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.6023 | 45.6261
5K50 | 699976 | CPCC | CPCC531806 | PP | OR | HOOD RIVER | KENWOOD | TR_174602_1510323094 | 2008 | Before | 2008-11-15 08:39 | 2008-11-15 09:46 | 1 | 67.617 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | PROSPER: Broken I-bolt on cutout. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 700430 | CPCC | CPCC528135 | PP | OR | HOOD RIVER | KENWOOD | TR_125001_20360165 | 2008 | Before | 2008-10-24 07:06 | 2008-10-24 08:12 | 1 | 65.983 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: replaced broken fuse | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 699489 | CPCC | CPCC530847 | PP | OR | HOOD RIVER | KENWOOD | TR_160701_64090719 | 2008 | Before | 2008-11-07 09:14 | 2008-11-07 10:11 | 1 | 56.75 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Refused transformer. Power restored | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 705149 | CPCC | CPCC547681 | PP | OR | HOOD RIVER | KENWOOD | Line Cut-32941 | 2009 | Before | 2009-01-07 05:17 | 2009-01-07 07:28 | 31 | 4049.633 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Crew made repairs to the overhead primary that was taken down by a tree. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.5941 | 45.6713
5K50 | 707565 | CPCC | CPCC549632 | PP | OR | HOOD RIVER | KENWOOD | TR_137406_20360208 | 2009 | Before | 2009-01-19 15:18 | 2009-01-19 17:08 | 1 | 110.35 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | SPLICE B/O OH |  |  |  | PROSPER: replaced splice in service | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 705160 | CPCC | CPCC547714 | PP | OR | HOOD RIVER | KENWOOD | OH_160561_64090670 | 2009 | Before | 2009-01-07 04:29 | 2009-01-07 07:36 | 175 | 32655 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Crew removed tree from line and refused. All customers back in service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.5859 | 45.6567
5K50 | 705678 | CPCC | CPCC547769 | PP | OR | HOOD RIVER | KENWOOD | OH_160060_64090666 | 2009 | Before | 2009-01-07 09:15 | 2009-01-07 13:23 | 3 | 744.9 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Tree fell through primary. Crew to make repairs. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.586 | 45.6503
5K50 | 704885 | CPCC | CPCC547651 | PP | OR | HOOD RIVER | KENWOOD | KWD_CB5K50 | 2009 | Before | 2009-01-07 03:01 | 2009-01-07 03:54 | 685 | 35996.75 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE | WEATHER | WIND | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: loss of transmission | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.5867 | 45.6536
5K50 | 708929 | CPCC | CPCC542449 | PP | OR | HOOD RIVER | KENWOOD | OH_185401_970000044 | 2008 | Before | 2008-12-25 10:04 | 2008-12-25 12:19 | 18 | 2413.8 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.6185 | 45.5697
5K50 | 702931 | CPCC | CPCC554556 | PP | OR | HOOD RIVER | KENWOOD | OH_164902_64090694 | 2009 | Before | 2009-02-26 08:12 | 2009-02-26 09:15 | 16 | 1013.067 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Blown fuse. No cause found. Servicman replaced and it is closed and holding. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.5764 | 45.6639
5K50 | 705424 | CPCC | CPCC547763 | PP | OR | HOOD RIVER | KENWOOD | TR_179104_278580310 | 2009 | Before | 2009-01-07 08:52 | 2009-01-07 13:26 | 1 | 274.067 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Associated to 547769. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 705426 | CPCC | CPCC547765 | PP | OR | HOOD RIVER | KENWOOD | TR_208960_278580419 | 2009 | Before | 2009-01-07 09:00 | 2009-01-07 13:26 | 1 | 266.25 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Associated to 547769. Bad connectivity. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 683145 | CPCC | CPCC507016 | PP | OR | HOOD RIVER | KENWOOD | TR_103300_64090373 | 2008 | Before | 2008-06-20 19:16 | 2008-06-20 20:31 | 1 | 74.85 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer ok. Cause was squirrel. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 683235 | CPCC | CPCC509435 | PP | OR | HOOD RIVER | KENWOOD | TR_137406_20360208 | 2008 | Before | 2008-06-29 19:49 | 2008-06-29 19:59 | 1 | 9.417 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: refused | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 684100 | CPCC | CPCC510326 | PP | OR | HOOD RIVER | KENWOOD | TR_087401_278580271 | 2008 | Before | 2008-07-03 11:04 | 2008-07-03 15:50 | 1 | 286.333 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | PROSPER: Crew made repairs to the B/O underground secondary service, customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 684690 | CPCC | CPCC514656 | PP | OR | HOOD RIVER | KENWOOD | TR_170900_278580373 | 2008 | Before | 2008-07-29 19:53 | 2008-07-29 21:02 | 1 | 69.417 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 719205 | CPCC | CPCC542519 | PP | OR | HOOD RIVER | KENWOOD | TR_100401_64090383 | 2008 | Before | 2008-12-25 14:49 | 2008-12-25 19:43 | 6 | 1765.3 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | SNOW, SLEET AND BLIZZARD | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Secondary line down | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 715986 | CPCC | CPCC540408 | PP | OR | HOOD RIVER | KENWOOD | RC_292460_278580237 | 2008 | Before | 2008-12-22 14:29 | 2008-12-22 16:55 | 279 | 40701.45 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | SNOW, SLEET AND BLIZZARD |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Field recloser locked out, reports of a line down. Line down due to snow. Crew is mkaing repairs. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.6023 | 45.6261
5K50 | 718844 | CPCC | CPCC537891 | PP | OR | HOOD RIVER | KENWOOD | KWD_CB5K50 | 2008 | Before | 2008-12-20 22:59 | 2008-12-21 01:05 | 684 | 86184 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Loss of transmission. Switched transmission line and power has been restored. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.5867 | 45.6536
5K50 | 716822 | CPCC | CPCC542702 | PP | OR | HOOD RIVER | KENWOOD | Line Cut-32713 | 2008 | Before | 2008-12-26 03:14 | 2008-12-26 06:54 | 5 | 1102.083 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | SNOW, SLEET AND BLIZZARD | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.591 | 45.6464
5K50 | 716826 | CPCC | CPCC542719 | PP | OR | HOOD RIVER | KENWOOD | TR_207700_278580418 | 2008 | Before | 2008-12-26 03:16 | 2008-12-26 06:58 | 9 | 1990.05 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | SNOW, SLEET AND BLIZZARD | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: branch on line | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 717340 | CPCC | CPCC541640 | PP | OR | HOOD RIVER | KENWOOD | OH_090102_64090565 | 2008 | Before | 2008-12-24 12:45 | 2008-12-24 13:59 | 1 | 73.7 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | SNOW, SLEET AND BLIZZARD |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: snow unload blown line fuse neutral needs repair | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.5856 | 45.6658
5K50 | 717770 | CPCC | CPCC537566 | PP | OR | HOOD RIVER | KENWOOD | TR_090205_64090647 | 2008 | Before | 2008-12-19 23:01 | 2008-12-20 02:20 | 1 | 198.45 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 717774 | CPCC | CPCC537573 | PP | OR | HOOD RIVER | KENWOOD | OH_090102_64090565 | 2008 | Before | 2008-12-20 01:52 | 2008-12-20 02:20 | 1 | 27.467 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.5856 | 45.6658
5K50 | 718567 | CPCC | CPCC537709 | PP | OR | HOOD RIVER | KENWOOD | RC_292460_278580237 | 2008 | Before | 2008-12-20 16:57 | 2008-12-20 23:12 | 274 | 102346.2 | 0 | 0 | 2 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | ICE | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Tree through the line. Made repairs and customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.6023 | 45.6261
5K50 | 718310 | CPCC | CPCC537679 | PP | OR | HOOD RIVER | KENWOOD | OH_310302_278580242 | 2008 | Before | 2008-12-20 13:11 | 2008-12-20 23:12 | 5 | 3004.5 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Tree throught line. Repairs made. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.6244 | 45.6113
5K50 | 716288 | CPCC | CPCC543127 | PP | OR | HOOD RIVER | KENWOOD | TR_134101_20360192 | 2008 | Before | 2008-12-27 13:31 | 2008-12-27 16:18 | 1 | 166.667 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 717947 | CPCC | CPCC533497 | PP | OR | HOOD RIVER | KENWOOD | TR_073001_970000039 | 2008 | Before | 2008-12-01 21:01 | 2008-12-01 22:31 | 1 | 90.033 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Blown fuse, cause was deterioration. Refused and customer is back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 729279 | CPCC | CPCC572465 | PP | OR | HOOD RIVER | KENWOOD | OH_087400_278580272 | 2009 | Before | 2009-06-24 14:17 | 2009-06-24 16:46 | 2 | 296.933 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | DIG-IN (NON-PACIFICORP PERSONNEL) |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: contractor dug into primiary, crew loading material, etc. will call repairs made, power back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.5926 | 45.6713
5K50 | 730053 | CPCC | CPCC562786 | PP | OR | HOOD RIVER | KENWOOD | TR_087200_278580264 | 2009 | Before | 2009-04-28 16:41 | 2009-04-28 16:49 | 1 | 7.417 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: see outage 562785 for crew times. Wrong site was used for outage call. Blown xfmr fuse. Serviceman refused xfmr and it held. Deteriorated fuse. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 729370 | CPCC | CPCC570775 | PP | OR | HOOD RIVER | KENWOOD | TR_179800_278580337 | 2009 | Before | 2009-06-12 11:06 | 2009-06-12 12:23 | 1 | 76.733 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | PROSPER: Employee hit ct can and meter with fork lift & separated from wall. Serviceman disconnected x-fmr bank on pole#179810 so electrician can make repairs. Customer will call back for reconnect. This pole and bank are not in Cad-ops, mapping change tag created | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 732947 | CPCC | CPCC562663 | PP | OR | HOOD RIVER | KENWOOD | TR_168961_64090689 | 2009 | Before | 2009-04-27 16:54 | 2009-04-27 18:12 | 6 | 465.6 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: broken trip o link fuse, replaced | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 734619 | CPCC | CPCC574876 | PP | OR | HOOD RIVER | KENWOOD | TR_155701_64090527 | 2009 | Before | 2009-07-10 07:57 | 2009-07-10 08:28 | 1 | 30.917 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: This outage created because customer gave wrong meter # for original outage (574873). See original outage for crew times. Per serviceman: Blown x-fmr fuse on pole # 155701 (no cause found). Serviceman re-fused x-fmr, fuse held. Customer back in service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 731945 | CPCC | CPCC572743 | PP | OR | HOOD RIVER | KENWOOD | TR_199900_278580442 | 2009 | Before | 2009-06-26 13:59 | 2009-06-26 14:36 | 2 | 72.567 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Per serviceman: Blown x-fmr fuse on pole # 199900 (triple link) due to deterioration. Serviceman replaced fuse and fuse held. All customers back in service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 709455 | CPCC | CPCC542533 | PP | OR | HOOD RIVER | KENWOOD | OH_072800_970000077 | 2008 | Before | 2008-12-25 14:51 | 2008-12-25 17:10 | 167 | 23238.05 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.6268 | 45.5898
5K50 | 709863 | CPCC | CPCC559074 | PP | OR | HOOD RIVER | KENWOOD | OH_100001_64090391 | 2009 | Before | 2009-03-31 16:12 | 2009-03-31 19:24 | 30 | 2225.4 | 0 | 0 | 2 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.5651 | 45.664
5K50 | 709864 | CPCC | CPCC559075 | PP | OR | HOOD RIVER | KENWOOD | OH_207700_1510574826 | 2009 | Before | 2009-03-31 16:13 | 2009-04-01 00:50 | 14 | 7234.033 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | POLE OH |  |  |  | PROSPER: pole on ground, crew going back for material. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.5907 | 45.6464
5K50 | 711098 | CPCC | CPCC546326 | PP | OR | HOOD RIVER | KENWOOD | TR_170402_278580362 | 2009 | Before | 2009-01-02 10:02 | 2009-01-02 16:25 | 1 | 382.967 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | SNOW, SLEET AND BLIZZARD |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: repaired broken nuet | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 713515 | CPCC | CPCC539055 | PP | OR | HOOD RIVER | KENWOOD | RC_292460_278580237 | 2008 | Before | 2008-12-21 16:25 | 2008-12-22 03:00 | 279 | 176965.283 | 0 | 0 | 2 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | SNOW, SLEET AND BLIZZARD | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Tree laying on all three phases. Primary wire down. Made repairs and going to close FR 5K60. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.6023 | 45.6261
5K50 | 713192 | CPCC | CPCC541127 | PP | OR | HOOD RIVER | KENWOOD | OH_310302_278580242 | 2008 | Before | 2008-12-23 14:06 | 2008-12-23 15:27 | 5 | 407.25 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | SNOW, SLEET AND BLIZZARD |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: line fuse blew due to snow load. refused and it is closed and holding. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.6244 | 45.6113
5K50 | 709589 | CPCC | CPCC558971 | PP | OR | HOOD RIVER | KENWOOD | KWD_CB5K50 | 2009 | Before | 2009-03-31 13:23 | 2009-03-31 14:03 | 690 | 27508 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE | TREES | TREE - NON-PREVENTABLE | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: tree thru line transmission | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.5867 | 45.6536
5K50 | 713246 | CPCC | CPCC538256 | PP | OR | HOOD RIVER | KENWOOD | TR_310203_278580487 | 2008 | Before | 2008-12-21 08:45 | 2008-12-21 10:40 | 2 | 229.2 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | SNOW, SLEET AND BLIZZARD | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: tree on transformer blown fuse | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 710123 | CPCC | CPCC559101 | PP | OR | HOOD RIVER | KENWOOD | OH_100001_64090391 | 2009 | Before | 2009-03-31 19:23 | 2009-03-31 19:23 | 0 | 0 | 34 | 18.7 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.5651 | 45.664
5K50 | 712931 | CPCC | CPCC541062 | PP | OR | HOOD RIVER | KENWOOD | TR_291301_278580386 | 2008 | Before | 2008-12-23 11:58 | 2008-12-23 14:11 | 1 | 132.517 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | SNOW, SLEET AND BLIZZARD |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: associate to outagbe 541069. Bad connectivity in cadops. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 712933 | CPCC | CPCC541069 | PP | OR | HOOD RIVER | KENWOOD | Line Cut-32643 | 2008 | Before | 2008-12-23 11:56 | 2008-12-23 14:08 | 16 | 2111.733 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | SNOW, SLEET AND BLIZZARD |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: wire down from pole 297801 due to snow. Crew to make repairs. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.6022 | 45.6258
5K50 | 712936 | CPCC | CPCC541111 | PP | OR | HOOD RIVER | KENWOOD | TR_292381_278580377 | 2008 | Before | 2008-12-23 13:31 | 2008-12-23 14:11 | 1 | 39.433 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | SNOW, SLEET AND BLIZZARD |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: associate to outagbe 541069. Bad connectivity in cadops. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 712937 | CPCC | CPCC541113 | PP | OR | HOOD RIVER | KENWOOD | TR_292381_278580377 | 2008 | Before | 2008-12-23 13:34 | 2008-12-23 14:11 | 1 | 37.083 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | SNOW, SLEET AND BLIZZARD |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: associate to outagbe 541069. Bad connectivity in cadops. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 713333 | CPCC | CPCC560859 | PP | OR | HOOD RIVER | KENWOOD | TR_160800_64090717 | 2009 | Before | 2009-04-14 13:59 | 2009-04-14 14:13 | 4 | 57.533 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | B/O EQUIPMENT | CUT-OUT B/O OH |  |  |  | PROSPER: Crew took an emergency outage to change out a b/o cut-out. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 714638 | CPCC | CPCC560376 | PP | OR | HOOD RIVER | KENWOOD | TR_101502_64090380 | 2009 | Before | 2009-04-10 07:58 | 2009-04-10 08:34 | 1 | 36.567 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: broken triple link fuse on x-fmr. looks like deterioration. serviceman to replace. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 751221 | CPCC | CPCC580699 | PP | OR | HOOD RIVER | KENWOOD | TR_101800_64090350 | 2009 | Before | 2009-08-05 03:40 | 2009-08-05 05:10 | 1 | 89.983 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: replaced transformer fuse | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 747239 | CPCC | CPCC582425 | PP | OR | HOOD RIVER | KENWOOD | TR_167800_1510004929 | 2009 | Before | 2009-08-14 12:04 | 2009-08-14 13:00 | 1 | 56.35 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 167800 and it held, the cause was a starling, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 746092 | CPCC | CPCC594073 | PP | OR | HOOD RIVER | KENWOOD | TR_185300_970000043 | 2009 | Before | 2009-10-16 18:16 | 2009-10-16 19:56 | 1 | 99.5 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: SQUIRELL BLOWN FUSE | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 759498 | CPCC | CPCC609720 | PP | OR | HOOD RIVER | KENWOOD | OH_310302_278580242 | 2009 | Before | 2009-12-29 13:53 | 2009-12-29 14:09 | 5 | 77.5 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | TREES | TREE - NON-PREVENTABLE | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Crew took an emergency outage to remove a tree from lines. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.6244 | 45.6113
5K50 | 759508 | CPCC | CPCC612330 | PP | OR | HOOD RIVER | KENWOOD | TR_016600_20360127 | 2010 | Before | 2010-01-15 13:53 | 2010-01-15 15:14 | 1 | 81.083 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: per svcman: tree branch thru line caused x-fmr fuse to blow. Serviceman replaced fuse and fuse held. Customer back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 756046 | CPCC | CPCC628408 | PP | OR | HOOD RIVER | KENWOOD | TR_103300_64090373 | 2010 | Before | 2010-04-16 11:11 | 2010-04-16 11:59 | 1 | 47.783 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Blown x-fmr fuse due to squirrel. Serviceman replaced fuse and fuse held. Customer back in service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 735224 | CPCC | CPCC564609 | PP | OR | HOOD RIVER | KENWOOD | TR_073001_970000039 | 2009 | Before | 2009-05-10 06:57 | 2009-05-10 08:34 | 1 | 96.933 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 735225 | CPCC | CPCC564616 | PP | OR | HOOD RIVER | KENWOOD | TR_125001_20360165 | 2009 | Before | 2009-05-10 07:15 | 2009-05-10 08:32 | 4 | 306.4 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 735228 | CPCC | CPCC564621 | PP | OR | HOOD RIVER | KENWOOD | OH_072800_970000077 | 2009 | Before | 2009-05-10 06:55 | 2009-05-10 08:32 | 134 | 12931 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.6268 | 45.5898
5K50 | 735229 | CPCC | CPCC564622 | PP | OR | HOOD RIVER | KENWOOD | TR_136801_20360116 | 2009 | Before | 2009-05-10 07:41 | 2009-05-10 08:32 | 1 | 50.383 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 736860 | CPCC | CPCC587779 | PP | OR | HOOD RIVER | KENWOOD | TR_364600_981200011 | 2009 | Before | 2009-09-18 20:55 | 2009-09-18 23:06 | 2 | 262.467 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Crew refused O/H transformer ok. Cause was squirrel. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 739900 | CPCC | CPCC580994 | PP | OR | HOOD RIVER | KENWOOD | TR_167800_1510004929 | 2009 | Before | 2009-08-06 09:35 | 2009-08-06 10:16 | 1 | 40.517 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 167800 and it held, the cause was a sparrow, customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 773838 | CPCC | CPCC647456 | PP | OR | HOOD RIVER | KENWOOD | TR_311102_278580488 | 2010 | Before | 2010-07-29 07:45 | 2010-07-29 08:25 | 2 | 80.433 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman replaced blown x-fmr fuse caused by squirrel. Customers back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 773162 | CPCC | CPCC648108 | PP | OR | HOOD RIVER | KENWOOD | TR_317801_278580475 | 2010 | Before | 2010-08-03 14:42 | 2010-08-03 15:27 | 2 | 90.967 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Blown xfmr fuse due to a squirrel. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 777696 | CPCC | CPCC648536 | PP | OR | HOOD RIVER | KENWOOD | OH_127400_20360153 | 2010 | Before | 2010-08-06 22:23 | 2010-08-07 06:58 | 85 | 33184.533 | 0 | 0 | 3 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | POLE OH |  |  |  | PROSPER: Car hit pole. Crew needed. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.6367 | 45.5853
5K50 | 777698 | CPCC | CPCC648542 | PP | OR | HOOD RIVER | KENWOOD | OH_127400_20360153 | 2010 | Before | 2010-08-06 23:27 | 2010-08-07 00:25 | 8 | 461.867 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | INTERFERENCE | VEHICLE ACCIDENT | POLE OH |  |  |  | PROSPER: Took emergency outage to make repairs. Isolated bad section and refused. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.6367 | 45.5853
5K50 | 767371 | CPCC | CPCC604843 | PP | OR | HOOD RIVER | KENWOOD | KWD_CB5K50 | 2009 | Before | 2009-12-09 03:43 | 2009-12-09 08:08 | 694 | 175187.6 | 0 | 0 | 2 | Y | N | N | N | N |  | PLANNED | TRANSMISSION REQUESTED |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Transmission post insulator failed and trans conductor made contact w/ distribution underbuild which locked out CB 5k50 (No distribution damage). Crew had to repair transmission before energizing circuit. Changed ON times. P44577. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.5867 | 45.6536
5K50 | 770547 | CPCC | CPCC639012 | PP | OR | HOOD RIVER | KENWOOD | TR_080200_278580291 | 2010 | Before | 2010-06-12 22:05 | 2010-06-12 23:02 | 4 | 229.667 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Blown transformer fuse. Bad order fuse. Refused and customers are back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 768631 | CPCC | CPCC619360 | PP | OR | HOOD RIVER | KENWOOD | TR_184000_970000052 | 2010 | Before | 2010-02-24 17:21 | 2010-02-24 19:54 | 1 | 153.05 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | PROSPER: repaired neutral connection. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 767478 | CPCC | CPCC615978 | PP | OR | HOOD RIVER | KENWOOD | OH_178701_278580340 | 2010 | Before | 2010-01-25 10:12 | 2010-01-25 12:03 | 35 | 3914.75 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | SNOW, SLEET AND BLIZZARD |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: crew enroute, traveling from mosier 20 min ETA. wire down, open fuses @ pole# 178701 to facilitate repairs. downed primary OH conductor due to snow unloading from line repaired, all customer power restored. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.5894 | 45.6609
5K50 | 770299 | CPCC | CPCC639004 | PP | OR | HOOD RIVER | KENWOOD | OH_127000_20360144 | 2010 | Before | 2010-06-12 19:40 | 2010-06-12 20:47 | 2 | 134.133 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | B/O EQUIPMENT | CUT-OUT B/O OH |  |  |  | PROSPER: Took outage to repair broken cross arm. See outage 638997 for the original call. Repairs made and customer is back on. Cause was a cracked cutout. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.6358 | 45.5796
5K50 | 768096 | CPCC | CPCC606874 | PP | OR | HOOD RIVER | KENWOOD | Line Cut-40052 | 2009 | Before | 2009-12-15 22:41 | 2009-12-16 04:03 | 19 | 6111.667 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: wire down, crew trimmed trees and made repairs. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.6185 | 45.5697
5K50 | 767711 | CPCC | CPCC605150 | PP | OR | HOOD RIVER | KENWOOD | OH_100500_64090343 | 2009 | Before | 2009-12-09 07:53 | 2009-12-09 10:56 | 31 | 5652.85 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | LIGHTNING ARRESTER OH |  |  |  | PROSPER: Blown tap-line fuse on pole # 100500. Due to b/o arrestor. Crew replaced b/o arrestor and fuse. All customers back in service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.565 | 45.6712
5K50 | 783322 | CPCC | CPCC633344 | PP | OR | HOOD RIVER | KENWOOD | OH_292401_278580380 | 2010 | Before | 2010-05-13 16:36 | 2010-05-14 00:41 | 4 | 1785.9 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: B/O primary U/G | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.6006 | 45.627
5K50 | 781458 | CPCC | CPCC645849 | PP | OR | HOOD RIVER | KENWOOD | TR_160561_64090724 | 2010 | Before | 2010-07-23 17:04 | 2010-07-23 18:28 | 1 | 83.517 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Tansformer fuse is blown. Found dead starling. Refused and customer is back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 785240 | CPCC | CPCC643116 | PP | OR | HOOD RIVER | KENWOOD | TR_184001_1020122079 | 2010 | Before | 2010-07-10 06:07 | 2010-07-10 07:10 | 1 | 62.417 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Squirrel | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 766195 | CPCC | CPCC609456 | PP | OR | HOOD RIVER | KENWOOD | TR_135900_20360217 | 2009 | Before | 2009-12-27 06:28 | 2009-12-27 07:54 | 4 | 340.667 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Blown transformer fuse, squirrel was the cause. Refused and customer is back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 762994 | CPCC | CPCC617794 | PP | OR | HOOD RIVER | KENWOOD | KWD_CB5K50 | 2010 | Before | 2010-02-10 12:13 | 2010-02-10 13:06 | 696 | 36725.6 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE | EQUIPMENT FAILURE | POLE FIRE | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: reported pole fire on x-mission pole | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.5867 | 45.6536
5K50 | 763003 | CPCC | CPCC617834 | PP | OR | HOOD RIVER | KENWOOD | TR_164862_64090699 | 2010 | Before | 2010-02-10 13:05 | 2010-02-10 13:06 | 0 | 0 | 1 | 0.783 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE | EQUIPMENT FAILURE | POLE FIRE | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Associated with outage 617794. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 765398 | CPCC | CPCC612015 | PP | OR | HOOD RIVER | KENWOOD | Line Cut-40601 | 2010 | Before | 2010-01-13 15:01 | 2010-01-13 20:34 | 3 | 999 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Serviceman took outage on the tapline fuse at pole# 084401 to make repairs to the overhead primary neutral that is down. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.5985 | 45.6712
5K50 | 765491 | CPCC | CPCC618881 | PP | OR | HOOD RIVER | KENWOOD | KWD_CB5K50 | 2010 | Before | 2010-02-21 10:57 | 2010-02-21 11:46 | 697 | 34315.633 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Breaker open at the substation. Serviceman has patrolled and is unable to locate any problems. Serviceman closed breaker. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.5867 | 45.6536
5K50 | 765632 | CPCC | CPCC606881 | PP | OR | HOOD RIVER | KENWOOD | OH_127400_20360153 | 2009 | Before | 2009-12-16 04:33 | 2009-12-16 08:26 | 90 | 20949 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Primary wire down due to tree. Crew made repairs to o/h primary. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.6367 | 45.5853
5K50 | 802454 | CPCC | CPCC664736 | PP | OR | HOOD RIVER | KENWOOD | TR_061601_970000074 | 2010 | Before | 2010-11-15 19:43 | 2010-11-16 00:39 | 2 | 591.767 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | TRANSFORMER OH |  |  |  | PROSPER: tree thru secondaries and broken transformer insulator | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 804364 | CPCC | CPCC685767 | PP | OR | HOOD RIVER | KENWOOD | OH_292303_1510574811 | 2011 | Before | 2011-02-28 14:35 | 2011-02-28 20:48 | 19 | 7077.5 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Crew onsite making repairs to the overhead primary that was taken down by a car that hit a pole. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.6022 | 45.6258
5K50 | 802131 | CPCC | CPCC660143 | PP | OR | HOOD RIVER | KENWOOD | OH_167701_64090328 | 2010 | Before | 2010-10-22 07:20 | 2010-10-22 14:49 | 2 | 897.967 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: Tapline fuse blown on pole# 167701 due to b/o primary cable. Crew making repairs. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.5698 | 45.6602
5K50 | 799781 | CPCC | CPCC657337 | PP | OR | HOOD RIVER | KENWOOD | OH_100500_64090343 | 2010 | Before | 2010-10-07 12:24 | 2010-10-07 14:00 | 36 | 3450 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Tree came down and took down primary conductor and blew two tapline fuses. Crew made repairs. All customers back in service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.565 | 45.6712
5K50 | 804198 | CPCC | CPCC678824 | PP | OR | HOOD RIVER | KENWOOD | TR_019003_20360139 | 2011 | Before | 2011-02-10 09:23 | 2011-02-10 10:10 | 1 | 47.483 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: broken fuse on pole 018000, svcman replaced fuse, customer b ack on | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 792922 | CPCC | CPCC664793 | PP | OR | HOOD RIVER | KENWOOD | TR_104004_64090396 | 2010 | Before | 2010-11-16 04:38 | 2010-11-16 05:43 | 2 | 130.267 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: blown transformer fuse | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 793184 | CPCC | CPCC664823 | PP | OR | HOOD RIVER | KENWOOD | OH_153900_64090557 | 2010 | Before | 2010-11-16 06:37 | 2010-11-16 08:17 | 3 | 299.65 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Blown line fuse. Serviceman patrolled, no cause found. Serviceman replaced fuse and it held. Customers back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.5579 | 45.6637
5K50 | 810233 | CPCC | CPCC669842 | PP | OR | HOOD RIVER | KENWOOD | TR_132201_20360172 | 2010 | Before | 2010-12-13 01:26 | 2010-12-13 02:27 | 1 | 61.15 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: replaced deteriorated xfmr fuse | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 805506 | CPCC | CPCC676233 | PP | OR | HOOD RIVER | KENWOOD | TR_207701_278580417 | 2011 | Before | 2011-01-17 07:56 | 2011-01-17 09:31 | 1 | 94.517 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: serviceman located pen fuse, investigated for damage/cause none found, refused, outage restored | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 806028 | CPCC | CPCC676437 | PP | OR | HOOD RIVER | KENWOOD | TR_137406_20360208 | 2011 | Before | 2011-01-17 14:19 | 2011-01-18 02:53 | 1 | 753.7 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | PROSPER: Serviceman on another job, will go here next. Bad order secondary UG service. Repairs made and customer is back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 790449 | CPCC | CPCC662443 | PP | OR | HOOD RIVER | KENWOOD | TR_165900_64090692 | 2010 | Before | 2010-10-31 14:19 | 2010-10-31 15:44 | 1 | 85.567 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: replaced transformer fuse | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 786168 | CPCC | CPCC642185 | PP | OR | HOOD RIVER | KENWOOD | TR_311102_278580488 | 2010 | Before | 2010-07-06 15:28 | 2010-07-06 17:30 | 1 | 121.65 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | OTHER UTILITY/CONTRACTOR |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Contract crew working in area snagged secondary service with an excavator and burnt open one hot leg and pulled weatherhead off of house. Serviceman to make repairs. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 789407 | CPCC | CPCC654405 | PP | OR | HOOD RIVER | KENWOOD | TR_108006_64090414 | 2010 | Before | 2010-09-15 17:08 | 2010-09-15 17:52 | 6 | 264.9 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 108006 and it held, the cause was a squirrel, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 824618 | CPCC | CPCC709042 | PP | OR | HOOD RIVER | KENWOOD | TR_137100_20360212 | 2011 | Before | 2011-06-17 17:43 | 2011-06-17 21:43 | 1 | 239.85 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CROSS ARM OH |  |  |  | PROSPER: broken cut-out, cross arm burned, calling a crew. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 824623 | CPCC | CPCC709088 | PP | OR | HOOD RIVER | KENWOOD | Line Cut-50527 | 2011 | Before | 2011-06-17 20:32 | 2011-06-17 21:43 | 7 | 495.6 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | CROSS ARM OH |  |  |  | PROSPER: Emergency outage to repair broken crossarm. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.6359 | 45.5667
5K50 | 828244 | CPCC | CPCC702197 | PP | OR | HOOD RIVER | KENWOOD | TR_099260_64090633 | 2011 | Before | 2011-04-23 06:27 | 2011-04-23 10:49 | 2 | 523.067 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | TRANSFORMER OH |  |  |  | PROSPER: Blown transformer fuse. crew to change transformer | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 826748 | CPCC | CPCC708261 | PP | OR | HOOD RIVER | KENWOOD | TR_364600_981200011 | 2011 | Before | 2011-06-12 07:51 | 2011-06-12 09:27 | 2 | 191.6 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Blown transformer fuse. Cause was squirrel. Refused and customers are back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 829487 | CPCC | CPCC707568 | PP | OR | HOOD RIVER | KENWOOD | KWD_CB5K50 | 2011 | Before | 2011-06-05 19:45 | 2011-06-05 20:51 | 705 | 46389 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE | WEATHER | LIGHTNING | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: transmission line outate, lightining in area. Isolated high line and restored power to customers. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.5867 | 45.6536
5K50 | 828800 | CPCC | CPCC704662 | PP | OR | HOOD RIVER | KENWOOD | TR_101800_64090350 | 2011 | Before | 2011-05-09 05:45 | 2011-05-09 07:01 | 2 | 153 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD SUSPECTED, NO MORTALITY |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Suspects owl. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 824553 | CPCC | CPCC712936 | PP | OR | HOOD RIVER | KENWOOD | TR_100105_64090390 | 2011 | Before | 2011-07-18 18:19 | 2011-07-18 19:01 | 1 | 41.6 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: deteriorated triple link fuse, fuse replaced, power restored | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 820252 | CPCC | CPCC685951 | PP | OR | HOOD RIVER | KENWOOD | OH_317903_278580467 | 2011 | Before | 2011-03-01 08:03 | 2011-03-01 09:12 | 1 | 69.233 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | SNOW, SLEET AND BLIZZARD |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Open tap line fuse due to snow unloading. Crew replaced fuse and it held. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.6116 | 45.6191
5K50 | 820751 | CPCC | CPCC684294 | PP | OR | HOOD RIVER | KENWOOD | TR_186101_970000046 | 2011 | Before | 2011-02-20 13:41 | 2011-02-20 19:30 | 1 | 348.85 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | PROSPER: crew to repair underground secondaries. Repairs made and customer is back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 820525 | CPCC | CPCC685993 | PP | OR | HOOD RIVER | KENWOOD | OH_207700_1510574826 | 2011 | Before | 2011-03-01 09:36 | 2011-03-01 11:34 | 15 | 1771 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | SNOW, SLEET AND BLIZZARD |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Blown tap line fuse due to snow unloading. Serviceman replaced fuse and it held. Customers back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.5907 | 45.6464
5K50 | 821374 | CPCC | CPCC716310 | PP | OR | HOOD RIVER | KENWOOD | TR_090205_1510600580 | 2011 | Before | 2011-08-05 12:27 | 2011-08-05 14:30 | 1 | 122.55 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Secondary hot leg rubbed in half by tree. Serviceman making repairs. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 834110 | CPCC | CPCC713608 | PP | OR | HOOD RIVER | KENWOOD | TR_080103_278580295 | 2011 | Before | 2011-07-24 11:11 | 2011-07-24 12:10 | 3 | 177.5 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: blown fuse, squirrel on transformer, fuse replace, power restored | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 830630 | CPCC | CPCC704650 | PP | OR | HOOD RIVER | KENWOOD | TR_094002_64090646 | 2011 | Before | 2011-05-08 17:29 | 2011-05-08 18:12 | 3 | 127.35 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Broken transformer fuse. Refused and customers are back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 835451 | CPCC | CPCC713671 | PP | OR | HOOD RIVER | KENWOOD | TR_136904_20360223 | 2011 | Before | 2011-07-25 07:22 | 2011-07-25 08:47 | 3 | 255.9 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Crew found open x-fmr fuse. Cause was a lightning strike. Crew replaced fuse and it held. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 832755 | CPCC | CPCC705012 | PP | OR | HOOD RIVER | KENWOOD | KWD_CB5K50 | 2011 | Before | 2011-05-11 20:08 | 2011-05-11 21:24 | 704 | 53844.267 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Outage due to loss of transmission, tree through transmission and primary distribution. Energized transmission picking up Kenwood sub. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.5867 | 45.6536
5K50 | 835120 | CPCC | CPCC708601 | PP | OR | HOOD RIVER | KENWOOD | TR_016600_20360127 | 2011 | Before | 2011-06-15 16:19 | 2011-06-15 17:47 | 2 | 175.733 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman arrived and found broken triple link . Will replace and report. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 813528 | CPCC | CPCC677408 | PP | OR | HOOD RIVER | KENWOOD | OH_160900_64090669 | 2011 | Before | 2011-01-26 11:28 | 2011-01-26 12:50 | 3 | 244.7 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | B/O EQUIPMENT | CUT-OUT B/O OH |  |  |  | PROSPER: Crew took outage on the tapline fuse at pole# 160900 to change out a cut-out and burnt crossarm on pole# 160904. Crossarm burnt due to b/o cut-out arcing. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.5859 | 45.6637
5K50 | 815963 | CPCC | CPCC679595 | PP | OR | HOOD RIVER | KENWOOD | TR_165900_64090692 | 2011 | Before | 2011-02-12 18:16 | 2011-02-13 07:14 | 11 | 8557.817 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: response reporting tree thru primary crew getting materials | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 815967 | CPCC | CPCC679625 | PP | OR | HOOD RIVER | KENWOOD | OH_169905_64090665 | 2011 | Before | 2011-02-12 18:32 | 2011-02-12 23:42 | 18 | 5584.2 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: response has located tree thru OH Primary, crew on site making repairs(11:18), repairs made, refused @ 23:42, outage restored | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.5654 | 45.663
5K50 | 815968 | CPCC | CPCC679626 | PP | OR | HOOD RIVER | KENWOOD | TR_100105_64090390 | 2011 | Before | 2011-02-12 18:41 | 2011-02-13 04:14 | 1 | 573.017 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: not captured should be on outage 679625 | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 816905 | CPCC | CPCC675657 | PP | OR | HOOD RIVER | KENWOOD | TR_123300_20360158 | 2011 | Before | 2011-01-14 09:47 | 2011-01-14 10:41 | 2 | 107.967 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Blown x-fmr fuse due to squirrel. Serviceman replaced fuse and it held. Customers back in service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 860056 | CPCC | CPCC730641 | PP | OR | HOOD RIVER | KENWOOD | OH_072300_970000038 | 2011 | Before | 2011-11-19 08:20 | 2011-11-19 22:07 | 30 | 18668.6 | 0 | 0 | 2 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | SNOW, SLEET AND BLIZZARD | POLE OH |  |  |  | SOURCE: snow took tree down, tree took pole & wire down Crew to repair Repairs made outage restored | DISTRIBUTION | DEVICE | MANUAL | 2011-11-19 22:30 | COMPLETED |  | 2011-11-19 08:20 | 2011-11-29 11:21 | 2011-11-20 06:30 | -121.6256 | 45.5835
5K50 | 861224 | CPCC | CPCC731755 | PP | OR | HOOD RIVER | KENWOOD | OH_310302_278580242 | 2011 | Before | 2011-11-22 15:05 | 2011-11-23 12:08 | 6 | 7580.8 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Blown tap line fuse due to tree on the line. Primary wire damaged. Crew to make repairs. Crew made repairs and refused, fuse blew again. Crew is going to wait till daylight to patroll. Customer notified. | DISTRIBUTION | DEVICE | MANUAL | 2011-11-23 11:45 | COMPLETED |  | 2011-11-22 15:05 | 2011-11-23 12:08 | 2011-11-23 12:12 | -121.6244 | 45.6113
5K50 | 860498 | CPCC | CPCC730823 | PP | OR | HOOD RIVER | KENWOOD | OH_183700_970000061 | 2011 | Before | 2011-11-21 09:04 | 2011-11-21 20:52 | 2 | 1417.033 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Serviceman found open dip fuse. Crew found b/o ug primary that runs 1/2 mile up to repeaters. Per Gf: not safe to repair tonight. Will fix tomorrow. 1 of 2 customers running on generator. District notified both customers of plan. | DISTRIBUTION | DEVICE | MANUAL | 2011-11-22 21:30 | COMPLETED |  | 2011-11-21 09:04 | 2011-11-21 20:52 | 2011-11-22 03:11 | -121.6209 | 45.5747
5K50 | 860992 | CPCC | CPCC731723 | PP | OR | HOOD RIVER | KENWOOD | OH_183700_970000061 | 2011 | Before | 2011-11-22 13:31 | 2011-11-22 23:01 | 2 | 1140.367 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: B/O ug primary. District having contractors clear a right away so they can get in to make repairs. | DISTRIBUTION | DEVICE | MANUAL | 2011-11-22 23:00 | COMPLETED |  | 2011-11-22 13:31 | 2011-11-22 23:01 | 2011-11-22 23:11 | -121.6209 | 45.5747
5K50 | 843422 | CPCC | CPCC718412 | PP | OR | HOOD RIVER | KENWOOD | TR_168961_64090689 | 2011 | Before | 2011-08-24 09:35 | 2011-08-24 10:58 | 1 | 83.383 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: B/O secondary connectors at the weatherhead. Serviceman replaced connectors. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 858291 | CPCC | CPCC729633 | PP | OR | HOOD RIVER | KENWOOD | TR_168961_64090689 | 2011 | Before | 2011-11-12 18:48 | 2011-11-12 20:01 | 6 | 439.6 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: replaced transformer fuse | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2011-11-12 22:00 | COMPLETED |  | 2011-11-12 18:48 | 2011-11-12 20:01 | 2011-11-12 20:03 | -121.5691 | 45.6639
5K50 | 841643 | CPCC | CPCC719732 | PP | OR | HOOD RIVER | KENWOOD | TR_101601_64090325 | 2011 | Before | 2011-08-29 22:26 | 2011-08-30 03:10 | 1 | 283.467 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | PROSPER: Bad order secondary, crew installed servicem saver. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5K50 | 842677 | CPCC | CPCC719654 | PP | OR | HOOD RIVER | KENWOOD | OH_178701_278580340 | 2011 | Before | 2011-08-29 09:34 | 2011-08-29 10:51 | 25 | 1932.083 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman locate open fuse @ FP# 17801(north Phase) Patroling for cause(10:08)no cause found, closed on test and it held. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.5894 | 45.6609
5K50 | 877985 | CPCC | CPCC744182 | PP | OR | HOOD RIVER | KENWOOD | TR_179104_278580310 | 2012 | Before | 2012-01-22 11:37 | 2012-01-23 10:25 | 1 | 1368.267 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Tree came down through primary. | DISTRIBUTION | CUSTOMER | AUTO |  | COMPLETED |  | 2012-01-22 11:37 | 2012-01-23 10:25 | 2012-01-23 10:31 | -121.5875 | 45.6512
5K50 | 878011 | CPCC | CPCC744344 | PP | OR | HOOD RIVER | KENWOOD | RC_292460_278580237 | 2012 | Before | 2012-01-22 20:22 | 2012-01-23 09:42 | 143 | 92817 | 0 | 0 | 3 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | SNOW, SLEET AND BLIZZARD | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Recloser opened back up due to tree on the line. Crew opened solid blades and closed recloser. Per circuit captain: Will resume in morning | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-01-22 20:39 | 2012-01-23 09:42 | 2012-01-23 11:46 | -121.6023 | 45.6261
5K50 | 879120 | CPCC | CPCC745159 | PP | OR | HOOD RIVER | KENWOOD | OH_183700_970000061 | 2012 | Before | 2012-01-27 08:34 | 2012-01-27 15:26 | 2 | 824.067 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: GF arrivied and verified dip fuse is blown. GF states that he spoke to both customers and they do not need service restored for a few days. District will make repairs at a later time. | DISTRIBUTION | DEVICE | MANUAL | 2012-01-27 16:00 | COMPLETED |  | 2012-01-27 08:34 | 2012-01-27 15:26 | 2012-01-27 16:31 | -121.6209 | 45.5747
5K50 | 883282 | CPCC | CPCC747872 | PP | OR | HOOD RIVER | KENWOOD | TR_133400_20360182 | 2012 | Before | 2012-02-21 18:21 | 2012-02-21 19:55 | 5 | 472.167 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: refused | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-02-21 21:30 | COMPLETED |  | 2012-02-21 18:21 | 2012-03-05 16:09 | 2012-02-21 20:55 | -121.6435 | 45.5705
5K50 | 875278 | CPCC | CPCC741319 | PP | OR | HOOD RIVER | KENWOOD | OH_207700_1510574826 | 2012 | Before | 2012-01-18 10:21 | 2012-01-18 15:32 | 15 | 4675.5 | 0 | 0 | 1 | Y | N | N | N | Y | 2012-01-17 to 2012-01-21 OR CoastPlus | WEATHER | SNOW, SLEET AND BLIZZARD |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman found an open tapline fuse. Serviceman patrolled and found no cause. Serviceman believes due to snow unloading. Serviceman replaced fuse and it held. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-01-18 10:22 | 2012-01-18 15:32 | 2012-01-18 19:22 | -121.5907 | 45.6464
5K50 | 875284 | CPCC | CPCC741746 | PP | OR | HOOD RIVER | KENWOOD | OH_131900_20360213 | 2012 | Before | 2012-01-18 14:19 | 2012-01-18 18:16 | 6 | 1421.4 | 0 | 0 | 1 | Y | N | N | N | Y | 2012-01-17 to 2012-01-21 OR CoastPlus | WEATHER | SNOW, SLEET AND BLIZZARD |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown fuse due to snow unloading | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-01-18 14:19 | 2012-01-18 18:16 | 2012-01-18 19:27 | -121.646 | 45.5777
5K50 | 878408 | CPCC | CPCC744009 | PP | OR | HOOD RIVER | KENWOOD | OH_086400_1510556289 | 2012 | Before | 2012-01-21 14:05 | 2012-01-23 18:46 | 33 | 98301.1 | 0 | 0 | 2 | Y | N | N | N | Y | 2012-01-17 to 2012-01-21 OR CoastPlus | TREES | TREE - NON-PREVENTABLE | WEATHER | ICE | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Crew needed to make repairs to the overhead primary that is down, custmr needs to make repairs before we can energize makeing req in css for this. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-01-21 14:14 | 2012-01-23 18:48 | 2012-01-24 16:26 | -121.5941 | 45.6713
5K50 | 871080 | CPCC | CPCC737862 | PP | OR | HOOD RIVER | KENWOOD | TR_130505_20360176 | 2011 | Before | 2011-12-29 20:00 | 2011-12-29 23:08 | 4 | 753.867 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: crew changed cut out | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2011-12-29 23:00 | COMPLETED |  | 2011-12-29 20:00 | 2011-12-29 23:08 | 2011-12-30 02:06 | -121.6503 | 45.5706
5K50 | 878160 | CPCC | CPCC744283 | PP | OR | HOOD RIVER | KENWOOD | TR_206880_278580415 | 2012 | Before | 2012-01-22 15:20 | 2012-01-23 11:44 | 1 | 1223.833 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | SNOW, SLEET AND BLIZZARD | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Crew made repairs to downed secondary. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2012-01-22 15:20 | 2012-01-23 11:44 | 2012-01-23 17:06 | -121.5925 | 45.6475
5K50 | 878161 | CPCC | CPCC744207 | PP | OR | HOOD RIVER | KENWOOD | TR_176080_278580303 | 2012 | Before | 2012-01-22 12:37 | 2012-01-23 11:45 | 1 | 1388.333 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | SNOW, SLEET AND BLIZZARD | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Crew made repairs to downed secondary. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2012-01-22 12:37 | 2012-01-23 11:45 | 2012-01-23 17:06 | -121.5933 | 45.6498
5K50 | 878412 | CPCC | CPCC744596 | PP | OR | HOOD RIVER | KENWOOD | TR_148204_20360241 | 2012 | Before | 2012-01-23 18:58 | 2012-01-23 21:04 | 1 | 126.433 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | ICE | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Crew made repairs to downed primary | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2012-01-23 18:58 | 2012-01-23 21:04 | 2012-01-24 16:26 | -121.6526 | 45.5662
5K50 | 878420 | CPCC | CPCC744698 | PP | OR | HOOD RIVER | KENWOOD | TR_099560_64090580 | 2012 | Before | 2012-01-24 09:17 | 2012-01-24 11:10 | 5 | 564.5 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Open x-fmr fuse. Cause unknown. Serviceman replaced fuse and it held. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2012-01-24 09:17 | 2012-01-24 11:10 | 2012-01-24 16:46 | -121.5653 | 45.672
5K50 | 878424 | CPCC | CPCC744749 | PP | OR | HOOD RIVER | KENWOOD | TR_174002_278580328 | 2012 | Before | 2012-01-24 14:29 | 2012-01-24 15:32 | 1 | 63.533 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | ICE | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Secondary service | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2012-01-24 14:29 | 2012-01-24 15:32 | 2012-01-24 16:46 | -121.5978 | 45.6499
5K50 | 878409 | CPCC | CPCC744482 | PP | OR | HOOD RIVER | KENWOOD | TR_209800_1510510747 | 2012 | Before | 2012-01-23 10:50 | 2012-01-23 20:26 | 1 | 575.483 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | ICE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Service line down due to ice. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2012-01-23 10:50 | 2012-01-23 20:26 | 2012-01-24 16:26 | -121.5865 | 45.6469
5K50 | 878411 | CPCC | CPCC744595 | PP | OR | HOOD RIVER | KENWOOD | TR_122102_20360163 | 2012 | Before | 2012-01-23 18:58 | 2012-01-23 21:13 | 2 | 271.333 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown fuse, no cause found, Serviceman replaced fuse. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2012-01-23 18:58 | 2012-01-23 21:13 | 2012-01-24 16:26 | -121.646 | 45.5798
5K50 | 877914 | CPCC | CPCC744144 | PP | OR | HOOD RIVER | KENWOOD | TR_161903_64090706 | 2012 | Before | 2012-01-22 08:57 | 2012-01-22 17:10 | 1 | 493.417 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: 4730 Portland Dr. tree took down service. Repairs made | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2012-01-22 08:57 | 2012-01-22 17:10 | 2012-01-23 08:57 | -121.5826 | 45.6626
5K50 | 877926 | CPCC | CPCC744228 | PP | OR | HOOD RIVER | KENWOOD | TR_176880_278580343 | 2012 | Before | 2012-01-22 13:36 | 2012-01-22 15:56 | 1 | 139.433 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | ICE | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: to assessor 1/22/12 13:42 | DISTRIBUTION | CUSTOMER | AUTO |  | COMPLETED |  | 2012-01-22 13:36 | 2012-01-22 15:56 | 2012-01-23 09:01 | -121.592 | 45.6624
5K50 | 878410 | CPCC | CPCC744563 | PP | OR | HOOD RIVER | KENWOOD | TR_185300_970000043 | 2012 | Before | 2012-01-23 14:33 | 2012-01-23 19:35 | 5 | 1510.25 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | ICE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown fuse due to ice | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2012-01-23 14:33 | 2012-01-23 19:35 | 2012-01-24 16:26 | -121.6176 | 45.5689
5K50 | 878421 | CPCC | CPCC744593 | PP | OR | HOOD RIVER | KENWOOD | OH_179261_278580324 | 2012 | Before | 2012-01-23 18:48 | 2012-01-24 14:24 | 17 | 19998.517 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | SNOW, SLEET AND BLIZZARD | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Crew made repairs to downed primary wire caused by tree/snow | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-01-23 18:48 | 2012-01-24 14:24 | 2012-01-24 16:46 | -121.5863 | 45.653
5K50 | 880336 | CPCC | CPCC746168 | PP | OR | HOOD RIVER | KENWOOD | TR_090205_1510600580 | 2012 | Before | 2012-02-03 08:15 | 2012-02-03 09:11 | 1 | 56.433 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Customers service & mast were taken down by a tree. Serviceman cut service in the clear so customer can make repairs. | DISTRIBUTION | CUSTOMER | AUTO | 2012-02-03 11:15 | COMPLETED |  | 2012-02-03 08:15 | 2012-02-03 09:11 | 2012-02-03 13:37 | -121.5848 | 45.6669
5K50 | 878876 | CPCC | CPCC742082 | PP | OR | HOOD RIVER | KENWOOD | KWD_CB5K50 | 2012 | Before | 2012-01-19 03:58 | 2012-01-26 13:30 | 718 | 3110742.718 | 0 | 0 | 37 | Y | N | N | N | Y | 2012-01-17 to 2012-01-21 OR CoastPlus | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE | TREES | TREE - NON-PREVENTABLE | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Loss of transmission, patrolling. Tree through the x-mission and distribution. Crew to make repairs. Several spots of Primary wire down due to trees. PROSPER: removed 2 houses on final rest stage - no longer exist or have been demolished | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-01-19 04:04 | 2012-02-03 09:46 | 2012-01-26 14:08 | -121.5867 | 45.6536
5K50 | 875285 | CPCC | CPCC741934 | PP | OR | HOOD RIVER | KENWOOD | OH_131400_20360180 | 2012 | Before | 2012-01-18 14:22 | 2012-01-18 18:16 | 26 | 6063.2 | 0 | 0 | 1 | Y | N | N | N | Y | 2012-01-17 to 2012-01-21 OR CoastPlus | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown line fuse due to limb on the line. Crew removed branch. Customers back in service. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-01-18 16:23 | 2012-01-18 18:16 | 2012-01-18 19:27 | -121.6477 | 45.5703
5K50 | 877822 | CPCC | CPCC743177 | PP | OR | HOOD RIVER | KENWOOD | TR_291303_278580387 | 2012 | Before | 2012-01-20 12:49 | 2012-01-22 21:29 | 4 | 13601.667 | 0 | 0 | 1 | Y | N | N | N | Y | 2012-01-17 to 2012-01-21 OR CoastPlus | WEATHER | SNOW, SLEET AND BLIZZARD |  |  | TRANSFORMER OH |  |  |  | SOURCE: X-fmr damaged and needs to be replaced. PTI Contract Crew made repairs | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2012-01-20 12:49 | 2012-01-22 21:30 | 2012-01-23 07:51 | -121.6037 | 45.6245
5K50 | 885883 | CPCC | CPCC750309 | PP | OR | HOOD RIVER | KENWOOD | TR_134400_20360195 | 2012 | Before | 2012-02-26 07:52 | 2012-02-26 08:45 | 1 | 52.75 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Squirrel on xfrmr, removed and restored power | DISTRIBUTION | CUSTOMER | AUTO | 2012-02-26 11:00 | COMPLETED |  | 2012-02-26 07:52 | 2012-02-26 08:45 | 2012-02-26 14:30 | -121.6409 | 45.5702
5K50 | 877860 | CPCC | CPCC743853 | PP | OR | HOOD RIVER | KENWOOD | Line Cut-57073 | 2012 | Before | 2012-01-19 17:55 | 2012-01-22 22:09 | 175 | 606156.284 | 0 | 0 | 7 | Y | N | N | N | Y | 2012-01-17 to 2012-01-21 OR CoastPlus | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE | WEATHER | SNOW, SLEET AND BLIZZARD | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Ken wood sub de-energized due to loss of x-mission. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-01-21 06:42 | 2012-01-22 22:09 | 2012-01-23 08:26 | -121.5864 | 45.6538
5K50 | 877950 | CPCC | CPCC744331 | PP | OR | HOOD RIVER | KENWOOD | TR_161500_64090723 | 2012 | Before | 2012-01-22 19:45 | 2012-01-23 09:06 | 1 | 801.467 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | ICE | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: O/H service is down. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2012-01-22 19:45 | 2012-01-23 09:06 | 2012-01-23 09:21 | -121.5838 | 45.6573
5K50 | 877959 | CPCC | CPCC744450 | PP | OR | HOOD RIVER | KENWOOD | OH_296802_278580251 | 2012 | Before | 2012-01-22 21:21 | 2012-01-23 09:26 | 2 | 1448.567 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | ICE |  |  | LIGHTNING ARRESTER OH |  |  |  | SOURCE: Blown lighting arrestor. Crew cleared it and refused dip. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-01-22 21:21 | 2012-01-23 09:26 | 2012-01-23 09:27 | -121.5934 | 45.6327
5K50 | 878012 | CPCC | CPCC744414 | PP | OR | HOOD RIVER | KENWOOD | TR_179800_278580337 | 2012 | Before | 2012-01-23 08:24 | 2012-01-23 10:01 | 1 | 96.833 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | ICE | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: secondary service. | DISTRIBUTION | CUSTOMER | AUTO |  | COMPLETED |  | 2012-01-23 08:24 | 2012-01-23 10:01 | 2012-01-23 11:46 | -121.5869 | 45.6616
5K50 | 878155 | CPCC | CPCC744462 | PP | OR | HOOD RIVER | KENWOOD | TR_315702_278580484 | 2012 | Before | 2012-01-23 09:45 | 2012-01-23 11:11 | 1 | 85.733 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | SNOW, SLEET AND BLIZZARD | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman made repairs to damaged secondary | DISTRIBUTION | CUSTOMER | AUTO |  | COMPLETED |  | 2012-01-23 09:45 | 2012-01-23 11:11 | 2012-01-23 17:01 | -121.6151 | 45.617
5K50 | 878158 | CPCC | CPCC744485 | PP | OR | HOOD RIVER | KENWOOD | Line Cut-57193 | 2012 | Before | 2012-01-23 10:51 | 2012-01-23 11:20 | 1 | 29.033 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | ICE | PRIMARY CONDUCTOR OH |  |  |  |  | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-01-23 10:51 | 2012-01-23 11:20 | 2012-01-23 17:01 | -121.5887 | 45.6459
5K50 | 876682 | CPCC | CPCC743185 | PP | OR | HOOD RIVER | KENWOOD | OH_292303_1510574811 | 2012 | Before | 2012-01-20 13:02 | 2012-01-20 14:33 | 21 | 1917.65 | 0 | 0 | 1 | Y | N | N | N | Y | 2012-01-17 to 2012-01-21 OR CoastPlus | WEATHER | SNOW, SLEET AND BLIZZARD |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Primary wire down. Crew made repairs. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-01-20 13:02 | 2012-01-20 14:33 | 2012-01-20 18:17 | -121.6022 | 45.6258
5K50 | 879342 | CPCC | CPCC745451 | PP | OR | HOOD RIVER | KENWOOD | TR_144203_20360233 | 2012 | Before | 2012-01-29 15:11 | 2012-01-29 17:52 | 1 | 160.567 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | SOURCE: replaced sec connection at wx/head | DISTRIBUTION | CUSTOMER | AUTO | 2012-01-29 18:15 | COMPLETED |  | 2012-01-29 15:11 | 2012-01-29 17:52 | 2012-01-29 18:05 | -121.6602 | 45.565
5K50 | 874735 | CPCC | CPCC740563 | PP | OR | HOOD RIVER | KENWOOD | OH_185401_970000044 | 2012 | Before | 2012-01-18 00:44 | 2012-01-18 03:57 | 19 | 3660.983 | 0 | 0 | 1 | Y | N | N | N | Y | 2012-01-17 to 2012-01-21 OR CoastPlus | TREES | TREE - NON-PREVENTABLE | WEATHER | SNOW, SLEET AND BLIZZARD | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Knocked limb and snow off of the line and refused | DISTRIBUTION | DEVICE | AUTO | 2012-01-18 05:30 | COMPLETED |  | 2012-01-18 02:28 | 2012-01-18 03:57 | 2012-01-18 04:47 | -121.6185 | 45.5697
5K50 | 869485 | CPCC | CPCC736311 | PP | OR | HOOD RIVER | KENWOOD | TR_151601_64090536 | 2011 | Before | 2011-12-20 08:09 | 2011-12-20 08:47 | 1 | 37.833 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown x-fmr fuse, no cause found. Serviceman replaced fuse. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2011-12-20 08:09 | 2011-12-20 08:47 | 2011-12-20 14:51 | -121.562 | 45.6585
5K50 | 877835 | CPCC | CPCC744265 | PP | OR | HOOD RIVER | KENWOOD | TR_099504_64090579 | 2012 | Before | 2012-01-22 14:54 | 2012-01-23 00:01 | 1 | 547.817 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: reinstalled service wire | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2012-01-22 14:54 | 2012-01-23 00:01 | 2012-01-23 08:01 | -121.5659 | 45.6713
5K50 | 878159 | CPCC | CPCC744186 | PP | OR | HOOD RIVER | KENWOOD | TR_207700_278580418 | 2012 | Before | 2012-01-22 11:49 | 2012-01-23 11:42 | 1 | 1433.167 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | SNOW, SLEET AND BLIZZARD | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Crew made repairs to downed secondary. | DISTRIBUTION | CUSTOMER | AUTO |  | COMPLETED |  | 2012-01-22 11:49 | 2012-01-23 11:42 | 2012-01-23 17:06 | -121.5906 | 45.6464
5K50 | 877941 | CPCC | CPCC744328 | PP | OR | HOOD RIVER | KENWOOD | TR_106201_64090403 | 2012 | Before | 2012-01-22 18:28 | 2012-01-22 22:59 | 1 | 271.9 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - TRIMMABLE | WEATHER | SNOW, SLEET AND BLIZZARD | TRANSFORMER OH |  |  |  | SOURCE: Damaged 25kva x-fmr needs to be replaced. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2012-01-22 18:28 | 2012-01-22 22:59 | 2012-01-23 09:16 | -121.552 | 45.6673
5K50 | 878014 | CPCC | CPCC744358 | PP | OR | HOOD RIVER | KENWOOD | Line Cut-57170 | 2012 | Before | 2012-01-22 22:09 | 2012-01-23 11:07 | 3 | 2334.3 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | SNOW, SLEET AND BLIZZARD | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Tree took down o/h primary. Crew made repairs. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-01-22 22:09 | 2012-01-23 11:07 | 2012-01-23 11:46 | -121.607 | 45.6219
5K50 | 878422 | CPCC | CPCC744723 | PP | OR | HOOD RIVER | KENWOOD | TR_132201_20360172 | 2012 | Before | 2012-01-24 12:14 | 2012-01-24 14:47 | 1 | 152.667 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | SNOW, SLEET AND BLIZZARD |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Crew made repairs to downed secondary. Customer back in service. | DISTRIBUTION | CUSTOMER | AUTO |  | COMPLETED |  | 2012-01-24 12:14 | 2012-01-24 14:47 | 2012-01-24 16:46 | -121.646 | 45.5668
5K50 | 883456 | CPCC | CPCC748064 | PP | OR | HOOD RIVER | KENWOOD | OH_100500_64090343 | 2012 | Before | 2012-02-22 11:03 | 2012-02-22 11:37 | 37 | 1237.65 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown tap line fuses due to wind blowing limbs into lines. | DISTRIBUTION | DEVICE | AUTO | 2012-02-22 14:15 | COMPLETED |  | 2012-02-22 11:13 | 2012-02-28 07:52 | 2012-02-22 11:41 | -121.565 | 45.6712
5K50 | 877919 | CPCC | CPCC744160 | PP | OR | HOOD RIVER | KENWOOD | TR_158901_64090556 | 2012 | Before | 2012-01-22 10:12 | 2012-01-22 20:56 | 1 | 643.333 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | SNOW, SLEET AND BLIZZARD | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Crew put service back up. customer in full service. | DISTRIBUTION | CUSTOMER | AUTO |  | COMPLETED |  | 2012-01-22 10:12 | 2012-01-22 20:56 | 2012-01-23 09:01 | -121.5479 | 45.6637
5K50 | 877923 | CPCC | CPCC744178 | PP | OR | HOOD RIVER | KENWOOD | TR_151601_64090536 | 2012 | Before | 2012-01-22 11:31 | 2012-01-22 23:24 | 1 | 712.967 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | SNOW, SLEET AND BLIZZARD | TRANSFORMER OH |  |  |  | SOURCE: crew replaced damaged transformer. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2012-01-22 11:31 | 2012-01-22 23:24 | 2012-01-23 09:01 | -121.562 | 45.6585
5K50 | 878156 | CPCC | CPCC744285 | PP | OR | HOOD RIVER | KENWOOD | OH_207700_1510574826 | 2012 | Before | 2012-01-22 15:49 | 2012-01-23 11:18 | 11 | 12864.5 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | SNOW, SLEET AND BLIZZARD | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Crew made repairs to downed primary. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-01-22 15:49 | 2012-01-23 11:18 | 2012-01-23 17:01 | -121.5907 | 45.6464
5K50 | 883183 | CPCC | CPCC747741 | PP | OR | HOOD RIVER | KENWOOD | OH_131400_20360180 | 2012 | Before | 2012-02-21 06:14 | 2012-02-21 08:59 | 26 | 4293.033 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman found an open tapline fuse. Search and patrolled and found no cause. Replaced fuse and it held | DISTRIBUTION | DEVICE | AUTO | 2012-02-21 09:30 | COMPLETED |  | 2012-02-21 06:18 | 2012-02-21 08:59 | 2012-02-21 13:30 | -121.6477 | 45.5703
5K50 | 877986 | CPCC | CPCC744468 | PP | OR | HOOD RIVER | KENWOOD | Line Cut-57191 | 2012 | Before | 2012-01-23 10:24 | 2012-01-23 10:28 | 0 | 0 | 2 | 9.4 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Tree came down through primary. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-01-23 10:24 | 2012-01-23 10:28 | 2012-01-23 10:31 | -121.5864 | 45.6509
5K50 | 878496 | CPCC | CPCC744493 | PP | OR | HOOD RIVER | KENWOOD | Line Cut-57195 | 2012 | Before | 2012-01-23 11:20 | 2012-01-24 21:44 | 8 | 16507.464 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | POLE OH |  |  |  | SOURCE: Broken poles and crossarms, crew will need an mc to get to this | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-01-23 11:20 | 2012-01-26 13:20 | 2012-01-24 22:51 | -121.5888 | 45.6458
5K50 | 878523 | CPCC | CPCC744822 | PP | OR | HOOD RIVER | KENWOOD | OH_178701_278580340 | 2012 | Before | 2012-01-24 23:45 | 2012-01-25 04:35 | 28 | 8138.676 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Tree limb hit primary and blew line fuse. Cleared limb and refused. Customers ae back on. One customers service has been torn away and will need to make repairs. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-01-24 23:45 | 2012-01-26 13:22 | 2012-01-25 04:41 | -121.5894 | 45.6609
5K50 | 879066 | CPCC | CPCC745171 | PP | OR | HOOD RIVER | KENWOOD | OH_207700_1510574826 | 2012 | Before | 2012-01-27 10:09 | 2012-01-27 12:01 | 15 | 1675.25 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | WEATHER | SNOW, SLEET AND BLIZZARD | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Crew opened tapline to repair primary neutral (from the storm). | DISTRIBUTION | DEVICE | MANUAL | 2012-01-27 12:00 | COMPLETED |  | 2012-01-27 10:09 | 2012-01-27 12:01 | 2012-01-27 13:31 | -121.5907 | 45.6464
5K50 | 889964 | CPCC | CPCC755537 | PP | OR | HOOD RIVER | KENWOOD | TR_160801_64090339 | 2012 | Before | 2012-03-13 17:07 | 2012-03-13 18:19 | 1 | 71.317 | 0 | 0 | 1 | Y | N | N | N | Y | 2012-03-12 to 2012-03-13 OR CoastPlus | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman made repairs to b/o secondary neutral. | DISTRIBUTION | CUSTOMER | AUTO | 2012-03-13 20:15 | COMPLETED |  | 2012-03-13 17:07 | 2012-03-13 18:19 | 2012-03-13 21:05 | -121.5856 | 45.6621
5K50 | 900931 | CPCC | CPCC766230 | PP | OR | HOOD RIVER | KENWOOD | OH_183700_970000061 | 2012 | Before | 2012-04-22 10:44 | 2012-04-22 16:56 | 2 | 742.867 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Bad order under ground primary, crew needed.see outage 766221 for original call.Rerpairs made, customers back in power PROSPER: original call 766223 | DISTRIBUTION | DEVICE | MANUAL | 2012-04-22 17:45 | COMPLETED |  | 2012-04-22 10:44 | 2012-05-02 11:39 | 2012-04-22 17:45 | -121.6209 | 45.5747
5K50 | 901019 | CPCC | CPCC766271 | PP | OR | HOOD RIVER | KENWOOD | OH_169905_64090665 | 2012 | Before | 2012-04-23 04:08 | 2012-04-23 06:42 | 19 | 2937.083 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: limb removed, will test | DISTRIBUTION | DEVICE | AUTO | 2012-04-23 07:15 | COMPLETED |  | 2012-04-23 04:08 | 2012-04-23 06:42 | 2012-04-23 06:45 | -121.5654 | 45.663
5K50 | 907598 | CPCC | CPCC770476 | PP | OR | HOOD RIVER | KENWOOD | TR_185003_278580448 | 2012 | Before | 2012-05-20 15:05 | 2012-05-20 17:01 | 1 | 116.333 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: Serviceman arrived and found b/o connector, replaced it outage restored | DISTRIBUTION | CUSTOMER | AUTO | 2012-05-20 18:15 | COMPLETED |  | 2012-05-20 15:05 | 2012-05-20 17:01 | 2012-05-20 18:18 | -121.6163 | 45.6501
5K50 | 892965 | CPCC | CPCC759398 | PP | OR | HOOD RIVER | KENWOOD | OH_310302_278580242 | 2012 | Before | 2012-03-22 09:15 | 2012-03-22 15:11 | 6 | 2134.2 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | SNOW, SLEET AND BLIZZARD |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Blown line fuse due to primary wire down. Crew to make repairs. | DISTRIBUTION | DEVICE | MANUAL | 2012-03-22 16:15 | COMPLETED |  | 2012-03-22 09:15 | 2012-03-22 15:11 | 2012-03-22 15:15 | -121.6244 | 45.6113
5K50 | 907240 | CPCC | CPCC770363 | PP | OR | HOOD RIVER | KENWOOD | Line Cut-62603 | 2012 | Before | 2012-05-18 15:05 | 2012-05-18 16:14 | 3 | 205.15 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: Crew made repairs to b/o primary jumper. | DISTRIBUTION | DEVICE | AUTO | 2012-05-18 18:15 | COMPLETED |  | 2012-05-18 15:05 | 2012-05-18 16:14 | 2012-05-18 16:20 | -121.6485 | 45.5698
5K50 | 928379 | CPCC | CPCC781429 | PP | OR | HOOD RIVER | KENWOOD | TR_167800_1510004929 | 2012 | Before | 2012-07-30 06:49 | 2012-07-30 07:22 | 1 | 33.367 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown x-fmr fuse due to bird. Serviceman replaced fuse and it held. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-07-30 10:00 | COMPLETED |  | 2012-07-30 06:49 | 2012-07-30 07:22 | 2012-07-30 13:35 | -121.5705 | 45.6612
5K50 | 913072 | CPCC | CPCC773345 | PP | OR | HOOD RIVER | KENWOOD | TR_080100_278580292 | 2012 | Before | 2012-06-10 14:03 | 2012-06-10 15:21 | 1 | 78.45 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | SNOW, SLEET AND BLIZZARD |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman arrived and found open fuse door. service has been out since earlier storm and customers just returned from AZ and requested reconnect. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-06-10 17:15 | COMPLETED |  | 2012-06-10 14:03 | 2012-06-10 15:21 | 2012-06-10 18:06 | -121.6059 | 45.667
5K50 | 923708 | CPCC | CPCC779117 | PP | OR | HOOD RIVER | KENWOOD | TR_185300_970000043 | 2012 | Before | 2012-07-15 12:41 | 2012-07-15 15:23 | 1 | 161.533 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: tree tore cust service pole down , temp repairs | DISTRIBUTION | CUSTOMER | AUTO | 2012-07-15 15:45 | COMPLETED |  | 2012-07-15 12:41 | 2012-07-15 15:23 | 2012-07-15 15:26 | -121.6176 | 45.5689
5K50 | 919496 | CPCC | CPCC776718 | PP | OR | HOOD RIVER | KENWOOD | TR_163600_64090336 | 2012 | Before | 2012-07-05 13:57 | 2012-07-05 15:34 | 1 | 97.667 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD SUSPECTED, NO MORTALITY |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown x-fmr fuse (bird suspected). Serviceman replaced fuse. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-07-05 17:00 | COMPLETED |  | 2012-07-05 13:57 | 2012-07-05 15:34 | 2012-07-05 15:56 | -121.5779 | 45.6595
5K50 | 918498 | CPCC | CPCC776309 | PP | OR | HOOD RIVER | KENWOOD | OH_087400_278580272 | 2012 | Before | 2012-07-01 19:49 | 2012-07-02 02:32 | 2 | 805.933 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Serviceman found blown dip fuse, needs 3 man crew to repair b/o UG Crew found the fault location and called for will wait for lacates and repair faulted cable. Repairs made | DISTRIBUTION | DEVICE | MANUAL | 2012-07-02 02:45 | COMPLETED |  | 2012-07-01 19:49 | 2012-07-02 02:32 | 2012-07-02 03:21 | -121.5926 | 45.6713
5K50 | 922508 | CPCC | CPCC778413 | PP | OR | HOOD RIVER | KENWOOD | OH_160561_64090670 | 2012 | Before | 2012-07-12 05:26 | 2012-07-12 12:06 | 239 | 56173.733 | 0 | 0 | 3 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | POLE OH |  |  |  | SOURCE: serviceman also found 2 100t fuse open @ fp-160561 and hot line clamp melted stirup because door didn't fall on the third. 3 man crew mobliized to help mason. Crew put up 1 span of wire and heated a portion up. Now replacing pole. | DISTRIBUTION | DEVICE | MANUAL | 2012-07-12 12:45 | COMPLETED |  | 2012-07-12 06:32 | 2012-07-12 12:06 | 2012-07-12 16:51 | -121.5859 | 45.6567
5K50 | 931138 | CPCC | CPCC783316 | PP | OR | HOOD RIVER | KENWOOD | TR_167800_1510004929 | 2012 | Before | 2012-08-07 10:56 | 2012-08-07 11:28 | 1 | 31.65 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown xfmr fuse but serviceman could not find a cause. Xfmr fuse replaced. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-08-07 14:00 | COMPLETED |  | 2012-08-07 10:56 | 2012-08-07 11:28 | 2012-08-07 13:11 | -121.5705 | 45.6612
5K50 | 1308364 | CPCC | CPCC787455 | PP | OR | HOOD RIVER | KENWOOD | OH_169905_64090665 | 2012 | Before | 2012-09-11 10:05 | 2012-09-11 11:53 | 14 | 1512.233 | 0 | 0 | 1 | Y | N | N | N | N |  | OPERATIONAL | INTERNAL TREE CONTRACTOR |  |  | POLE OH |  |  |  | SOURCE: tree crew caught the phone and cable line with their bucket when the drove into a driveway, which caused the pole to break, serviceman states that the service was very low | DISTRIBUTION | DEVICE | MANUAL | 2012-09-11 15:15 | COMPLETED |  | 2012-09-11 10:08 | 2012-09-11 11:53 | 2012-09-11 15:35 | -121.5654 | 45.663
5K50 | 1308365 | CPCC | CPCC787458 | PP | OR | HOOD RIVER | KENWOOD | OH_169905_64090665 | 2012 | Before | 2012-09-11 10:21 | 2012-09-11 11:53 | 5 | 461.667 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | OPERATIONAL | INTERNAL TREE CONTRACTOR | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Trees inc. caught a very low telephone and cable line with their bucket truck, causing th pole to break | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-09-11 10:21 | 2012-09-11 11:53 | 2012-09-11 15:35 | -121.5654 | 45.663
5K50 | 1320045 | CPCC | CPCC795409 | PP | OR | HOOD RIVER | KENWOOD | TR_293481_278580382 | 2012 | Before | 2012-11-02 07:04 | 2012-11-02 11:34 | 1 | 270.333 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | SOURCE: crew installed the service saver, customers are back in service | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2012-11-02 11:30 | COMPLETED |  | 2012-11-02 07:04 | 2012-11-02 11:34 | 2012-11-02 16:36 | -121.5994 | 45.6265
5K50 | 1315597 | CPCC | CPCC792719 | PP | OR | HOOD RIVER | KENWOOD | OH_160561_64090670 | 2012 | Before | 2012-10-16 03:53 | 2012-10-16 05:51 | 115 | 13501 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: Serviceman arrived and found jumper broken on highside of cutout, repaired and restored power. | DISTRIBUTION | DEVICE | AUTO | 2012-10-16 07:00 | COMPLETED |  | 2012-10-16 04:00 | 2012-10-18 10:48 | 2012-10-16 06:00 | -121.5859 | 45.6567
5K50 | 1314465 | CPCC | CPCC791290 | PP | OR | HOOD RIVER | KENWOOD | TR_080103_278580295 | 2012 | Before | 2012-10-11 11:40 | 2012-10-11 12:15 | 3 | 103.25 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown x-fmr fuse due to squirrel. Serviceman replaced fuse and it held. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-10-11 14:45 | COMPLETED |  | 2012-10-11 11:40 | 2012-10-11 12:15 | 2012-10-11 15:25 | -121.6056 | 45.6657
5K50 | 1315017 | CPCC | CPCC792114 | PP | OR | HOOD RIVER | KENWOOD | TR_294501_278580388 | 2012 | Before | 2012-10-13 13:52 | 2012-10-13 14:52 | 5 | 301.333 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown transformer fuse. Fatigued fuse, refused and customers are back on. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-10-13 17:00 | COMPLETED |  | 2012-10-13 13:52 | 2012-10-13 14:52 | 2012-10-13 14:55 | -121.599 | 45.6281
5K50 | 1320229 | CPCC | CPCC795543 | PP | OR | HOOD RIVER | KENWOOD | OH_183700_970000061 | 2012 | Before | 2012-11-03 16:02 | 2012-11-04 12:32 | 2 | 2578.6 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Serviceman found blown fuse on underground primary riser, in very rough terain, per manager, will repair tomorrow in daylight, customers contacted. 11/4/2012 Bad section of cable located, repaired , power restored | DISTRIBUTION | DEVICE | MANUAL | 2012-11-04 19:15 | COMPLETED |  | 2012-11-03 16:02 | 2012-11-04 12:32 | 2012-11-04 12:50 | -121.6209 | 45.5747
5K50 | 1309118 | CPCC | CPCC787875 | PP | OR | HOOD RIVER | KENWOOD | TR_101800_64090350 | 2012 | Before | 2012-09-14 23:35 | 2012-09-15 00:45 | 4 | 280.6 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman found blown xfmr fuse, Squrril. Refused & restored power | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-09-15 02:45 | COMPLETED |  | 2012-09-14 23:35 | 2012-09-15 00:45 | 2012-09-15 00:51 | -121.563 | 45.676
5K50 | 1309219 | CPCC | CPCC787918 | PP | OR | HOOD RIVER | KENWOOD | TR_184001_1020122079 | 2012 | Before | 2012-09-15 18:25 | 2012-09-15 19:25 | 1 | 60.017 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman had blown xfmr fuse. Starling at base of pole | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-09-15 21:30 | COMPLETED |  | 2012-09-15 18:25 | 2012-09-15 20:05 | 2012-09-15 20:10 | -121.6202 | 45.5639
5K50 | 1314040 | CPCC | CPCC791045 | PP | OR | HOOD RIVER | KENWOOD | TR_080103_278580295 | 2012 | Before | 2012-10-09 14:34 | 2012-10-09 15:05 | 3 | 93.65 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: squirell caused outage, serviceman refused the cutout, customers are back in service | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-10-09 17:45 | COMPLETED |  | 2012-10-09 14:34 | 2012-10-09 15:05 | 2012-10-09 15:20 | -121.6056 | 45.6657
5K50 | 1336334 | CPCC | CPCC813953 | PP | OR | HOOD RIVER | KENWOOD | OH_185401_970000044 | 2012 | Before | 2012-12-26 03:38 | 2012-12-26 05:57 | 19 | 2644.167 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | SNOW, SLEET AND BLIZZARD |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown line fuse, serviceman is patrolling. Serviceman reports cause was most likely snow unloading. | DISTRIBUTION | DEVICE | AUTO | 2012-12-26 07:00 | COMPLETED |  | 2012-12-26 03:51 | 2012-12-26 05:57 | 2012-12-26 06:00 | -121.6185 | 45.5697
5K50 | 1340197 | CPCC | CPCC816738 | PP | OR | HOOD RIVER | KENWOOD | TR_019603_20360132 | 2013 | Before | 2013-01-13 08:39 | 2013-01-13 10:57 | 1 | 138.55 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | SOURCE: replaced connector at transformer | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-01-13 11:45 | COMPLETED |  | 2013-01-13 08:39 | 2013-01-13 10:57 | 2013-01-13 11:00 | -121.6293 | 45.6023
5K50 | 1351764 | CPCC | CPCC823832 | PP | OR | HOOD RIVER | KENWOOD | OH_310206_278580483 | 2013 | Before | 2013-03-18 04:44 | 2013-03-18 07:41 | 2 | 353.6 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: repaired broken jumper going to cut out | DISTRIBUTION | DEVICE | AUTO | 2013-03-18 07:45 | COMPLETED |  | 2013-03-18 04:44 | 2013-03-18 07:41 | 2013-03-18 15:10 | -121.6252 | 45.6095
5K50 | 1365337 | CPCC | CPCC832806 | PP | OR | HOOD RIVER | KENWOOD | KWD_CB5K50 | 2013 | Before | 2013-05-15 14:37 | 2013-05-15 14:39 | 0 | 0 | 725 | 1607.083 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Loss of transmission | DISTRIBUTION | DEVICE | AUTO | 2013-05-15 17:45 | COMPLETED |  | 2013-05-15 14:40 | 2013-05-15 14:51 | 2013-05-15 16:21 | -121.5867 | 45.6536
5K50 | 1357599 | CPCC | CPCC827087 | PP | OR | HOOD RIVER | KENWOOD | TR_134800_20360201 | 2013 | Before | 2013-04-12 19:36 | 2013-04-12 21:12 | 1 | 96.083 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman found deteriorated triple link xfmr fuse. Refused & restored power | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-04-12 22:45 | COMPLETED |  | 2013-04-12 19:36 | 2013-04-12 21:18 | 2013-04-12 21:22 | -121.6409 | 45.5762
5K50 | 1361119 | CPCC | CPCC829366 | PP | OR | HOOD RIVER | KENWOOD | TR_174002_278580328 | 2013 | Before | 2013-04-30 08:12 | 2013-04-30 09:07 | 1 | 54.983 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman reports raccoon got into phase, serviceman will replace fuse and report. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-04-30 11:15 | COMPLETED |  | 2013-04-30 08:12 | 2013-04-30 09:07 | 2013-04-30 09:51 | -121.5978 | 45.6499
5K50 | 1385965 | CPCC | CPCC843735 | PP | OR | HOOD RIVER | KENWOOD | TR_099906_64090604 | 2013 | Before | 2013-07-27 07:52 | 2013-07-27 08:53 | 2 | 121.1 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: serviceman refused the cutout and customers are back in service | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-07-27 11:00 | COMPLETED |  | 2013-07-27 07:52 | 2013-07-27 08:53 | 2013-07-27 13:42 | -121.5663 | 45.6773
5K50 | 1393830 | CPCC | CPCC846595 | PP | OR | HOOD RIVER | KENWOOD | TR_137104_20360211 | 2013 | Before | 2013-08-14 12:25 | 2013-08-14 13:21 | 1 | 56.1 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: Serviceman replaced b/o jumper. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-08-14 15:30 | COMPLETED |  | 2013-08-14 12:25 | 2013-08-14 13:21 | 2013-08-14 16:16 | -121.6359 | 45.5665
5K50 | 1387012 | CPCC | CPCC844165 | PP | OR | HOOD RIVER | KENWOOD | TR_163402_1510612180 | 2013 | Before | 2013-07-30 16:35 | 2013-07-30 16:52 | 1 | 16.617 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown x-fmr fuse (cause unknown). Serviceman replaced fuse and it held. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-07-30 19:45 | COMPLETED |  | 2013-07-30 16:35 | 2013-07-30 16:52 | 2013-07-30 17:26 | -121.5783 | 45.6554
5K50 | 1400283 | CPCC | CPCC851719 | PP | OR | HOOD RIVER | KENWOOD | TR_184300_970000057 | 2013 | Before | 2013-09-05 11:27 | 2013-09-05 15:46 | 1 | 258.517 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | SOURCE: B/O ug service. Crew to make repairs. | DISTRIBUTION | CUSTOMER | MANUAL | 2013-09-05 18:15 | COMPLETED |  | 2013-09-05 11:27 | 2013-09-05 15:46 | 2013-09-05 17:07 | -121.621 | 45.5692
5K50 | 1409623 | CPCC | CPCC858967 | PP | OR | HOOD RIVER | KENWOOD | OH_183700_970000061 | 2013 | Before | 2013-09-29 17:44 | 2013-09-30 14:35 | 2 | 2502 | 0 | 0 | 1 | Y | N | N | N | Y | 2013-09-28 to 2013-09-29 OR CoastPlus | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Serviceman reports fuse blown on primary riser pole, will trouble shoot underground primary cable, crew had to pull of for the evening, could not find bad spot in ug primary, will be back in the am to continue trouble shooting, cable repaired,power resto | DISTRIBUTION | DEVICE | MANUAL | 2013-09-30 01:30 | COMPLETED |  | 2013-09-29 17:44 | 2013-09-30 14:35 | 2013-09-30 14:47 | -121.6209 | 45.5747
5K50 | 1406045 | CPCC | CPCC856209 | PP | OR | HOOD RIVER | KENWOOD | OH_292303_1510574811 | 2013 | Before | 2013-09-21 19:32 | 2013-09-22 01:00 | 21 | 6878.55 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | INTERFERENCE | VEHICLE ACCIDENT | POLE OH |  |  |  | SOURCE: Took emergency outage due to car pole. Crew needed. See outage 856206 for original call. Repairs made. | DISTRIBUTION | DEVICE | MANUAL | 2013-09-22 08:45 | COMPLETED |  | 2013-09-21 19:32 | 2013-09-22 07:06 | 2013-09-22 07:11 | -121.6022 | 45.6258
5K50 | 1410186 | CPCC | CPCC860222 | PP | OR | HOOD RIVER | KENWOOD | OH_176701_1510384931 | 2013 | Before | 2013-10-01 09:14 | 2013-10-01 15:30 | 3 | 1125.55 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Serviceman reports dip open and B/O primary UG. Crew to make repairs. Crew has made repairs. | DISTRIBUTION | DEVICE | MANUAL | 2013-10-01 16:30 | COMPLETED |  | 2013-10-01 09:14 | 2013-10-01 15:30 | 2013-10-01 15:46 | -121.593 | 45.6609
5K50 | 1423594 | CPCC | CPCC867401 | PP | OR | HOOD RIVER | KENWOOD | TR_185002_970000048 | 2013 | Before | 2013-11-22 10:53 | 2013-11-22 15:22 | 1 | 268.167 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | SOURCE: Serviceman reports bad secondary underground,crew to make repairs | DISTRIBUTION | CUSTOMER | MANUAL | 2013-11-22 16:00 | COMPLETED |  | 2013-11-22 10:53 | 2013-11-22 15:22 | 2013-11-22 16:03 | -121.6184 | 45.565
5K50 | 1444862 | CPCC | CPCC885648 | PP | OR | HOOD RIVER | KENWOOD | Line Cut-83373 | 2014 | Before | 2014-02-17 06:54 | 2014-02-17 11:54 | 4 | 1200.4 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Tree through primary, crew to make repairs | DISTRIBUTION | DEVICE | AUTO | 2014-02-17 10:00 | COMPLETED |  | 2014-02-17 06:54 | 2014-02-17 11:54 | 2014-02-17 16:09 | -121.5654 | 45.6553
5K50 | 1425302 | CPCC | CPCC868199 | PP | OR | HOOD RIVER | KENWOOD | TR_185003_278580448 | 2013 | Before | 2013-12-01 00:26 | 2013-12-01 02:51 | 1 | 144.7 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Customer service burnt up due to tree. Repairs made and customer is back on. | DISTRIBUTION | CUSTOMER | AUTO | 2013-12-01 03:30 | COMPLETED |  | 2013-12-01 00:26 | 2013-12-01 02:51 | 2013-12-01 11:25 | -121.6163 | 45.6501
5K50 | 1470290 | CPCC | CPCC899694 | PP | OR | HOOD RIVER | KENWOOD | TR_158901_64090556 | 2014 | Before | 2014-05-30 16:16 | 2014-05-30 17:31 | 7 | 525.117 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | OTHER, KNOWN CAUSE |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: transformer fuse melt out when heat pump came on | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-05-30 19:15 | COMPLETED |  | 2014-05-30 16:16 | 2014-05-30 17:31 | 2014-05-30 18:58 | -121.5479 | 45.6637
5K50 | 1452425 | CPCC | CPCC890444 | PP | OR | HOOD RIVER | KENWOOD | OH_183700_970000061 | 2014 | Before | 2014-03-22 08:18 | 2014-03-22 15:23 | 2 | 850.5 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Bad order primary UG, 3 man crew needed. Repairs made and customers are back on. | DISTRIBUTION | DEVICE | MANUAL | 2014-03-22 16:00 | COMPLETED |  | 2014-03-22 08:18 | 2014-03-22 15:23 | 2014-03-22 18:31 | -121.6209 | 45.5747
5K50 | 1468961 | CPCC | CPCC898996 | PP | OR | HOOD RIVER | KENWOOD | TR_208960_278580419 | 2014 | Before | 2014-05-25 21:42 | 2014-05-26 01:46 | 1 | 243.933 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | POLE OH |  |  |  | SOURCE: Serviceman arrived and found broken pole, wants 2 men to help secure pole for the holliday and they will repair at a later date. Pole secured. | DISTRIBUTION | CUSTOMER | AUTO | 2014-05-26 00:45 | COMPLETED |  | 2014-05-25 21:42 | 2014-05-26 01:46 | 2014-05-26 03:18 | -121.5883 | 45.6492
5K50 | 1465167 | CPCC | CPCC897099 | PP | OR | HOOD RIVER | KENWOOD | TR_104700_64090368 | 2014 | Before | 2014-05-10 17:15 | 2014-05-10 19:27 | 1 | 132.717 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman found bad order xfmr. 3 man crew called to replace & restore after rurther review, poss customer issue PROSPER: Changed Direct from Other, Known Cause. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-05-10 20:15 | COMPLETED |  | 2014-05-10 17:15 | 2014-05-12 09:14 | 2014-05-10 21:23 | -121.5554 | 45.6744
5K50 | 1482582 | CPCC | CPCC906309 | PP | OR | HOOD RIVER | KENWOOD | OH_183700_970000061 | 2014 | Before | 2014-07-13 09:21 | 2014-07-13 14:42 | 2 | 641.367 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: B/O UG Crew made repairs and restored power. | DISTRIBUTION | DEVICE | AUTO | 2014-07-13 12:30 | COMPLETED |  | 2014-07-13 09:21 | 2014-07-13 14:42 | 2014-07-13 15:48 | -121.6209 | 45.5747
5K50 | 1485523 | CPCC | CPCC908200 | PP | OR | HOOD RIVER | KENWOOD | TR_170900_278580373 | 2014 | Before | 2014-07-21 09:07 | 2014-07-21 10:33 | 5 | 428.5 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Servicema replaced melted transformer fuse | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-07-21 12:15 | COMPLETED |  | 2014-07-21 09:07 | 2014-07-21 10:33 | 2014-07-21 12:50 | -121.6064 | 45.6638
5K50 | 1493862 | CPCC | CPCC914167 | PP | OR | HOOD RIVER | KENWOOD | TR_162901_64090703 | 2014 | Before | 2014-08-14 16:16 | 2014-08-14 17:34 | 6 | 466.7 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman stated that this triple link fuse was broken, refused the cutout and customers are back in service | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-08-14 19:30 | COMPLETED |  | 2014-08-14 16:16 | 2014-08-14 17:34 | 2014-08-14 18:39 | -121.5813 | 45.6639
5K50 | 1493462 | CPCC | CPCC913791 | PP | OR | HOOD RIVER | KENWOOD | OH_365200_981200012 | 2014 | Before | 2014-08-12 15:02 | 2014-08-13 06:35 | 1 | 933.05 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Blown dip fuse due to b/o ug primary. | DISTRIBUTION | DEVICE | MANUAL | 2014-08-13 07:30 | COMPLETED |  | 2014-08-12 15:02 | 2014-08-13 06:35 | 2014-08-13 16:10 | -121.6409 | 45.6128
5K50 | 1485944 | CPCC | CPCC908425 | PP | OR | HOOD RIVER | KENWOOD | TR_163402_1510612180 | 2014 | Before | 2014-07-22 12:06 | 2014-07-22 13:09 | 1 | 63.4 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown x-fmr fuse due to starling. Serviceman replaced fuse and it held. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-07-22 15:15 | COMPLETED |  | 2014-07-22 12:06 | 2014-07-22 13:09 | 2014-07-23 15:33 | -121.5783 | 45.6554
5K50 | 1482399 | CPCC | CPCC906180 | PP | OR | HOOD RIVER | KENWOOD | OH_183700_970000061 | 2014 | Before | 2014-07-12 08:02 | 2014-07-12 14:03 | 2 | 722.5 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: B/O UG 3 man crew made repairs. Power restored. | DISTRIBUTION | DEVICE | AUTO | 2014-07-12 11:15 | COMPLETED |  | 2014-07-12 08:02 | 2014-07-12 14:03 | 2014-07-12 18:13 | -121.6209 | 45.5747
5K50 | 1474452 | CPCC | CPCC902076 | PP | OR | HOOD RIVER | KENWOOD | TR_364600_981200011 | 2014 | Before | 2014-06-15 20:19 | 2014-06-15 21:53 | 1 | 93.567 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Squirrel - replaced transformer fuse | DISTRIBUTION | CUSTOMER | AUTO | 2014-06-15 23:30 | COMPLETED |  | 2014-06-15 20:19 | 2014-06-15 21:53 | 2014-06-15 22:13 | -121.6373 | 45.6173
5K50 | 1480775 | CPCC | CPCC905269 | PP | OR | HOOD RIVER | KENWOOD | OH_183700_970000061 | 2014 | Before | 2014-07-07 16:28 | 2014-07-07 22:33 | 2 | 730.4 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Crew made repairs. B/O UG outage resolved. | DISTRIBUTION | DEVICE | MANUAL | 2014-07-07 22:30 | COMPLETED |  | 2014-07-07 16:28 | 2014-07-07 22:33 | 2014-07-08 01:26 | -121.6209 | 45.5747
5K50 | 1492964 | CPCC | CPCC913691 | PP | OR | HOOD RIVER | KENWOOD | OH_169905_64090665 | 2014 | Before | 2014-08-12 14:26 | 2014-08-12 18:06 | 15 | 2041.833 | 0 | 0 | 2 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Line down due to tree. Crew made repairs. | DISTRIBUTION | DEVICE | AUTO | 2014-08-12 18:45 | COMPLETED |  | 2014-08-12 15:43 | 2014-08-12 18:06 | 2014-08-12 19:17 | -121.5654 | 45.663
5K50 | 1507128 | CPCC | CPCC921572 | PP | OR | HOOD RIVER | KENWOOD | TR_184001_1020122079 | 2014 | Before | 2014-10-02 08:56 | 2014-10-02 09:37 | 1 | 41.133 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman found transformer fuse open on pole # 184001; serviceman found a dead squirrel, re-fused and it held. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-10-02 12:00 | COMPLETED |  | 2014-10-02 08:56 | 2014-10-02 09:37 | 2014-10-02 11:43 | -121.6202 | 45.5639
5K50 | 1500775 | CPCC | CPCC917793 | PP | OR | HOOD RIVER | KENWOOD | TR_099602_64090568 | 2014 | Before | 2014-09-09 07:17 | 2014-09-09 08:04 | 1 | 46.683 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman found blown fuse due to starling, re-fused and it held | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-09-09 10:30 | COMPLETED |  | 2014-09-09 07:17 | 2014-09-09 08:04 | 2014-09-09 08:48 | -121.5657 | 45.6735
5K50 | 1510400 | CPCC | CPCC923501 | PP | OR | HOOD RIVER | KENWOOD | TR_185100_970000047 | 2014 | Before | 2014-10-18 17:34 | 2014-10-18 21:04 | 1 | 209.3 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | SOURCE: Serviceman found B/O ug Service connected service savor and got customers back in power. | DISTRIBUTION | CUSTOMER | AUTO | 2014-10-18 20:45 | COMPLETED |  | 2014-10-18 17:34 | 2014-10-18 21:04 | 2014-10-19 03:53 | -121.6177 | 45.5661
5K50 | 1526712 | CPCC | CPCC940635 | PP | OR | HOOD RIVER | KENWOOD | RC_292460_278580237 | 2014 | Before | 2014-12-21 00:46 | 2014-12-21 05:42 | 296 | 87586.4 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  |  | DISTRIBUTION | DEVICE | MANUAL | 2014-12-21 07:30 | COMPLETED |  | 2014-12-21 01:03 | 2014-12-22 08:18 | 2014-12-21 05:53 | -121.6023 | 45.6261
5K50 | 1522664 | CPCC | CPCC935688 | PP | OR | HOOD RIVER | KENWOOD | OH_365500_981200015 | 2014 | Before | 2014-12-06 10:46 | 2014-12-06 13:40 | 1 | 173.767 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Stranded condutor made contact with neutral and blew lien fuse. Crew made repairs. | DISTRIBUTION | DEVICE | AUTO | 2014-12-06 14:00 | COMPLETED |  | 2014-12-06 10:46 | 2014-12-06 13:40 | 2014-12-06 13:48 | -121.6365 | 45.6148
5K50 | 1546528 | CPCC | CPCC956004 | PP | OR | HOOD RIVER | KENWOOD | OH_185401_970000044 | 2015 | Before | 2015-03-22 18:41 | 2015-03-22 19:16 | 19 | 666.267 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | INTENTIONAL TO CLEAR TROUBLE | TREES | TREE - NON-PREVENTABLE | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Crew opened a line fuse to remove a tree branch from o/h primary | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2015-03-22 18:41 | 2015-03-22 20:57 | 2015-03-22 21:03 | -121.6185 | 45.5697
5K50 | 1559583 | CPCC | CPCC964087 | PP | OR | HOOD RIVER | KENWOOD | Line Cut-95751 | 2015 | Before | 2015-05-12 11:07 | 2015-05-12 15:15 | 50 | 12400.833 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | OTHER UTILITY/CONTRACTOR |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Tree trimmer fell a tree through a line; crew made repairs | DISTRIBUTION | DEVICE | MANUAL | 2015-05-12 16:30 | COMPLETED |  | 2015-05-12 11:08 | 2015-05-12 16:08 | 2015-05-12 16:13 | -121.646 | 45.5776
5K50 | 1549763 | CPCC | CPCC958278 | PP | OR | HOOD RIVER | KENWOOD | TR_184201_970000056 | 2015 | Before | 2015-04-06 18:04 | 2015-04-06 21:00 | 1 | 176.2 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | SOURCE: B/O ug secondary leg. Crew installed a service saver and will make repairs at a later time. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-04-06 21:15 | COMPLETED |  | 2015-04-06 18:04 | 2015-04-06 21:04 | 2015-04-06 21:08 | -121.6197 | 45.5672
5K50 | 1563069 | CPCC | CPCC965882 | PP | OR | HOOD RIVER | KENWOOD | OH_183700_970000061 | 2015 | Before | 2015-05-26 08:12 | 2015-05-26 13:49 | 2 | 673.833 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Serviceman found a blown dip fuse on pole # 183700; crew made repairs. | DISTRIBUTION | DEVICE | MANUAL | 2015-05-26 14:30 | COMPLETED |  | 2015-05-26 08:12 | 2015-05-26 15:03 | 2015-05-26 15:04 | -121.6209 | 45.5747
5K50 | 1553487 | CPCC | CPCC960647 | PP | OR | HOOD RIVER | KENWOOD | TR_127804_20360141 | 2015 | Before | 2015-04-17 12:00 | 2015-04-17 12:40 | 1 | 40.35 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Serviceman reports there is a bad cutout, tracking; will have crew out after lunch to change it out. | DISTRIBUTION | CUSTOMER | AUTO | 2015-04-17 15:00 | COMPLETED |  | 2015-04-17 12:00 | 2015-04-17 15:44 | 2015-04-17 15:48 | -121.6358 | 45.5898
5K50 | 1561780 | CPCC | CPCC965068 | PP | OR | HOOD RIVER | KENWOOD | OH_165961_64090693 | 2015 | Before | 2015-05-20 19:34 | 2015-05-21 02:26 | 1 | 411.7 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | POLE OH |  |  |  | SOURCE: Log truck snagged a line and broke our pole. Crew to make repairs. | DISTRIBUTION | DEVICE | MANUAL | 2015-05-21 05:00 | COMPLETED |  | 2015-05-20 19:34 | 2015-05-21 02:27 | 2015-05-21 02:28 | -121.5758 | 45.6639
5K50 | 1559571 | CPCC | CPCC964096 | PP | OR | HOOD RIVER | KENWOOD | Line Cut-95753 | 2015 | Before | 2015-05-12 11:07 | 2015-05-12 15:15 | 7 | 1736.117 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | OTHER UTILITY/CONTRACTOR |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: associate to outage # 964087 | DISTRIBUTION | DEVICE | MANUAL | 2015-05-12 16:30 | COMPLETED |  | 2015-05-12 12:10 | 2015-05-12 15:41 | 2015-05-12 15:43 | -121.646 | 45.5777
5K50 | 1548108 | CPCC | CPCC957036 | PP | OR | HOOD RIVER | KENWOOD | TR_137300_20360209 | 2015 | Before | 2015-03-29 18:01 | 2015-03-29 18:48 | 2 | 92.833 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: replaced transformer fuse | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-03-29 21:15 | COMPLETED |  | 2015-03-29 18:01 | 2015-03-30 02:41 | 2015-03-30 02:43 | -121.6359 | 45.5691
5K50 | 1545153 | CPCC | CPCC954844 | PP | OR | HOOD RIVER | KENWOOD | OH_169701_64090540 | 2015 | Before | 2015-03-15 16:34 | 2015-03-16 03:34 | 5 | 3299.25 | 0 | 0 | 1 | Y | N | N | N | Y | 3/15/2015 Coast Plus | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Tree down through O/H primary | DISTRIBUTION | DEVICE | AUTO | 2015-03-15 19:45 | COMPLETED |  | 2015-03-15 16:36 | 2015-03-16 03:47 | 2015-03-16 03:48 | -121.5654 | 45.6603
5K50 | 1558524 | CPCC | CPCC963436 | PP | OR | HOOD RIVER | KENWOOD | OH_138903_20360227 | 2015 | Before | 2015-05-07 17:19 | 2015-05-07 18:41 | 2 | 164.267 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman reports broken fuse at FP 138903, No Cause Found, Re-Fused and Holding, Customers Restored | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2015-05-07 18:37 | 2015-05-07 18:42 | 2015-05-07 18:44 | -121.6311 | 45.5783
5K50 | 1541504 | CPCC | CPCC952785 | PP | OR | HOOD RIVER | KENWOOD | TR_169301_64090672 | 2015 | Before | 2015-02-27 10:18 | 2015-02-27 12:48 | 5 | 751.417 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Crew replaced broken cut out. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-02-27 13:30 | COMPLETED |  | 2015-02-27 10:18 | 2015-02-27 13:34 | 2015-02-27 13:38 | -121.5656 | 45.6539
5K50 | 1555107 | CPCC | CPCC961873 | PP | OR | HOOD RIVER | KENWOOD | TR_080103_278580295 | 2015 | Before | 2015-04-24 10:52 | 2015-04-24 11:26 | 3 | 103.15 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown transformer fuse due squirrel; re-fused and it held. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-04-24 14:00 | COMPLETED |  | 2015-04-24 10:52 | 2015-04-24 11:31 | 2015-04-24 11:33 | -121.6056 | 45.6657
5K50 | 1576677 | CPCC | CPCC974155 | PP | OR | HOOD RIVER | KENWOOD | TR_134101_20360192 | 2015 | Before | 2015-07-06 13:01 | 2015-07-06 15:21 | 4 | 558.8 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman took outage on the transformer to make repairs to the overhead secondary service that was damaged by a tree. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-07-06 17:00 | COMPLETED |  | 2015-07-06 13:48 | 2015-07-06 17:22 | 2015-07-06 17:23 | -121.641 | 45.5655
5K50 | 1578257 | CPCC | CPCC975599 | PP | OR | HOOD RIVER | KENWOOD | TR_107002_64090410 | 2015 | Before | 2015-07-09 14:32 | 2015-07-09 15:18 | 4 | 181.8 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman found transformer fuse open due to starling; re-fused and it held. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-07-09 17:45 | COMPLETED |  | 2015-07-09 14:33 | 2015-07-09 15:42 | 2015-07-09 15:48 | -121.5498 | 45.6648
5K50 | 1567099 | CPCC | CPCC968228 | PP | OR | HOOD RIVER | KENWOOD | OH_103500_64090371 | 2015 | Before | 2015-06-08 19:10 | 2015-06-08 20:33 | 1 | 82.75 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Fuse blown @ junction pole & transformer-- serviceman will investigate -- no trouble found -- re-fused both | DISTRIBUTION | DEVICE | AUTO | 2015-06-08 22:15 | COMPLETED |  | 2015-06-08 19:10 | 2015-06-08 21:40 | 2015-06-08 21:43 | -121.5588 | 45.6712
5K50 | 1576323 | CPCC | CPCC974010 | PP | OR | HOOD RIVER | KENWOOD | RC_292460_278580237 | 2015 | Before | 2015-07-05 23:05 | 2015-07-05 23:18 | 300 | 3875 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | INTERFERENCE | VEHICLE ACCIDENT | POLE OH |  |  |  | SOURCE: service man opened to clear trouble, car hit guy stub, crew to replace | DISTRIBUTION | DEVICE | AUTO | 2015-07-06 02:15 | COMPLETED |  | 2015-07-05 23:08 | 2015-07-08 11:33 | 2015-07-06 04:13 | -121.6023 | 45.6261
5K50 | 1573499 | CPCC | CPCC971957 | PP | OR | HOOD RIVER | KENWOOD | TR_179104_278580310 | 2015 | Before | 2015-06-29 01:27 | 2015-06-29 03:25 | 1 | 118.583 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman replaced a blown fuse | DISTRIBUTION | CUSTOMER | AUTO | 2015-06-29 04:30 | COMPLETED |  | 2015-06-29 01:27 | 2015-06-29 05:52 | 2015-06-29 05:53 | -121.5875 | 45.6512
5K50 | 1575080 | CPCC | CPCC972985 | PP | OR | HOOD RIVER | KENWOOD | TR_103300_64090373 | 2015 | Before | 2015-07-01 19:03 | 2015-07-01 20:16 | 1 | 72.85 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman reports Squirrel suicide, re- fused and restored customer | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-07-01 22:15 | COMPLETED |  | 2015-07-01 19:03 | 2015-07-01 22:17 | 2015-07-01 22:18 | -121.5588 | 45.6696
5K50 | 1578201 | CPCC | CPCC975576 | PP | OR | HOOD RIVER | KENWOOD | TR_163402_1510612180 | 2015 | Before | 2015-07-09 12:43 | 2015-07-09 13:14 | 1 | 31.367 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman found transformer fuse open due to starling. Re-fused and it held. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-07-09 15:45 | COMPLETED |  | 2015-07-09 12:43 | 2015-07-09 13:53 | 2015-07-09 13:58 | -121.5783 | 45.6554
5K50 | 1584258 | CPCC | CPCC980289 | PP | OR | HOOD RIVER | KENWOOD | TR_132500_20360184 | 2015 | Before | 2015-07-29 12:05 | 2015-07-29 12:55 | 3 | 151.3 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman found fuse open due wind. Re-fused and it held. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-07-29 15:45 | COMPLETED |  | 2015-07-29 12:46 | 2015-07-29 13:34 | 2015-07-29 13:39 | -121.646 | 45.5716
5K50 | 1587171 | CPCC | CPCC982560 | PP | OR | HOOD RIVER | KENWOOD | OH_183700_970000061 | 2015 | Before | 2015-08-06 21:31 | 2015-08-07 07:21 | 2 | 1179.967 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Blown dip fuse, bad order primary UG. | DISTRIBUTION | DEVICE | MANUAL | 2015-08-07 08:30 | COMPLETED |  | 2015-08-06 21:31 | 2015-08-07 09:30 | 2015-08-07 09:34 | -121.6209 | 45.5747
5K50 | 1568482 | CPCC | CPCC969155 | PP | OR | HOOD RIVER | KENWOOD | TR_080100_278580292 | 2015 | Before | 2015-06-12 19:08 | 2015-06-12 20:47 | 1 | 98.983 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Tree rubbed throug secondary service neutral. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-06-12 22:15 | COMPLETED |  | 2015-06-12 19:13 | 2015-06-12 22:46 | 2015-06-12 22:48 | -121.6059 | 45.667
5K50 | 1573146 | CPCC | CPCC971783 | PP | OR | HOOD RIVER | KENWOOD | OH_179160_278580312 | 2015 | Before | 2015-06-27 18:45 | 2015-06-27 19:51 | 180 | 11838 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman replaced a melted fuse | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2015-06-27 19:55 | 2015-06-28 00:35 | 2015-06-28 00:38 | -121.5863 | 45.6518
5K50 | 1577111 | CPCC | CPCC974355 | PP | OR | HOOD RIVER | KENWOOD | OH_183700_970000061 | 2015 | Before | 2015-07-07 01:34 | 2015-07-07 08:01 | 2 | 773.467 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Bad pri UG crew to make repairs | DISTRIBUTION | DEVICE | AUTO | 2015-07-07 04:45 | COMPLETED |  | 2015-07-07 01:34 | 2015-07-07 17:54 | 2015-07-07 17:58 | -121.6209 | 45.5747
5K50 | 1583874 | CPCC | CPCC980134 | PP | OR | HOOD RIVER | KENWOOD | TR_167800_1510004929 | 2015 | Before | 2015-07-28 09:39 | 2015-07-28 10:19 | 1 | 39.35 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman found transformer fuse open due to starling, re-fused and it held. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-07-28 12:45 | COMPLETED |  | 2015-07-28 09:40 | 2015-07-28 10:41 | 2015-07-28 10:44 | -121.5705 | 45.6612
5K50 | 1579110 | CPCC | CPCC976450 | PP | OR | HOOD RIVER | KENWOOD | TR_134902_20360216 | 2015 | Before | 2015-07-12 10:59 | 2015-07-12 12:17 | 3 | 231.25 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: replaced broken fuse | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-07-12 14:00 | COMPLETED |  | 2015-07-12 11:00 | 2015-07-12 12:42 | 2015-07-12 12:43 | -121.6409 | 45.5773
5K50 | 1605061 | CPCC | CPCC994208 | PP | OR | HOOD RIVER | KENWOOD | TR_165900_64090692 | 2015 | Before | 2015-10-13 12:17 | 2015-10-13 12:54 | 10 | 371.833 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman found blown transformer fuse due to squirrel. Re-fused and i theld. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-10-13 15:30 | COMPLETED |  | 2015-10-13 12:18 | 2015-10-14 10:13 | 2015-10-14 10:14 | -121.5749 | 45.6639
5K50 | 1609046 | CPCC | CPCC996807 | PP | OR | HOOD RIVER | KENWOOD | OH_310302_278580242 | 2015 | Before | 2015-10-31 18:56 | 2015-11-01 16:17 | 4 | 5365.467 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Junction blown -- primary down in the river -- due to weather 'rain' river is realy moving fast and dangerous -- crew will come back in daylight to make repairs -- customers out till then. Work complete. | DISTRIBUTION | DEVICE | MANUAL | 2015-11-01 16:00 | COMPLETED |  | 2015-10-31 18:56 | 2015-11-01 17:55 | 2015-11-01 17:59 | -121.6243 | 45.6113
5K50 | 1604405 | CPCC | CPCC993870 | PP | OR | HOOD RIVER | KENWOOD | TR_311102_278580488 | 2015 | Before | 2015-10-10 20:06 | 2015-10-10 21:18 | 1 | 72.133 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman replaced a blown fuse | DISTRIBUTION | CUSTOMER | AUTO | 2015-10-10 23:15 | COMPLETED |  | 2015-10-10 20:06 | 2015-10-11 06:31 | 2015-10-11 06:32 | -121.6236 | 45.6089
5K50 | 1608878 | CPCC | CPCC996880 | PP | OR | HOOD RIVER | KENWOOD | OH_178701_278580340 | 2015 | Before | 2015-10-31 19:16 | 2015-11-01 01:58 | 21 | 9675.317 | 0 | 0 | 3 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Tree fell & took primary & neutral down -- crew made repairs | DISTRIBUTION | DEVICE | MANUAL | 2015-11-01 02:15 | COMPLETED |  | 2015-10-31 21:14 | 2015-11-01 01:59 | 2015-11-01 02:04 | -121.5894 | 45.6609
5K50 | 1605363 | CPCC | CPCC994427 | PP | OR | HOOD RIVER | KENWOOD | RC_292460_278580237 | 2015 | Before | 2015-10-15 05:24 | 2015-10-15 08:40 | 283 | 55458.567 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | INSULATOR OH |  |  |  | SOURCE: Power line down starting fires, Line down at FP 061501, Arcos Callout initiated for 3 man crew and flaggers, Mason, Traver, and Harris accepted callout. Broken insulator swung & hit tree, sat there and smoldered | DISTRIBUTION | DEVICE | AUTO | 2015-10-15 09:00 | COMPLETED |  | 2015-10-15 05:25 | 2015-10-15 15:05 | 2015-10-15 15:09 | -121.6023 | 45.6261
5K50 | 1608876 | CPCC | CPCC996919 | PP | OR | HOOD RIVER | KENWOOD | OH_178701_278580340 | 2015 | Before | 2015-11-01 01:20 | 2015-11-01 01:58 | 15 | 542.55 | 0 | 0 | 2 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | TREES | TREE - NON-PREVENTABLE | PLANNED OUTAGE |  |  |  | SOURCE: Servieman opened to allow for repairs of down line between FP 187300 and 187301. Tree came through line and was still resting on hot phase | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2015-11-01 01:20 | 2015-11-10 11:26 | 2015-11-01 02:04 | -121.5894 | 45.6609
5K50 | 1608889 | CPCC | CPCC996722 | PP | OR | HOOD RIVER | KENWOOD | TR_169301_64090672 | 2015 | Before | 2015-10-31 13:22 | 2015-10-31 18:29 | 5 | 1533.917 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - TRIMMABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Crew removed the tree from the line and repaired the primary Conductors | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-10-31 16:30 | COMPLETED |  | 2015-10-31 13:23 | 2015-11-01 03:03 | 2015-11-01 03:04 | -121.5656 | 45.6539
5K50 | 1589491 | CPCC | CPCC983833 | PP | OR | HOOD RIVER | KENWOOD | OH_104400_64090347 | 2015 | Before | 2015-08-14 12:21 | 2015-08-14 13:32 | 5 | 356.333 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman found transformer fuse blown on pole 104402 due to squirrel and also found line fuse blown on pole 104400; Re-fused and they held. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2015-08-14 13:36 | 2015-08-14 14:56 | 2015-08-14 14:59 | -121.557 | 45.6713
5K50 | 1605938 | CPCC | CPCC995102 | PP | OR | HOOD RIVER | KENWOOD | TR_160201_64090727 | 2015 | Before | 2015-10-18 08:29 | 2015-10-18 11:42 | 1 | 192.917 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Crew changed out a bad cut out | DISTRIBUTION | CUSTOMER | AUTO | 2015-10-18 11:30 | COMPLETED |  | 2015-10-18 08:30 | 2015-10-18 16:13 | 2015-10-18 16:14 | -121.5859 | 45.653
5K50 | 1624433 | CPCC | CPCC1013306 | PP | OR | HOOD RIVER | KENWOOD | OH_310302_278580242 | 2015 | Before | 2015-12-17 20:14 | 2015-12-18 00:37 | 4 | 1052.6 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman removed a tree from the line and replaced a blown fuse | DISTRIBUTION | DEVICE | AUTO | 2015-12-17 23:30 | COMPLETED |  | 2015-12-17 20:14 | 2015-12-18 07:04 | 2015-12-18 07:09 | -121.6243 | 45.6113
5K50 | 1626273 | CPCC | CPCC1014911 | PP | OR | HOOD RIVER | KENWOOD | OH_160501_64090671 | 2015 | Before | 2015-12-21 17:55 | 2015-12-21 23:10 | 55 | 17292.917 | 0 | 0 | 1 | Y | N | N | N | Y | OR Coast Plus 12-21-2015 | WEATHER | WIND |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: burnt up strirup, replaced and closed in cutout. | DISTRIBUTION | DEVICE | AUTO | 2015-12-21 22:30 | COMPLETED |  | 2015-12-21 19:25 | 2015-12-22 16:40 | 2015-12-22 16:43 | -121.586 | 45.6573
5K50 | 1624929 | CPCC | CPCC1013742 | PP | OR | HOOD RIVER | KENWOOD | OH_160501_64090671 | 2015 | Before | 2015-12-19 15:27 | 2015-12-19 18:05 | 63 | 9971.85 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman found down wire due to failed fargo connector, crew made repairs and restored all customers | DISTRIBUTION | DEVICE | MANUAL | 2015-12-19 21:00 | COMPLETED |  | 2015-12-19 15:52 | 2015-12-19 18:08 | 2015-12-19 18:10 | -121.586 | 45.6573
5K50 | 1614059 | CPCC | CPCC1000993 | PP | OR | HOOD RIVER | KENWOOD | TR_061401_970000076 | 2015 | Before | 2015-11-19 09:35 | 2015-11-19 14:00 | 2 | 530.7 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | INTERFERENCE | VEHICLE ACCIDENT | POLE OH |  |  |  | SOURCE: De-energized to remove vehicle that hit pole across from this pole (see report # 2420509); crew to change out pole that was hit | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2015-11-19 09:35 | 2015-11-19 16:27 | 2015-11-19 16:29 | -121.6283 | 45.6001
5K50 | 1625952 | CPCC | CPCC1014943 | PP | OR | HOOD RIVER | KENWOOD | TR_187301_278580451 | 2015 | Before | 2015-12-21 20:25 | 2015-12-21 23:18 | 1 | 172.5 | 0 | 0 | 1 | Y | N | N | N | Y | OR Coast Plus 12-21-2015 | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  |  | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-12-21 23:30 | COMPLETED |  | 2015-12-21 20:25 | 2015-12-22 10:44 | 2015-12-22 10:48 | -121.6117 | 45.6544
5K50 | 1624431 | CPCC | CPCC1013303 | PP | OR | HOOD RIVER | KENWOOD | OH_131900_20360213 | 2015 | Before | 2015-12-17 17:30 | 2015-12-17 20:30 | 25 | 4500 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | ICE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman reported thatsnow and ice caused the line fuse to blow. Removed snow and ice off the line and a tree branch close to the line. Replaced blown fuse | DISTRIBUTION | DEVICE | AUTO | 2015-12-17 23:15 | COMPLETED |  | 2015-12-17 20:07 | 2015-12-18 07:04 | 2015-12-18 07:05 | -121.646 | 45.5777
5K50 | 1620983 | CPCC | CPCC1010986 | PP | OR | HOOD RIVER | KENWOOD | OH_089403_278580270 | 2015 | Before | 2015-12-13 16:59 | 2015-12-13 21:54 | 3 | 882.4 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Tap fuse blown @ FP# 089403 -- serviceman patrolling line -- bad cutout, repairs completed , all customers restored | DISTRIBUTION | DEVICE | AUTO | 2015-12-13 20:00 | COMPLETED |  | 2015-12-13 17:00 | 2015-12-14 04:58 | 2015-12-14 04:59 | -121.5864 | 45.6713
5K50 | 1618944 | CPCC | CPCC1005467 | PP | OR | HOOD RIVER | KENWOOD | OH_089403_278580270 | 2015 | Before | 2015-12-08 18:57 | 2015-12-09 02:00 | 39 | 16497.65 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Crew removed a tree from the line and repaired broken conductors Related to 1005275 | DISTRIBUTION | DEVICE | AUTO | 2015-12-09 05:00 | COMPLETED |  | 2015-12-09 01:49 | 2015-12-09 10:33 | 2015-12-09 10:34 | -121.5864 | 45.6713
5K50 | 1618948 | CPCC | CPCC1005275 | PP | OR | HOOD RIVER | KENWOOD | OH_089403_278580270 | 2015 | Before | 2015-12-08 19:28 | 2015-12-09 01:40 | 3 | 1116 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Crew removed a tree from the line and repaired broken conductors | DISTRIBUTION | DEVICE | AUTO | 2015-12-08 22:45 | COMPLETED |  | 2015-12-08 19:04 | 2015-12-09 10:34 | 2015-12-09 10:39 | -121.5864 | 45.6713
5K50 | 1618109 | CPCC | CPCC1004370 | PP | OR | HOOD RIVER | KENWOOD | OH_207700_1510574826 | 2015 | Before | 2015-12-06 23:34 | 2015-12-07 02:21 | 13 | 2159.517 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Tap fuse blown -- did callout for 1 man to help patrol -- cleared tree on the line & re-fused | DISTRIBUTION | DEVICE | AUTO | 2015-12-07 04:15 | COMPLETED |  | 2015-12-07 01:13 | 2015-12-07 03:25 | 2015-12-07 03:29 | -121.5907 | 45.6464
5K50 | 1625045 | CPCC | CPCC1013816 | PP | OR | HOOD RIVER | KENWOOD | OH_087400_278580272 | 2015 | Before | 2015-12-20 11:30 | 2015-12-20 16:31 | 3 | 901.25 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: B/O Underground, Crew called out, Repairs completed, all customers restored | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2015-12-20 12:16 | 2015-12-20 16:32 | 2015-12-20 16:34 | -121.5926 | 45.6713
5K50 | 1625955 | CPCC | CPCC1014905 | PP | OR | HOOD RIVER | KENWOOD | TR_016600_20360127 | 2015 | Before | 2015-12-21 18:59 | 2015-12-22 08:33 | 2 | 1627.2 | 0 | 0 | 1 | Y | N | N | N | Y | OR Coast Plus 12-21-2015 | TREES | TREE - NON-PREVENTABLE |  |  | POLE OH |  |  |  | SOURCE: Crew completed repairs to pole top( tree took/snapped top of pole off) | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2015-12-22 09:00 | COMPLETED |  | 2015-12-21 19:00 | 2015-12-22 10:44 | 2015-12-22 10:48 | -121.6375 | 45.6033
5K50 | 1613551 | CPCC | CPCC1000737 | PP | OR | HOOD RIVER | KENWOOD | TR_185100_970000047 | 2015 | Before | 2015-11-18 06:07 | 2015-11-18 09:36 | 1 | 208.917 | 0 | 0 | 1 | Y | N | N | N | Y | OR Coast Plus 11-17-2015 | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | SOURCE: b/o secondary ug; will go back to shop to get service saver to install | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-11-18 09:15 | COMPLETED |  | 2015-11-18 06:07 | 2015-11-18 14:40 | 2015-11-18 14:43 | -121.6177 | 45.5661
5K50 | 1613742 | CPCC | CPCC999230 | PP | OR | HOOD RIVER | KENWOOD | TR_203260_278580435 | 2015 | Before | 2015-11-17 13:08 | 2015-11-17 17:20 | 1 | 251.583 | 0 | 0 | 1 | Y | N | N | N | Y | OR Coast Plus 11-17-2015 | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: primary wire down - trees thru line | DISTRIBUTION | CUSTOMER | AUTO | 2015-11-17 16:15 | COMPLETED |  | 2015-11-17 13:09 | 2015-11-18 23:32 | 2015-11-18 23:33 | -121.5987 | 45.6393
5K50 | 1613754 | CPCC | CPCC999283 | PP | OR | HOOD RIVER | KENWOOD | OH_207700_1510574826 | 2015 | Before | 2015-11-17 13:48 | 2015-11-17 16:36 | 12 | 2023.6 | 0 | 0 | 1 | Y | N | N | N | Y | OR Coast Plus 11-17-2015 | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Crew made repairs to the overhead primary that was taken down by a tree | DISTRIBUTION | DEVICE | AUTO | 2015-11-17 17:15 | COMPLETED |  | 2015-11-17 14:14 | 2015-11-18 23:39 | 2015-11-18 23:43 | -121.5907 | 45.6464
5K50 | 1632703 | CPCC | CPCC1020587 | PP | OR | HOOD RIVER | KENWOOD | OH_072800_970000077 | 2016 | Before | 2016-01-20 08:16 | 2016-01-20 09:28 | 102 | 7340.6 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Found fuse blown on pole 072800; patrolled, didn't find anything; re-fused and it held. b/o fuse | DISTRIBUTION | DEVICE | AUTO | 2016-01-20 12:00 | COMPLETED |  | 2016-01-20 08:48 | 2016-01-20 13:15 | 2016-01-20 13:18 | -121.6268 | 45.5898
5K50 | 1624588 | CPCC | CPCC1013389 | PP | OR | HOOD RIVER | KENWOOD | TR_130301_20360179 | 2015 | Before | 2015-12-18 07:33 | 2015-12-18 09:50 | 1 | 137.567 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | SNOW, SLEET AND BLIZZARD | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: line down to a pump; will need to remove ice/limbs to get wire back up | DISTRIBUTION | CUSTOMER | AUTO | 2015-12-18 10:45 | COMPLETED |  | 2015-12-18 07:33 | 2015-12-18 13:47 | 2015-12-18 13:49 | -121.6485 | 45.5676
5K50 | 1624589 | CPCC | CPCC1013392 | PP | OR | HOOD RIVER | KENWOOD | TR_090205_1510600580 | 2015 | Before | 2015-12-18 07:53 | 2015-12-18 13:02 | 5 | 1545.25 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | ICE | TRANSFORMER OH |  |  |  | SOURCE: Tree fell and broke bushing, need to change out xfmr | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2015-12-18 12:30 | COMPLETED |  | 2015-12-18 07:53 | 2015-12-18 13:48 | 2015-12-18 13:49 | -121.5848 | 45.6669
5K50 | 1620135 | CPCC | CPCC1007142 | PP | OR | HOOD RIVER | KENWOOD | OH_131900_20360213 | 2015 | Before | 2015-12-11 07:51 | 2015-12-11 09:21 | 53 | 4445.433 | 0 | 0 | 2 | Y | N | N | N | Y | OR Coast Plus 12-08-2015 | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Found fuse open on pole 131900; patrolled, didn't find anything; re-fused and it held | DISTRIBUTION | DEVICE | MANUAL |  | COMPLETED |  | 2015-12-11 08:33 | 2015-12-11 14:39 | 2015-12-11 14:42 | -121.646 | 45.5777
5K50 | 1625953 | CPCC | CPCC1015178 | PP | OR | HOOD RIVER | KENWOOD | TR_160902_1510601584 | 2015 | Before | 2015-12-21 18:16 | 2015-12-22 00:16 | 4 | 1443.267 | 0 | 0 | 1 | Y | N | N | N | Y | OR Coast Plus 12-21-2015 | EQUIPMENT FAILURE | B/O EQUIPMENT | WEATHER | WIND | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: Associate to outage 1014911, burnt up strirup, replaced and closed in cutout. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-12-22 02:15 | COMPLETED |  | 2015-12-21 23:03 | 2015-12-22 10:44 | 2015-12-22 10:48 | -121.5859 | 45.6632
5K50 | 1619196 | CPCC | CPCC1005570 | PP | OR | HOOD RIVER | KENWOOD | Line Cut-99219 | 2015 | Before | 2015-12-09 04:05 | 2015-12-09 16:06 | 22 | 15878.133 | 0 | 0 | 1 | Y | N | N | N | Y | OR Coast Plus 12-08-2015 | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Line Cut at 080100 to isolate the fault | DISTRIBUTION | DEVICE | MANUAL | 2015-12-09 18:30 | COMPLETED |  | 2015-12-09 05:57 | 2015-12-09 16:57 | 2015-12-09 16:59 | -121.606 | 45.6669
5K50 | 1626274 | CPCC | CPCC1014549 | PP | OR | HOOD RIVER | KENWOOD | Line Cut-99488 | 2015 | Before | 2015-12-21 15:04 | 2015-12-21 16:24 | 691 | 55441.233 | 0 | 0 | 1 | Y | N | N | N | Y | OR Coast Plus 12-21-2015 | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: 69 CB 3K46 locked open -- crew will patrol | DISTRIBUTION | DEVICE | AUTO | 2015-12-21 18:15 | COMPLETED |  | 2015-12-21 15:08 | 2015-12-22 16:39 | 2015-12-22 16:43 | -121.5865 | 45.6538
5K50 | 1624706 | CPCC | CPCC1013546 | PP | OR | HOOD RIVER | KENWOOD | TR_090205_1510600580 | 2015 | Before | 2015-12-18 16:46 | 2015-12-18 18:14 | 1 | 87.367 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman cleared limb from Secondary neutral, reouted neutral, and restored all customers | DISTRIBUTION | CUSTOMER | AUTO | 2015-12-18 20:00 | COMPLETED |  | 2015-12-18 16:46 | 2015-12-18 18:43 | 2015-12-18 18:44 | -121.5848 | 45.6669
5K50 | 1620985 | CPCC | CPCC1011191 | PP | OR | HOOD RIVER | KENWOOD | OH_089403_278580270 | 2015 | Before | 2015-12-13 19:58 | 2015-12-13 21:53 | 39 | 4485.65 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | PLANNED OUTAGE |  |  |  | SOURCE: Crew made repairs to C phase Cutout, all customers restored | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2015-12-13 19:58 | 2015-12-14 04:59 | 2015-12-14 04:59 | -121.5864 | 45.6713
5K50 | 1613613 | CPCC | CPCC999222 | PP | OR | HOOD RIVER | KENWOOD | TR_169301_64090672 | 2015 | Before | 2015-11-17 12:56 | 2015-11-17 22:17 | 1 | 561.083 | 0 | 0 | 1 | Y | N | N | N | Y | OR Coast Plus 11-17-2015 | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Crews repaired down wires due to trees/wind, all customers restored | DISTRIBUTION | CUSTOMER | MANUAL | 2015-11-18 04:01 | COMPLETED |  | 2015-11-17 12:57 | 2015-12-02 15:55 | 2015-11-18 17:03 | -121.5656 | 45.6539
5K50 | 1625954 | CPCC | CPCC1015179 | PP | OR | HOOD RIVER | KENWOOD | TR_160801_64090339 | 2015 | Before | 2015-12-21 18:37 | 2015-12-22 00:17 | 1 | 340.133 | 0 | 0 | 1 | Y | N | N | N | Y | OR Coast Plus 12-21-2015 | EQUIPMENT FAILURE | B/O EQUIPMENT | WEATHER | WIND | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: Associate to outage 1014911, burnt up strirup, replaced and closed in cutout. | DISTRIBUTION | CUSTOMER | AUTO | 2015-12-22 02:15 | COMPLETED |  | 2015-12-21 23:03 | 2015-12-22 10:44 | 2015-12-22 10:48 | -121.5856 | 45.6621
5K50 | 1643982 | CPCC | CPCC1029237 | PP | OR | HOOD RIVER | KENWOOD | OH_169701_64090540 | 2016 | Before | 2016-03-07 11:42 | 2016-03-07 13:59 | 4 | 547.2 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Found fuse blown on pole 169701; removed tree branch | DISTRIBUTION | DEVICE | AUTO | 2016-03-07 14:45 | COMPLETED |  | 2016-03-07 11:42 | 2016-03-07 14:52 | 2016-03-07 14:57 | -121.5654 | 45.6603
5K50 | 1642032 | CPCC | CPCC1027179 | PP | OR | HOOD RIVER | KENWOOD | RC_292460_278580237 | 2016 | Before | 2016-02-28 11:32 | 2016-02-28 15:30 | 281 | 61100.383 | 0 | 0 | 2 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman reports tree across line, Crew requested, ARCOS callout initiated, only 1 taker, call in to duty supervisor. Isolated and restored 36 customers by opening solid blades at FP 316800 and closing Recloser, Repairs complete, all customers restored | DISTRIBUTION | DEVICE | AUTO | 2016-02-28 14:45 | COMPLETED |  | 2016-02-28 11:34 | 2016-02-28 15:50 | 2016-02-28 15:54 | -121.6023 | 45.6261
5K50 | 1635695 | CPCC | CPCC1022587 | PP | OR | HOOD RIVER | KENWOOD | SW_099060_64090562 | 2016 | Before | 2016-02-02 18:50 | 2016-02-03 03:40 | 108 | 27830.3 | 0 | 0 | 2 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | POLE OH |  |  |  | SOURCE: Crew replaced the broken pole PROSPER: Hazard | DISTRIBUTION | DEVICE | MANUAL | 2016-02-03 00:10 | COMPLETED |  | 2016-02-02 18:51 | 2016-02-04 14:17 | 2016-02-03 09:09 | -121.5654 | 45.6647
5K50 | 1638797 | CPCC | CPCC1025231 | PP | OR | HOOD RIVER | KENWOOD | OH_178701_278580340 | 2016 | Before | 2016-02-17 18:00 | 2016-02-17 21:39 | 21 | 1748.25 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Bad Cut Out at F/P 187305 | DISTRIBUTION | DEVICE | AUTO | 2016-02-17 21:15 | COMPLETED |  | 2016-02-17 18:00 | 2016-02-18 00:53 | 2016-02-18 00:58 | -121.5894 | 45.6609
5K50 | 1645350 | CPCC | CPCC1031066 | PP | OR | HOOD RIVER | KENWOOD | OH_183700_970000061 | 2016 | Before | 2016-03-11 15:44 | 2016-03-11 23:37 | 2 | 946.133 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: crew to make repairs | DISTRIBUTION | DEVICE | AUTO | 2016-03-11 18:45 | COMPLETED |  | 2016-03-11 15:44 | 2016-03-11 23:38 | 2016-03-11 23:42 | -121.6209 | 45.5747
5K50 | 1650534 | CPCC | CPCC1034982 | PP | OR | HOOD RIVER | KENWOOD | TR_099480_64090576 | 2016 | Before | 2016-04-01 18:05 | 2016-04-01 19:47 | 2 | 204.3 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman replaced a blown fuse at F/P 099360 | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2016-04-01 18:07 | 2016-04-02 06:41 | 2016-04-02 06:43 | -121.5671 | 45.6703
5K50 | 1655529 | CPCC | CPCC1041541 | PP | OR | HOOD RIVER | KENWOOD | TR_134703_20360200 | 2016 | Before | 2016-04-20 20:29 | 2016-04-21 01:11 | 1 | 281.683 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | POLE OH |  |  |  | SOURCE: Crew needed to change out pole due to vehicle accident, ARCOS calout initiated, Crew onsite, repairs underway, Pole changed out, all customers restored PROSPER: power out | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2016-04-21 02:30 | COMPLETED |  | 2016-04-20 20:30 | 2016-04-21 14:34 | 2016-04-21 01:17 | -121.6403 | 45.574
5K50 | 1646387 | CPCC | CPCC1032685 | PP | OR | HOOD RIVER | KENWOOD | OH_072800_970000077 | 2016 | Before | 2016-03-15 10:52 | 2016-03-15 15:20 | 175 | 36772.8 | 0 | 0 | 2 | Y | N | N | N | N |  | INTERFERENCE | OTHER UTILITY/CONTRACTOR |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: @ pole 072800 found fuses open; @ 1206 svcmn isolated at pole 017002 due to wire down to west. PROSPER: added from CPCC1032719 and CPCC1032714 | DISTRIBUTION | DEVICE | MANUAL | 2016-03-15 15:00 | COMPLETED |  | 2016-03-15 11:48 | 2016-03-17 10:26 | 2016-03-15 15:47 | -121.6268 | 45.5898
5K50 | 1642116 | CPCC | CPCC1027272 | PP | OR | HOOD RIVER | KENWOOD | OH_183700_970000061 | 2016 | Before | 2016-02-28 20:00 | 2016-02-29 02:48 | 2 | 816.367 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Crew repaired bad underground | DISTRIBUTION | DEVICE | AUTO | 2016-02-28 23:00 | COMPLETED |  | 2016-02-28 20:00 | 2016-03-01 13:27 | 2016-02-29 07:12 | -121.6209 | 45.5747
5K50 | 1662693 | CPCC | CPCC1044437 | PP | OR | HOOD RIVER | KENWOOD | TR_100903_64090349 | 2016 | Before | 2016-05-09 11:56 | 2016-05-09 13:25 | 2 | 178.567 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: b/o fuse replaced and holding | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2016-05-09 11:56 | 2016-05-09 13:40 | 2016-05-09 13:43 | -121.5641 | 45.6774
5K50 | 1661665 | CPCC | CPCC1043817 | PP | OR | HOOD RIVER | KENWOOD | TR_135902_20360219 | 2016 | Before | 2016-05-06 07:32 | 2016-05-06 08:50 | 1 | 78.017 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman replaced transformer fuse, no cause found, restored all customers | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2016-05-06 08:32 | 2016-05-06 11:24 | 2016-05-06 11:28 | -121.6384 | 45.578
5K50 | 1673998 | CPCC | CPCC1050903 | PP | OR | HOOD RIVER | KENWOOD | KWD_CB5K50 | 2016 | Before | 2016-06-13 17:46 | 2016-06-13 20:02 | 694 | 94187.367 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF FEED FROM SUPPLIER |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: The problem is a broken 115 kV Switch in the BPA Substation at Tucker | DISTRIBUTION | DEVICE | AUTO | 2016-06-13 21:00 | COMPLETED |  | 2016-06-13 18:03 | 2016-06-20 11:31 | 2016-06-15 02:13 | -121.5865 | 45.6538
5K50 | 1678116 | CPCC | CPCC1053363 | PP | OR | HOOD RIVER | KENWOOD | TR_163402_1510612180 | 2016 | Before | 2016-06-28 20:58 | 2016-06-28 22:05 | 1 | 66.467 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman refused Transformer Fuse blown due to Starlings, All customers restored | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2016-06-29 | COMPLETED |  | 2016-06-28 20:58 | 2016-06-28 22:44 | 2016-06-28 22:48 | -121.5783 | 45.6554
5K50 | 1665788 | CPCC | CPCC1045805 | PP | OR | HOOD RIVER | KENWOOD | OH_072300_970000038 | 2016 | Before | 2016-05-18 16:57 | 2016-05-18 17:07 | 29 | 307.4 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | PLANNED OUTAGE |  |  |  | SOURCE: Crews opened fuses to remove phone line wrapped around primary conductor, see outage 1045786 | DISTRIBUTION | DEVICE | AUTO | 2016-05-18 20:00 | COMPLETED |  | 2016-05-18 16:57 | 2016-05-18 18:00 | 2016-05-18 18:03 | -121.6256 | 45.5835
5K50 | 1706165 | CPCC | CPCC1072113 | PP | OR | HOOD RIVER | KENWOOD | TR_132404_20360183 | 2016 | Before | 2016-09-29 11:35 | 2016-09-29 12:12 | 1 | 36.383 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman replaced a blown fuse due to a Squirrel. F/P 132404 | DISTRIBUTION | CUSTOMER | AUTO | 2016-09-29 14:45 | COMPLETED |  | 2016-09-29 11:35 | 2016-09-29 13:49 | 2016-09-29 13:53 | -121.646 | 45.5697
5K50 | 1688162 | CPCC | CPCC1060515 | PP | OR | HOOD RIVER | KENWOOD | TR_169904_64090685 | 2016 | Before | 2016-07-29 07:46 | 2016-07-29 08:43 | 4 | 227.467 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Squirrel in xfmr. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2016-07-29 11:00 | COMPLETED |  | 2016-07-29 07:46 | 2016-07-29 14:40 | 2016-07-29 14:43 | -121.5654 | 45.6634
5K50 | 1739666 | CPCC | CPCC1107117 | PP | OR | HOOD RIVER | KENWOOD | Line Cut-105199 | 2017 | Before | 2017-01-19 05:02 | 2017-01-19 09:36 | 40 | 8190.934 | 0 | 0 | 3 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: Blown line fuse, cause was bad order connector where OH primary terminates to UG primary. | DISTRIBUTION | DEVICE | MANUAL | 2017-01-19 13:00 | COMPLETED |  | 2017-01-19 08:08 | 2017-01-19 10:32 | 2017-01-19 10:38 | -121.5908 | 45.6713
5K50 | 1745885 | CPCC | CPCC1113854 | PP | OR | HOOD RIVER | KENWOOD | TR_126402_20360154 | 2017 | Before | 2017-02-09 16:28 | 2017-02-09 17:29 | 6 | 365.2 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: replaced transformer fuse | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2017-02-09 16:28 | 2017-02-09 18:23 | 2017-02-09 18:23 | -121.6384 | 45.5841
5K50 | 1745453 | CPCC | CPCC1113177 | PP | OR | HOOD RIVER | KENWOOD | OH_310302_278580242 | 2017 | Before | 2017-02-08 13:12 | 2017-02-08 16:14 | 4 | 730.133 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: FUSE OPEN, PATROLING LINE floater, tie wire broke | DISTRIBUTION | DEVICE | AUTO | 2017-02-08 16:15 | COMPLETED |  | 2017-02-08 13:12 | 2017-02-08 18:25 | 2017-02-08 18:28 | -121.6243 | 45.6113
5K50 | 1745981 | CPCC | CPCC1113864 | PP | OR | HOOD RIVER | KENWOOD | TR_148203_20360122 | 2017 | Before | 2017-02-09 17:00 | 2017-02-09 18:45 | 1 | 105.467 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Replaced broken cutout | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2017-02-09 20:00 | COMPLETED |  | 2017-02-09 17:00 | 2017-02-10 02:44 | 2017-02-10 02:48 | -121.6535 | 45.5661
5K50 | 1748018 | CPCC | CPCC1115184 | PP | OR | HOOD RIVER | KENWOOD | OH_207700_1510574826 | 2017 | Before | 2017-02-17 12:44 | 2017-02-17 21:14 | 13 | 1416.133 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | POLE OH |  |  |  | SOURCE: pole top | DISTRIBUTION | DEVICE | MANUAL | 2017-02-17 18:00 | COMPLETED |  | 2017-02-17 12:51 | 2017-02-17 21:34 | 2017-02-17 21:39 | -121.5907 | 45.6464
5K50 | 1745829 | CPCC | CPCC1113698 | PP | OR | HOOD RIVER | KENWOOD | OH_310302_278580242 | 2017 | Before | 2017-02-09 10:23 | 2017-02-09 13:46 | 4 | 811 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown line fuse, serviceman needs to get side by side and patrol. | DISTRIBUTION | DEVICE | MANUAL | 2017-02-09 15:00 | COMPLETED |  | 2017-02-09 10:24 | 2017-02-09 16:29 | 2017-02-09 16:33 | -121.6243 | 45.6113
5K50 | 1778326 | CPCC | CPCC1142613 | PP | OR | HOOD RIVER | KENWOOD | TR_132304_20360173 | 2017 | Before | 2017-05-26 08:45 | 2017-05-26 09:33 | 1 | 47.95 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman found Open Fuse, Found No Cause, Refused and restored all customers | DISTRIBUTION | CUSTOMER | AUTO | 2017-05-26 11:45 | COMPLETED |  | 2017-05-26 08:46 | 2017-05-26 11:01 | 2017-05-26 11:03 | -121.646 | 45.5676
5K50 | 1757402 | CPCC | CPCC1122595 | PP | OR | HOOD RIVER | KENWOOD | OH_160501_64090671 | 2017 | Before | 2017-03-23 08:30 | 2017-03-23 09:33 | 127 | 7979.833 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: Junper burnt open at tap pole fp# 160501 -- crew making repairs | DISTRIBUTION | DEVICE | AUTO | 2017-03-23 12:00 | COMPLETED |  | 2017-03-23 08:36 | 2017-03-23 14:00 | 2017-03-23 14:03 | -121.586 | 45.6573
5K50 | 1778801 | CPCC | CPCC1143012 | PP | OR | HOOD RIVER | KENWOOD | OH_185401_970000044 | 2017 | Before | 2017-05-28 15:09 | 2017-05-28 18:11 | 18 | 3285 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Tree in line, wire down. Needs crew, Crew made repairs and restored all customers | DISTRIBUTION | DEVICE | MANUAL | 2017-05-28 20:15 | COMPLETED |  | 2017-05-28 15:14 | 2017-05-28 18:31 | 2017-05-28 18:33 | -121.6185 | 45.5697
5K50 | 1779166 | CPCC | CPCC1143208 | PP | OR | HOOD RIVER | KENWOOD | TR_132301_20360174 | 2017 | Before | 2017-05-30 07:59 | 2017-05-30 10:02 | 2 | 245.667 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Replaced switch | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2017-05-30 12:30 | COMPLETED |  | 2017-05-30 09:16 | 2017-05-30 12:46 | 2017-05-30 12:48 | -121.646 | 45.5683
5K50 | 1783867 | CPCC | CPCC1145934 | PP | OR | HOOD RIVER | KENWOOD | TR_134303_20360194 | 2017 | Before | 2017-06-13 06:58 | 2017-06-13 08:04 | 1 | 66.417 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman replaced a blown transformer fuse | DISTRIBUTION | CUSTOMER | AUTO | 2017-06-13 10:00 | COMPLETED |  | 2017-06-13 06:58 | 2017-06-13 12:00 | 2017-06-13 12:03 | -121.641 | 45.5679
5K50 | 1785860 | CPCC | CPCC1146937 | PP | OR | HOOD RIVER | KENWOOD | TR_134703_20360200 | 2017 | Before | 2017-06-19 13:24 | 2017-06-19 14:25 | 1 | 60.8 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | SOURCE: serviceman reports starling caused transformer fuse to open, refused and customer restored | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2017-06-19 16:30 | COMPLETED |  | 2017-06-19 13:24 | 2017-06-19 17:18 | 2017-06-19 17:19 | -121.6403 | 45.574
5K50 | 1788566 | CPCC | CPCC1149080 | PP | OR | HOOD RIVER | KENWOOD | TR_129800_20360169 | 2017 | Before | 2017-06-26 19:34 | 2017-06-26 21:06 | 1 | 91.567 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown transformer fuse, serviceman refused and restored, no cause found | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2017-06-26 22:45 | COMPLETED |  | 2017-06-26 19:35 | 2017-06-26 22:39 | 2017-06-26 22:43 | -121.6313 | 45.5915
5K50 | 1792054 | CPCC | CPCC1150813 | PP | OR | HOOD RIVER | KENWOOD | OH_153900_64090557 | 2017 | Before | 2017-07-06 19:20 | 2017-07-06 20:25 | 4 | 258.8 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman refused line Fuse blown due to squirrel, restored all customers | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2017-07-06 20:10 | 2017-07-06 21:08 | 2017-07-06 21:13 | -121.5579 | 45.6637
5K50 | 1792055 | CPCC | CPCC1150764 | PP | OR | HOOD RIVER | KENWOOD | OH_167500_64090680 | 2017 | Before | 2017-07-06 11:35 | 2017-07-06 13:31 | 2 | 231.367 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | DIG-IN (NON-PACIFICORP PERSONNEL) |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: repairs completed. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2017-07-06 11:35 | 2017-07-06 21:08 | 2017-07-06 21:13 | -121.5699 | 45.6574
5K50 | 1797739 | CPCC | CPCC1154303 | PP | OR | HOOD RIVER | KENWOOD | TR_090003_64090316 | 2017 | Before | 2017-07-23 18:00 | 2017-07-23 19:51 | 1 | 111.45 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman refused transformer fuse blown due to Starling, restored all customers | DISTRIBUTION | CUSTOMER | AUTO | 2017-07-23 21:00 | COMPLETED |  | 2017-07-23 18:00 | 2017-07-23 20:39 | 2017-07-23 20:43 | -121.5859 | 45.6641
5K50 | 1801704 | CPCC | CPCC1156648 | PP | OR | HOOD RIVER | KENWOOD | TR_090003_64090316 | 2017 | Before | 2017-08-03 19:52 | 2017-08-03 20:47 | 1 | 54.833 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: starling blew fuse | DISTRIBUTION | CUSTOMER | AUTO | 2017-08-03 22:00 | COMPLETED |  | 2017-08-03 19:53 | 2017-08-04 11:19 | 2017-08-04 11:23 | -121.5859 | 45.6641
5K50 | 1808452 | CPCC | CPCC1160668 | PP | OR | HOOD RIVER | KENWOOD | OH_176701_1510384931 | 2017 | Before | 2017-08-26 05:13 | 2017-08-26 10:02 | 3 | 865.6 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: bad UG primary, need 3 man crew to make repairs, radial fed, investigating what section is bad | DISTRIBUTION | DEVICE | MANUAL | 2017-08-26 13:45 | COMPLETED |  | 2017-08-26 05:13 | 2017-08-26 15:26 | 2017-08-26 15:28 | -121.593 | 45.6609
5K50 | 1809551 | CPCC | CPCC1161302 | PP | OR | HOOD RIVER | KENWOOD | TR_099602_64090568 | 2017 | Before | 2017-08-30 10:22 | 2017-08-30 12:08 | 1 | 106.2 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: b/o cut out | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2017-08-30 13:00 | COMPLETED |  | 2017-08-30 10:22 | 2017-08-30 15:31 | 2017-08-30 15:33 | -121.5657 | 45.6735
5K50 | 1811715 | CPCC | CPCC1162346 | PP | OR | HOOD RIVER | KENWOOD | TR_165900_64090692 | 2017 | Before | 2017-09-07 10:46 | 2017-09-07 11:58 | 10 | 721 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown transformer fuse caused by squirrel | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2017-09-07 12:45 | COMPLETED |  | 2017-09-07 10:46 | 2017-09-07 13:19 | 2017-09-07 13:23 | -121.5749 | 45.6639
5K50 | 1811768 | CPCC | CPCC1162459 | PP | OR | HOOD RIVER | KENWOOD | TR_163600_64090336 | 2017 | Before | 2017-09-07 13:33 | 2017-09-07 15:00 | 1 | 87.133 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown transformer fuse, cause was starling. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2017-09-07 17:00 | COMPLETED |  | 2017-09-07 14:24 | 2017-09-07 16:14 | 2017-09-07 16:18 | -121.5779 | 45.6595
5K50 | 1814943 | CPCC | CPCC1164358 | PP | OR | HOOD RIVER | KENWOOD | TR_158901_64090556 | 2017 | Before | 2017-09-18 18:07 | 2017-09-18 18:46 | 6 | 231.7 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | SOURCE: squirrel caused transformer fuse to open, tested, refused and customer has been restored | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2017-09-18 20:15 | COMPLETED |  | 2017-09-18 18:08 | 2017-09-18 22:24 | 2017-09-18 22:28 | -121.5479 | 45.6637
5K50 | 1816819 | CPCC | CPCC1165347 | PP | OR | HOOD RIVER | KENWOOD | TR_165900_64090692 | 2017 | Before | 2017-09-25 11:59 | 2017-09-25 13:37 | 1 | 98.75 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman refused transformer fuse blown due to squirrel | DISTRIBUTION | CUSTOMER | MANUAL | 2017-09-25 16:00 | COMPLETED |  | 2017-09-25 11:59 | 2017-09-25 18:51 | 2017-09-25 18:53 | -121.5749 | 45.6639
5K50 | 1818375 | CPCC | CPCC1166573 | PP | OR | HOOD RIVER | KENWOOD | TR_090701_64090661 | 2017 | Before | 2017-10-02 12:24 | 2017-10-02 14:01 | 1 | 97.3 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: found blown fuse on FP 090701; due to squirrel | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2017-10-02 18:00 | COMPLETED |  | 2017-10-02 12:24 | 2017-10-02 16:52 | 2017-10-02 16:54 | -121.5858 | 45.6745
5K50 | 1819032 | CPCC | CPCC1166855 | PP | OR | HOOD RIVER | KENWOOD | OH_292401_278580380 | 2017 | Before | 2017-10-04 12:53 | 2017-10-04 18:02 | 4 | 1236.533 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: open dip fuse at FP 292401, radial with 2 transformers, bad UG primary | DISTRIBUTION | DEVICE | MANUAL | 2017-10-04 19:00 | COMPLETED |  | 2017-10-04 12:53 | 2017-10-04 19:08 | 2017-10-04 19:09 | -121.6006 | 45.627
5K50 | 1823826 | CPCC | CPCC1170078 | PP | OR | HOOD RIVER | KENWOOD | OH_292300_1510574811 | 2017 | Before | 2017-10-22 03:10 | 2017-10-22 07:53 | 21 | 5937.4 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Crew removed tree limbs from the line and repaired primary conductor | DISTRIBUTION | DEVICE | MANUAL | 2017-10-22 12:30 | COMPLETED |  | 2017-10-22 03:10 | 2017-10-22 11:07 | 2017-10-22 11:09 | -121.6022 | 45.6258
5K50 | 1831373 | CPCC | CPCC1175832 | PP | OR | HOOD RIVER | KENWOOD | OH_185401_970000044 | 2017 | Before | 2017-11-21 10:19 | 2017-11-21 18:44 | 18 | 9097.5 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Tree through line, wire down, broken pole, broken transformer | DISTRIBUTION | DEVICE | MANUAL | 2017-11-21 19:32 | COMPLETED |  | 2017-11-21 10:23 | 2017-11-22 05:02 | 2017-11-22 05:03 | -121.6185 | 45.5697
5K50 | 1831475 | CPCC | CPCC1176012 | PP | OR | HOOD RIVER | KENWOOD | TR_134101_20360192 | 2017 | Before | 2017-11-22 11:38 | 2017-11-22 13:06 | 1 | 87.517 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD SUSPECTED, NO MORTALITY |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: found transformer fuse open on FP 134703 due to non-protected bird | DISTRIBUTION | CUSTOMER | MANUAL | 2017-11-22 14:45 | COMPLETED |  | 2017-11-22 11:38 | 2017-11-22 14:07 | 2017-11-22 14:09 | -121.641 | 45.5655
5K50 | 1841804 | CPCC | CPCC1183563 | PP | OR | HOOD RIVER | KENWOOD | OH_365500_981200015 | 2018 | Before | 2018-01-12 00:26 | 2018-01-12 05:16 | 1 | 289.933 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: serviceman reports he believes wind caused phases to slap together that caused fuse at FP 365500 to open, patrolled line out on foot, no other cause found, refused and customer has been restored | DISTRIBUTION | DEVICE | MANUAL | 2018-01-12 06:00 | COMPLETED |  | 2018-01-12 00:30 | 2018-01-12 05:17 | 2018-01-12 05:19 | -121.6365 | 45.6148
5K50 | 1843841 | CPCC | CPCC1185682 | PP | OR | HOOD RIVER | KENWOOD | RC_292460_278580237 | 2018 | Before | 2018-01-23 06:28 | 2018-01-23 07:59 | 293 | 26765.55 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: tree fell into line | DISTRIBUTION | DEVICE | AUTO | 2018-01-23 10:30 | COMPLETED |  | 2018-01-23 06:29 | 2018-01-23 07:59 | 2018-01-23 08:04 | -121.6023 | 45.6261
5K50 | 1847086 | CPCC | CPCC1187848 | PP | OR | HOOD RIVER | KENWOOD | OH_179901__4507493 | 2018 | Before | 2018-02-09 14:09 | 2018-02-09 15:09 | 2 | 120.267 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: limb possibility, refused | DISTRIBUTION | DEVICE | AUTO | 2018-02-09 17:45 | COMPLETED |  | 2018-02-09 15:02 | 2018-02-09 16:21 | 2018-02-09 16:24 | -121.5863 | 45.6631
5K50 | 1848334 | CPCC | CPCC1188354 | PP | OR | HOOD RIVER | KENWOOD | OH_167500_64090680 | 2018 | Before | 2018-02-16 10:00 | 2018-02-16 10:30 | 2 | 60 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | DIG-IN (NON-PACIFICORP PERSONNEL) |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Crew repaired damaged primary cable due to a backhoe | DISTRIBUTION | DEVICE | AUTO | 2018-02-16 12:15 | COMPLETED |  | 2018-02-16 10:04 | 2018-02-16 14:30 | 2018-02-16 14:34 | -121.5699 | 45.6574
5K50 | 1848974 | CPCC | CPCC1188926 | PP | OR | HOOD RIVER | KENWOOD | OH_070802__3864317 | 2018 | Before | 2018-02-18 18:22 | 2018-02-18 23:35 | 55 | 17215.917 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: Jumper burned off @ fp# 019003 -- ran Arcos for a crew | DISTRIBUTION | DEVICE | MANUAL | 2018-02-19 01:00 | COMPLETED |  | 2018-02-18 20:40 | 2018-02-19 04:41 | 2018-02-19 04:44 | -121.6297 | 45.5896
5K50 | 1848973 | CPCC | CPCC1188945 | PP | OR | HOOD RIVER | KENWOOD | OH_070802__3864317 | 2018 | Before | 2018-02-18 23:22 | 2018-02-18 23:35 | 116 | 1515.733 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Part of outage# 1188926 -- opened other 2 phases to make repairs | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2018-02-18 23:22 | 2018-02-19 04:41 | 2018-02-19 04:44 | -121.6297 | 45.5896
5K50 | 1849171 | CPCC | CPCC1188659 | PP | OR | HOOD RIVER | KENWOOD | OH_070802__3864317 | 2018 | Before | 2018-02-17 17:32 | 2018-02-17 23:59 | 169 | 43444.267 | 0 | 0 | 2 | Y | N | N | N | N |  | WEATHER | WIND |  |  | CROSS ARM OH |  |  |  | SOURCE: crew replacing burned crossarm | DISTRIBUTION | DEVICE | MANUAL | 2018-02-18 04:00 | COMPLETED |  | 2018-02-17 17:42 | 2018-02-19 12:37 | 2018-02-19 12:39 | -121.6297 | 45.5896
5K50 | 1864267 | CPCC | CPCC1199146 | PP | OR | HOOD RIVER | KENWOOD | TR_137900_20360224 | 2018 | Before | 2018-04-19 16:47 | 2018-04-19 18:06 | 7 | 553.583 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: reports open fuse due to squirrel contact, no damage, refused and restored | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2018-04-19 20:00 | COMPLETED |  | 2018-04-19 16:47 | 2018-04-19 18:06 | 2018-04-19 18:10 | -121.6343 | 45.5782
5K50 | 1873569 | CPCC | CPCC1204774 | PP | OR | HOOD RIVER | KENWOOD | TR_130301_20360179 | 2018 | Before | 2018-06-04 07:30 | 2018-06-04 08:59 | 1 | 89.467 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: B/O Connection at weatherhead | DISTRIBUTION | CUSTOMER | MANUAL | 2018-06-04 11:30 | COMPLETED |  | 2018-06-04 07:30 | 2018-06-04 17:08 | 2018-06-04 17:10 | -121.6485 | 45.5676
5K50 | 1874929 | CPCC | CPCC1205718 | PP | OR | HOOD RIVER | KENWOOD | TR_099005_64090640 | 2018 | Before | 2018-06-09 18:22 | 2018-06-09 20:17 | 1 | 114.317 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: bad order connector replaced. | DISTRIBUTION | CUSTOMER | MANUAL | 2018-06-09 21:15 | COMPLETED |  | 2018-06-09 18:22 | 2018-06-09 23:00 | 2018-06-09 23:05 | -121.5655 | 45.6643
5K50 | 1876392 | CPCC | CPCC1206546 | PP | OR | HOOD RIVER | KENWOOD | TR_163402_1510612180 | 2018 | Before | 2018-06-15 08:16 | 2018-06-15 09:03 | 1 | 47.033 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman reports that outage was due to bird | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2018-06-15 11:00 | COMPLETED |  | 2018-06-15 08:16 | 2018-06-15 17:36 | 2018-06-15 17:40 | -121.5783 | 45.6554
5K50 | 1876611 | CPCC | CPCC1206764 | PP | OR | HOOD RIVER | KENWOOD | KWD_CB5K50 | 2018 | Before | 2018-06-16 15:59 | 2018-06-16 18:25 | 721 | 105049.7 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: loss of transmission, Tucker CB 3K48 tripped open(16:09 r4r), located broken 69kV inuslator due to car pole, crew and flaggers needed, arcos(16:48 r4r) | DISTRIBUTION | DEVICE | MANUAL | 2018-06-16 21:45 | COMPLETED |  | 2018-06-16 16:05 | 2018-06-19 11:34 | 2018-06-16 20:40 | -121.5863 | 45.6537
5K50 | 1878103 | CPCC | CPCC1210940 | PP | OR | HOOD RIVER | KENWOOD | TR_199900_278580442 | 2018 | Before | 2018-06-20 20:23 | 2018-06-21 01:35 | 3 | 934.6 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman reports blown transformer fuse. Fuse replaced and service restored. | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2018-06-21 05:00 | COMPLETED |  | 2018-06-20 20:23 | 2018-06-21 05:54 | 2018-06-21 05:55 | -121.6073 | 45.6494
5K50 | 1889347 | CPCC | CPCC1218695 | PP | OR | HOOD RIVER | KENWOOD | TR_090003_64090316 | 2018 | Before | 2018-07-30 20:43 | 2018-07-30 21:57 | 1 | 74.067 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: replaced fuse blown due to Starling | DISTRIBUTION | CUSTOMER | AUTO | 2018-07-30 23:15 | COMPLETED |  | 2018-07-30 20:43 | 2018-07-31 05:51 | 2018-07-31 05:55 | -121.5859 | 45.6641
5K50 | 1893127 | CPCC | CPCC1220882 | PP | OR | HOOD RIVER | KENWOOD | TR_090003_64090316 | 2018 | Before | 2018-08-14 17:06 | 2018-08-14 18:04 | 1 | 57.7 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown fuse due to Sparrow, refused and restored | DISTRIBUTION | CUSTOMER | AUTO | 2018-08-14 19:45 | COMPLETED |  | 2018-08-14 17:06 | 2018-08-14 18:13 | 2018-08-14 18:15 | -121.5859 | 45.6641
5K50 | 1899143 | CPCC | CPCC1226239 | PP | OR | HOOD RIVER | KENWOOD | TR_147202_20360238 | 2018 | Before | 2018-09-08 00:52 | 2018-09-08 01:07 | 1 | 15.5 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: PART OF OUTAGE 2964537 | DISTRIBUTION | CUSTOMER | AUTO | 2018-09-08 03:30 | COMPLETED |  | 2018-09-08 00:52 | 2018-09-08 01:34 | 2018-09-08 01:40 | -121.6556 | 45.5654
5K50 | 1899342 | CPCC | CPCC1226382 | PP | OR | HOOD RIVER | KENWOOD | TR_145201_20360235 | 2018 | Before | 2018-09-08 21:39 | 2018-09-09 00:29 | 1 | 169.833 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: squirrel | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2018-09-09 01:30 | COMPLETED |  | 2018-09-08 21:39 | 2018-09-09 05:16 | 2018-09-09 05:20 | -121.6591 | 45.5648
5K50 | 1900108 | CPCC | CPCC1226827 | PP | OR | HOOD RIVER | KENWOOD | OH_160900_64090669 | 2018 | Before | 2018-09-12 13:30 | 2018-09-12 13:50 | 2 | 39.7 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | POLE OH |  |  |  | SOURCE: See outgae 1226825 pole fire. Repairs made. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2018-09-12 13:30 | 2018-09-12 18:24 | 2018-09-12 18:25 | -121.5859 | 45.6637
5K50 | 1902887 | CPCC | CPCC1230686 | PP | OR | HOOD RIVER | KENWOOD | TR_184001_1020122079 | 2018 | Before | 2018-09-24 18:18 | 2018-09-24 19:12 | 1 | 54.033 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: blowen fuse - refused and powe back on | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2018-09-24 21:00 | COMPLETED |  | 2018-09-24 18:18 | 2018-09-24 20:51 | 2018-09-24 20:55 | -121.6202 | 45.5639
5K50 | 1923812 | CPCC | CPCC1252475 | PP | OR | HOOD RIVER | KENWOOD | OH_072300_970000038 | 2018 | After | 2018-12-30 00:54 | 2018-12-30 05:46 | 28 | 8202.6 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: serviceman reports a blown fuse, patrolling for cause, serviceman reports wire down due to tree. Repairs made customers are back in service PROSPER: tree, wind | DISTRIBUTION | DEVICE | MANUAL | 2018-12-30 07:15 | COMPLETED |  | 2018-12-30 00:54 | 2018-12-31 08:10 | 2018-12-30 07:00 | -121.6256 | 45.5835
5K50 | 1923857 | CPCC | CPCC1252487 | PP | OR | HOOD RIVER | KENWOOD | OH_179261_278580324 | 2018 | After | 2018-12-30 03:01 | 2018-12-30 14:06 | 20 | 13282.667 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: serviceman reports that there is a large tree through the line, getting a tree crew to remove the tree to make repairs to conductor damaged by the tree PROSPER: tree, wind | DISTRIBUTION | DEVICE | MANUAL | 2018-12-30 15:00 | COMPLETED |  | 2018-12-30 04:04 | 2018-12-31 08:10 | 2018-12-30 14:20 | -121.5864 | 45.653
5K50 | 1925003 | CPCC | CPCC1253039 | PP | OR | HOOD RIVER | KENWOOD | TR_103501_64090372 | 2019 | After | 2019-01-03 15:48 | 2019-01-03 16:58 | 1 | 70.017 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Broken Fuse, Serviceman replaced and restored | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2019-01-03 15:48 | 2019-01-03 18:49 | 2019-01-03 18:50 | -121.5579 | 45.6713
5K50 | 1930649 | CPCC | CPCC1257982 | PP | OR | HOOD RIVER | KENWOOD | TR_101800_64090350 | 2019 | After | 2019-01-25 13:25 | 2019-01-25 15:05 | 6 | 597.3 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown fuse, caused by squirrel | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2019-01-25 16:15 | COMPLETED |  | 2019-01-25 13:25 | 2019-01-25 18:08 | 2019-01-25 18:10 | -121.563 | 45.676
5K50 | 1934965 | CPCC | CPCC1261140 | PP | OR | HOOD RIVER | KENWOOD | KWD_CB5K50 | 2019 | After | 2019-02-11 23:33 | 2019-02-12 01:01 | 830 | 72971.11 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE | WEATHER | SNOW, SLEET AND BLIZZARD | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Open SW 3K12 at Willard Johnson and energized from CB 3K48 at Tucker at 0101 on 2/12/19 Line patrol in progress from Willard Johnson to Powerdale | DISTRIBUTION | DEVICE | AUTO | 2019-02-12 02:30 | COMPLETED |  | 2019-02-11 23:38 | 2019-02-18 09:12 | 2019-02-12 06:40 | -121.5867 | 45.6536
5K50 | 1935244 | CPCC | CPCC1261506 | PP | OR | HOOD RIVER | KENWOOD | OH_185401_970000044 | 2019 | After | 2019-02-13 03:10 | 2019-02-13 08:20 | 19 | 5875.75 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Line Fuse Open, Tree thru line, 2 Spans of wire down, Crew to repair | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2019-02-13 03:11 | 2019-02-13 11:13 | 2019-02-13 11:15 | -121.6185 | 45.5697
5K50 | 1938447 | CPCC | CPCC1263967 | PP | OR | HOOD RIVER | KENWOOD | TR_136900_20360222 | 2019 | After | 2019-02-24 12:41 | 2019-02-24 16:19 | 1 | 217.483 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Burned off hot leg of transformer | DISTRIBUTION | CUSTOMER | MANUAL | 2019-02-24 17:30 | COMPLETED |  | 2019-02-24 12:41 | 2019-02-24 18:59 | 2019-02-24 19:00 | -121.6366 | 45.5781
5L82 | 602039 | CPCC | CPCC398958 | PP | CA | TULELAKE | TULELAKE | TR_037000_1890031790 | 2007 | Before | 2007-02-11 03:54 | 2007-02-11 07:34 | 1 | 219.867 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: b/o cut out | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 623163 | CPCC | CPCC425926 | PP | CA | TULELAKE | TULELAKE | TR_365400_1890067791 | 2007 | Before | 2007-07-07 08:58 | 2007-07-07 09:02 | 0 | 0 | 2 | 6.433 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | PROSPER: refused | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 619312 | CPCC | CPCC420730 | PP | CA | TULELAKE | TULELAKE | TR_364400_1890073506 | 2007 | Before | 2007-06-04 18:57 | 2007-06-04 19:12 | 1 | 15.067 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: associate to 420702 | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 623800 | CPCC | CPCC427184 | PP | CA | TULELAKE | TULELAKE | TR_074600_1890044258 | 2007 | Before | 2007-07-11 15:29 | 2007-07-12 17:05 | 1 | 1535.783 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | PROSPER: b/o xfrmr, DHaggard to arrange for crew to complete | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 619145 | CPCC | CPCC421872 | PP | CA | TULELAKE | TULELAKE | TR_326200_1890076274 | 2007 | Before | 2007-06-13 06:59 | 2007-06-13 09:00 | 1 | 120.967 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Blown fuse on 3 phase bank Refused and held | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 613219 | CPCC | CPCC412693 | PP | CA | TULELAKE | TULELAKE | OH_073901_1890034153 | 2007 | Before | 2007-04-05 06:43 | 2007-04-05 08:31 | 25 | 2695 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD SUSPECTED, NO MORTALITY |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Geese in area, but unknown cause Patrolled found nothing | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4494 | 41.9363
5L82 | 614641 | CPCC | CPCC418022 | PP | CA | TULELAKE | TULELAKE | TR_257900_1890062548 | 2007 | Before | 2007-05-17 09:50 | 2007-05-17 15:30 | 2 | 679.5 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | PROSPER: cut out to be changed, bird gaurd to be installed, also bad order xfmr. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 626427 | CPCC | CPCC425700 | PP | CA | TULELAKE | TULELAKE | TUL_CB5L82 | 2007 | Before | 2007-07-06 20:07 | 2007-07-06 22:41 | 500 | 76775 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE | WEATHER | LIGHTNING | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4714 | 41.9534
5L82 | 625019 | CPCC | CPCC424658 | PP | CA | TULELAKE | TULELAKE | TR_015801_1890026814 | 2007 | Before | 2007-07-02 12:01 | 2007-07-02 12:07 | 1 | 6.317 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | CROSS ARM OH |  |  |  | PROSPER: bad connectivity, associated to outage 424651 | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 629094 | CPCC | CPCC430402 | PP | CA | TULELAKE | TULELAKE | LINECUT-24136 | 2007 | Before | 2007-07-18 13:38 | 2007-07-18 14:59 | 1 | 80.267 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | INTERFERENCE | VEHICLE ACCIDENT | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Serviceman opened the jumpers on pole# 256200 to make repairs to the overhead primary neutral that was taken down by a piece of equipment. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.3457 | 41.9679
5L82 | 627582 | CPCC | CPCC431919 | PP | CA | TULELAKE | TULELAKE | TR_082201_1890034408 | 2007 | Before | 2007-07-26 07:50 | 2007-07-26 10:10 | 1 | 140.417 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Replacing service | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 610816 | CPCC | CPCC413244 | PP | CA | TULELAKE | TULELAKE | TUL_CB5L82 | 2007 | Before | 2007-04-08 14:08 | 2007-04-08 14:14 | 500 | 3000 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Semi hit pole at HWY 39 and Mattney | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4714 | 41.9534
5L82 | 605196 | CPCC | CPCC397494 | PP | CA | TULELAKE | TULELAKE | TR_196700_1890070549 | 2007 | Before | 2007-02-03 16:04 | 2007-02-03 18:12 | 1 | 128.55 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Customer's tractor tore down their own service and damaged their panel. Associate to 397496 | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 610766 | CPCC | CPCC412211 | PP | CA | TULELAKE | TULELAKE | OH_070200_1890037468 | 2007 | Before | 2007-03-31 11:47 | 2007-03-31 14:02 | 6 | 809.7 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Unknown cause | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.457 | 41.9251
5L82 | 648685 | CPCC | CPCC451399 | PP | CA | TULELAKE | TULELAKE | TR_324901_1890076093 | 2007 | Before | 2007-10-31 14:42 | 2007-10-31 15:29 | 1 | 46.967 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Haggard out today - Metcalf enroute Metcalf repaired | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 641254 | CPCC | CPCC443084 | PP | CA | TULELAKE | TULELAKE | TR_219502_1890036328 | 2007 | Before | 2007-09-22 14:51 | 2007-09-22 15:24 | 1 | 33.233 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | CIRCUIT BREAKER SUB |  |  |  | PROSPER: b/o connectivity Lakeview CB 5L100 opened, cause unknown | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 642605 | CPCC | CPCC443203 | PP | CA | TULELAKE | TULELAKE | TR_035000_1890031796 | 2007 | Before | 2007-09-24 07:59 | 2007-09-24 11:18 | 2 | 398.067 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: Broken cutout and will need crew | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 651403 | CPCC | CPCC460422 | PP | CA | TULELAKE | TULELAKE | TR_142904_1890038046 | 2007 | Before | 2007-12-02 19:55 | 2007-12-02 21:38 | 1 | 103.133 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: District Lineman refused on pole A-6239 and it is holding. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 656247 | CPCC | CPCC473325 | PP | CA | TULELAKE | TULELAKE | TR_015801_1890026814 | 2008 | Before | 2008-01-04 17:28 | 2008-01-04 19:52 | 1 | 144.367 | 0 | 0 | 1 | Y | N | N | N | Y | 732 - 2008-01-04 to 2008-01-08 CA Tulelake | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Wire down here on pole A 3297. Bruner to help restore. Bunny | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 656729 | CPCC | CPCC469567 | PP | CA | TULELAKE | TULELAKE | OH_073901_1890034153 | 2008 | Before | 2008-01-03 08:49 | 2008-01-03 15:37 | 29 | 11834.417 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Wire down at A 6818 Tree limb thru wire | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4494 | 41.9363
5L82 | 634323 | CPCC | CPCC434585 | PP | CA | TULELAKE | TULELAKE | OH_070200_1890037468 | 2007 | Before | 2007-08-10 16:03 | 2007-08-10 16:59 | 6 | 338.9 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: refused | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.457 | 41.9251
5L82 | 636194 | CPCC | CPCC438901 | PP | CA | TULELAKE | TULELAKE | TR_196700_1890070549 | 2007 | Before | 2007-08-31 17:38 | 2007-08-31 22:22 | 1 | 283.8 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: arrestor jumper | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 675380 | CPCC | CPCC498039 | PP | CA | TULELAKE | TULELAKE | OH_070200_1890037468 | 2008 | Before | 2008-04-27 07:44 | 2008-04-27 09:58 | 6 | 804.8 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD SUSPECTED, NO MORTALITY |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused tap line ok. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.457 | 41.9251
5L82 | 675387 | CPCC | CPCC498123 | PP | CA | TULELAKE | TULELAKE | OH_070200_1890037468 | 2008 | Before | 2008-04-27 13:23 | 2008-04-27 14:55 | 6 | 546.7 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD SUSPECTED, NO MORTALITY |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: no dead body - cause assumed to be Canadian Geese per SLiguori | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.457 | 41.9251
5L82 | 672262 | CPCC | CPCC501576 | PP | CA | TULELAKE | TULELAKE | TR_022200_1890031189 | 2008 | Before | 2008-05-14 14:40 | 2008-05-14 15:49 | 2 | 136.833 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: nothing found, refused | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 671184 | CPCC | CPCC501800 | PP | CA | TULELAKE | TULELAKE | OH_093902_1890032525 | 2008 | Before | 2008-05-15 13:23 | 2008-05-15 13:28 | 2 | 11.433 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: open fuses, serviceman patrolling. refused at pole A 8238 and holding | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4122 | 41.9358
5L82 | 674821 | CPCC | CPCC497985 | PP | CA | TULELAKE | TULELAKE | TR_362103_1890067520 | 2008 | Before | 2008-04-26 10:45 | 2008-04-26 12:30 | 2 | 208.3 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused transformer ok. Cause is unknown. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 674544 | CPCC | CPCC497924 | PP | CA | TULELAKE | TULELAKE | TR_292900_1890075228 | 2008 | Before | 2008-04-25 15:59 | 2008-04-25 18:31 | 1 | 152.017 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: Serviceman replaced broken jumper to top of fused cutout. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 670895 | CPCC | CPCC495152 | PP | CA | TULELAKE | TULELAKE | TR_130900_1890037574 | 2008 | Before | 2008-04-06 19:26 | 2008-04-06 20:05 | 3 | 119.55 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | OTHER, KNOWN CAUSE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: cutout door not latching - adjusted and closed in with no damage | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 669778 | CPCC | CPCC494469 | PP | CA | TULELAKE | TULELAKE | Line Cut-28450 | 2008 | Before | 2008-04-01 11:00 | 2008-04-01 11:05 | 0 | 0 | 143 | 641.117 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | PLANNED OUTAGE |  |  |  | PROSPER: crew had to take outage to take b/o reg bank off line. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4478 | 41.9517
5L82 | 669508 | CPCC | CPCC495144 | PP | CA | TULELAKE | TULELAKE | OH_150900_1890037435 | 2008 | Before | 2008-04-06 16:42 | 2008-04-06 18:25 | 78 | 8078.2 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Line fuse blown | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.3981 | 41.9219
5L82 | 669509 | CPCC | CPCC495145 | PP | CA | TULELAKE | TULELAKE | TR_215802_1890036198 | 2008 | Before | 2008-04-06 17:11 | 2008-04-06 18:27 | 1 | 76.183 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Associate to 495144 call center used one of the other act # for this farm. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 669511 | CPCC | CPCC495151 | PP | CA | TULELAKE | TULELAKE | TR_130900_1890037574 | 2008 | Before | 2008-04-06 18:39 | 2008-04-06 19:24 | 3 | 134.25 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: blowen transformer fuse posible a melted out fuse | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 664151 | CPCC | CPCC485874 | PP | CA | TULELAKE | TULELAKE | TUL_CB5L82 | 2008 | Before | 2008-01-31 12:49 | 2008-01-31 14:15 | 491 | 42340.567 | 0 | 0 | 1 | Y | N | N | N | Y | 746 - 2008-01-31 to 2008-01-31 CA Tulelake | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: closed | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4714 | 41.9534
5L82 | 667054 | CPCC | CPCC491213 | PP | CA | TULELAKE | TULELAKE | TR_070201_1890033995 | 2008 | Before | 2008-03-06 09:40 | 2008-03-06 10:03 | 1 | 22.933 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: serviceman patrolled line and found nothing, refused tap line and it held | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 668458 | CPCC | CPCC490603 | PP | CA | TULELAKE | TULELAKE | TR_062302_1890033615 | 2008 | Before | 2008-03-02 08:41 | 2008-03-02 11:30 | 1 | 168.8 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Service burned down mid span no cause detected. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 679036 | CPCC | CPCC504422 | PP | CA | TULELAKE | TULELAKE | TR_230501_1890029956 | 2008 | Before | 2008-05-31 11:12 | 2008-05-31 13:45 | 2 | 306.033 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | CONNECTOR OH |  |  |  | PROSPER: District Lineman replaced connection at weatherhead and refused transformer ok. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 680314 | CPCC | CPCC506056 | PP | CA | TULELAKE | TULELAKE | TR_265800_1890072789 | 2008 | Before | 2008-06-13 21:47 | 2008-06-14 00:13 | 1 | 146.4 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 681961 | CPCC | CPCC511651 | PP | CA | TULELAKE | TULELAKE | TR_352302_1890073342 | 2008 | Before | 2008-07-09 20:19 | 2008-07-09 21:30 | 1 | 70.683 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: District Lineman refused transformer ok. Cause is unknown. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 680390 | CPCC | CPCC507391 | PP | CA | TULELAKE | TULELAKE | TR_074900_1890044496 | 2008 | Before | 2008-06-22 09:45 | 2008-06-22 11:09 | 1 | 84.633 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 679608 | CPCC | CPCC504612 | PP | CA | TULELAKE | TULELAKE | TUL_CB5L82 | 2008 | Before | 2008-06-01 22:08 | 2008-06-02 10:19 | 490 | 83591.9 | 0 | 0 | 2 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | POLE OH |  |  |  | PROSPER: replaced pole | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4714 | 41.9534
5L82 | 676833 | CPCC | CPCC504655 | PP | CA | TULELAKE | TULELAKE | OH_061201_1890037446 | 2008 | Before | 2008-06-02 09:42 | 2008-06-02 10:19 | 33 | 1216.05 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Opened fuse on pole A 2526 to make up jumpers on pole A 9730 from car pole last night | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4538 | 41.9391
5L82 | 680554 | CPCC | CPCC510494 | PP | CA | TULELAKE | TULELAKE | TR_209503_1890035161 | 2008 | Before | 2008-07-04 07:20 | 2008-07-04 10:45 | 1 | 204.467 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused transformer ok. Cause is unknown. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 681032 | CPCC | CPCC508333 | PP | CA | TULELAKE | TULELAKE | TR_337700_1890074814 | 2008 | Before | 2008-06-28 19:47 | 2008-06-29 08:38 | 1 | 770.6 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: refused and closed | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 657338 | CPCC | CPCC472810 | PP | CA | TULELAKE | TULELAKE | TR_355002_1890073133 | 2008 | Before | 2008-01-04 13:05 | 2008-01-04 21:40 | 1 | 514.85 | 0 | 0 | 1 | Y | N | N | N | Y | 732 - 2008-01-04 to 2008-01-08 CA Tulelake | WEATHER | WIND |  |  | TRANSFORMER OH |  |  |  | PROSPER: per customer - they are back in power | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 702645 | CPCC | CPCC553687 | PP | CA | TULELAKE | TULELAKE | RC_369161_1890125624 | 2009 | Before | 2009-02-19 15:58 | 2009-02-19 17:07 | 144 | 9938.4 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | RECLOSER-NORMAL OPERATION OH (NO CAUSE FOUND) |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4478 | 41.9518
5L82 | 702646 | CPCC | CPCC553694 | PP | CA | TULELAKE | TULELAKE | TR_332700_1890074648 | 2009 | Before | 2009-02-19 16:52 | 2009-02-19 17:07 | 1 | 14.5 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | RECLOSER-NORMAL OPERATION OH (NO CAUSE FOUND) |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 696668 | CPCC | CPCC522901 | PP | CA | TULELAKE | TULELAKE | RC_369301_1890125623 | 2008 | Before | 2008-09-16 18:08 | 2008-09-17 00:43 | 112 | 44210.133 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Tree through primary, crew completed repairs. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4478 | 41.9555
5L82 | 697517 | CPCC | CPCC523267 | PP | CA | TULELAKE | TULELAKE | OH_070200_1890037468 | 2008 | Before | 2008-09-18 15:09 | 2008-09-18 16:17 | 6 | 405.1 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: closed in two line fuses and holding. no cause found | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.457 | 41.9251
5L82 | 696737 | CPCC | CPCC522333 | PP | CA | TULELAKE | TULELAKE | SB_285400_1890077816 | 2008 | Before | 2008-09-12 11:36 | 2008-09-12 20:38 | 2 | 1083 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | DIG-IN (NON-PACIFICORP PERSONNEL) |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: Primary Dig In | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.2889 | 41.9723
5L82 | 702516 | CPCC | CPCC548057 | PP | CA | TULELAKE | TULELAKE | OH_179201_1890154342 | 2009 | Before | 2009-01-08 10:22 | 2009-01-08 10:36 | 7 | 98.7 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | CROSS ARM OH |  |  |  | PROSPER: Serviceman found a cross-arm that the wind had adjusted so the b phase made contact with primary neutral. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4182 | 41.9104
5L82 | 696210 | CPCC | CPCC523691 | PP | CA | TULELAKE | TULELAKE | TR_260401_1890072875 | 2008 | Before | 2008-09-22 03:50 | 2008-09-22 07:10 | 3 | 599.9 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | PROSPER: Secondary is burn't up. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 692139 | CPCC | CPCC519612 | PP | CA | TULELAKE | TULELAKE | TR_013700_1890030824 | 2008 | Before | 2008-08-25 09:38 | 2008-08-25 13:14 | 1 | 216.467 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: replace b/o cutout and secondary connections | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 691787 | CPCC | CPCC517356 | PP | CA | TULELAKE | TULELAKE | TR_332700_1890074648 | 2008 | Before | 2008-08-15 10:36 | 2008-08-15 12:53 | 4 | 549.133 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Open fuse on transformer bank, no cause found | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 692257 | CPCC | CPCC516587 | PP | CA | TULELAKE | TULELAKE | TR_337700_1890074814 | 2008 | Before | 2008-08-10 09:35 | 2008-08-10 12:46 | 1 | 191.467 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | PROSPER: Serviceman replaced connections on secondary service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 695162 | CPCC | CPCC524679 | PP | CA | TULELAKE | TULELAKE | RC_369161_1890125624 | 2008 | Before | 2008-09-30 06:43 | 2008-09-30 10:01 | 144 | 28392 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Patroling, found nothing, set on non-reclose, close for test. 0900, did not hold.continue to patrol....Tested again with recloser on and tested good. Possible B/O recloser | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4478 | 41.9518
5L82 | 692740 | CPCC | CPCC520062 | PP | CA | TULELAKE | TULELAKE | TR_332700_1890074648 | 2008 | Before | 2008-08-27 15:51 | 2008-08-27 17:33 | 1 | 102.25 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: starling | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 709099 | CPCC | CPCC557326 | PP | CA | TULELAKE | TULELAKE | TR_165900_1890037331 | 2009 | Before | 2009-03-17 13:44 | 2009-03-17 14:46 | 1 | 62.017 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | PROSPER: Pole A-4513 Broken mousetrap - likely caused by tree limbs | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 706367 | CPCC | CPCC554382 | PP | CA | TULELAKE | TULELAKE | OH_060202_1890037457 | 2009 | Before | 2009-02-25 09:20 | 2009-02-25 09:56 | 15 | 540.5 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD SUSPECTED, NO MORTALITY |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Patroling | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4571 | 41.9399
5L82 | 703975 | CPCC | CPCC553988 | PP | CA | TULELAKE | TULELAKE | OH_060202_1890037457 | 2009 | Before | 2009-02-23 10:50 | 2009-02-23 11:17 | 15 | 399 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Patroling after fuse found open. Found nothing so refused and power restored | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4571 | 41.9399
5L82 | 705583 | CPCC | CPCC555360 | PP | CA | TULELAKE | TULELAKE | OH_060202_1890037457 | 2009 | Before | 2009-03-02 09:18 | 2009-03-02 10:35 | 12 | 923.2 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: serviceman found center phase open, patrolling. found nothing, closed cutout fuse. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4571 | 41.9399
5L82 | 703697 | CPCC | CPCC551710 | PP | CA | TULELAKE | TULELAKE | OH_060202_1890037457 | 2009 | Before | 2009-02-09 10:14 | 2009-02-09 10:36 | 16 | 345.6 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: customer called, serviceman patrolling | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4571 | 41.9399
5L82 | 705289 | CPCC | CPCC551848 | PP | CA | TULELAKE | TULELAKE | OH_310401_1890043891 | 2009 | Before | 2009-02-10 11:28 | 2009-02-10 12:32 | 1 | 63.617 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: found open fuse, patrolling found nothing here, refused line fuse. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4571 | 41.8706
5L82 | 703003 | CPCC | CPCC535058 | PP | CA | TULELAKE | TULELAKE | TUL_CB5L82 | 2008 | Before | 2008-12-12 20:59 | 2008-12-12 22:59 | 495 | 59457.75 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | CIRCUIT BREAKER SUB |  |  |  | PROSPER: breaker verified open at sub, EMR patrolling | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4714 | 41.9534
5L82 | 709031 | CPCC | CPCC558283 | PP | CA | TULELAKE | TULELAKE | OH_179201_1890154342 | 2009 | Before | 2009-03-26 14:52 | 2009-03-26 15:28 | 8 | 288.667 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Patroling..........Refused on A 2734 and closed and holding | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4182 | 41.9104
5L82 | 687222 | CPCC | CPCC514805 | PP | CA | TULELAKE | TULELAKE | TR_078301_1890033922 | 2008 | Before | 2008-07-30 17:19 | 2008-07-30 18:10 | 1 | 50.617 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | LIGHTNING ARRESTER OH |  |  |  | PROSPER: Trans fuse blown | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 688347 | CPCC | CPCC515410 | PP | CA | TULELAKE | TULELAKE | TR_209503_1890035161 | 2008 | Before | 2008-08-04 07:40 | 2008-08-04 09:00 | 1 | 79.9 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: patrolling..... Changed three cutouts on pole A 7072 | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 726260 | CPCC | CPCC564163 | PP | CA | TULELAKE | TULELAKE | TR_069900_1890033354 | 2009 | Before | 2009-05-05 20:47 | 2009-05-06 00:09 | 2 | 403.767 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: broken cut out | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 725122 | CPCC | CPCC579021 | PP | CA | TULELAKE | TULELAKE | Line Cut-36789 | 2009 | Before | 2009-08-01 16:00 | 2009-08-01 18:48 | 492 | 82893.8 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4713 | 41.9536
5L82 | 723516 | CPCC | CPCC579932 | PP | CA | TULELAKE | TULELAKE | OH_010000_1890030966 | 2009 | Before | 2009-08-02 08:42 | 2009-08-02 10:16 | 4 | 376.333 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.3596 | 41.9359
5L82 | 723627 | CPCC | CPCC567710 | PP | CA | TULELAKE | TULELAKE | TR_332700_1890074648 | 2009 | Before | 2009-06-01 06:44 | 2009-06-01 09:49 | 1 | 184.25 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: power is restored to all but one customer, customer to repair their facilities refused transformer | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 724435 | CPCC | CPCC567774 | PP | CA | TULELAKE | TULELAKE | TR_332700_1890074648 | 2009 | Before | 2009-06-01 09:48 | 2009-06-01 09:49 | 0 | 0 | 4 | 5.6 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: assoc. # 567710 | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 717999 | CPCC | CPCC533357 | PP | CA | TULELAKE | TULELAKE | TR_259500_1890062527 | 2008 | Before | 2008-11-30 12:59 | 2008-11-30 14:44 | 1 | 105.083 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 720076 | CPCC | CPCC562079 | PP | CA | TULELAKE | TULELAKE | TR_128700_1890031592 | 2009 | Before | 2009-04-23 14:16 | 2009-04-23 15:53 | 1 | 97.133 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: repaired bad jumpers, refused transformer bank | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 719313 | CPCC | CPCC565141 | PP | CA | TULELAKE | TULELAKE | TR_262201_1890072939 | 2009 | Before | 2009-05-14 14:42 | 2009-05-14 17:23 | 1 | 161.767 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | TRANSFORMER OH |  |  |  | PROSPER: Truck took out service, broke bushings on transformer, crew in route to repair. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 719836 | CPCC | CPCC565198 | PP | CA | TULELAKE | TULELAKE | TR_122500_1890031544 | 2009 | Before | 2009-05-15 09:35 | 2009-05-15 12:00 | 1 | 144.9 | 0 | 0 | 1 | Y | N | N | N | N |  | OPERATIONAL | PACIFICORP EMPLOYEE - FIELD |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: This service was cut in error at the pole. There was a mix-up on a diconnect order. Serviceman repaired. Customer back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 720226 | CPCC | CPCC567521 | PP | CA | TULELAKE | TULELAKE | TR_272500_1890073758 | 2009 | Before | 2009-05-31 20:06 | 2009-06-01 01:26 | 1 | 320 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: refused | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 715812 | CPCC | CPCC534461 | PP | CA | TULELAKE | TULELAKE | RC_369161_1890125624 | 2008 | Before | 2008-12-09 12:44 | 2008-12-09 13:50 | 144 | 9513.6 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: found recloser open, patrolling Found nothing after patrol, so closed on test and held | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4478 | 41.9518
5L82 | 717862 | CPCC | CPCC541958 | PP | CA | TULELAKE | TULELAKE | RC_369301_1890125623 | 2008 | Before | 2008-12-24 20:26 | 2008-12-25 03:02 | 114 | 45187.7 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: wire down crew to make repairs | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4478 | 41.9555
5L82 | 715823 | CPCC | CPCC534492 | PP | CA | TULELAKE | TULELAKE | TR_030960_1890032101 | 2008 | Before | 2008-12-09 17:02 | 2008-12-09 18:38 | 1 | 95.867 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 732395 | CPCC | CPCC573984 | PP | CA | TULELAKE | TULELAKE | Line Cut-36050 | 2009 | Before | 2009-07-03 23:16 | 2009-07-04 00:20 | 492 | 31611 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | TRANSFORMER OH |  |  |  | PROSPER: pole fire 6/004 with under build of 12kV | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4713 | 41.9536
5L82 | 732652 | CPCC | CPCC574027 | PP | CA | TULELAKE | TULELAKE | TR_100561_1890032958 | 2009 | Before | 2009-07-04 00:40 | 2009-07-04 00:44 | 0 | 0 | 1 | 3.283 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | OTHER SUB (EXPLAIN IN COMMENTS) |  |  |  | PROSPER: CB 3L179 tripped open while energizing upto Henly | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 730294 | CPCC | CPCC572153 | PP | CA | TULELAKE | TULELAKE | TR_162201_1890036006 | 2009 | Before | 2009-06-22 09:44 | 2009-06-22 12:13 | 1 | 149.283 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: patrolling serviceman says fuse open, refused, power on | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 732711 | CPCC | CPCC566304 | PP | CA | TULELAKE | TULELAKE | TR_062202_1890033597 | 2009 | Before | 2009-05-25 09:05 | 2009-05-25 10:52 | 1 | 106.75 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | PROSPER: patrolling repaired/replaced bad connections on the service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 732716 | CPCC | CPCC566699 | PP | CA | TULELAKE | TULELAKE | TR_132903_1890037541 | 2009 | Before | 2009-05-28 18:25 | 2009-05-28 20:08 | 1 | 103.683 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 709548 | CPCC | CPCC555647 | PP | CA | TULELAKE | TULELAKE | TR_300901_1890075535 | 2009 | Before | 2009-03-03 11:20 | 2009-03-03 13:14 | 1 | 113.7 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | SNOW, SLEET AND BLIZZARD |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: spoke to customer. power is restored | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 710079 | CPCC | CPCC555713 | PP | CA | TULELAKE | TULELAKE | TUL_CB5L82 | 2009 | Before | 2009-03-03 02:45 | 2009-03-03 04:42 | 494 | 57798 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE | WEATHER | SNOW, SLEET AND BLIZZARD | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4714 | 41.9534
5L82 | 753513 | CPCC | CPCC621788 | PP | CA | TULELAKE | TULELAKE | Line Cut-41722 | 2010 | Before | 2010-03-12 18:08 | 2010-03-12 19:05 | 493 | 28109.217 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Patrilled no cause found, snowing | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4713 | 41.9534
5L82 | 752409 | CPCC | CPCC601824 | PP | CA | TULELAKE | TULELAKE | Line Cut-39644 | 2009 | Before | 2009-11-28 13:18 | 2009-11-28 13:23 | 491 | 2635.033 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4713 | 41.9535
5L82 | 753202 | CPCC | CPCC601365 | PP | CA | TULELAKE | TULELAKE | TR_350401_1890030623 | 2009 | Before | 2009-11-24 14:36 | 2009-11-24 14:45 | 1 | 9.067 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Bad connectivity | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 753650 | CPCC | CPCC626840 | PP | CA | TULELAKE | TULELAKE | TR_257900_1890062548 | 2010 | Before | 2010-04-07 15:14 | 2010-04-07 15:31 | 2 | 34.1 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: serviceman called and created own outage ticket, dispatch left message, to verify, located and refused deteriorated fuses, outage restored | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 753371 | CPCC | CPCC624284 | PP | CA | TULELAKE | TULELAKE | RC_369301_1890125623 | 2010 | Before | 2010-03-29 08:06 | 2010-03-29 11:48 | 114 | 25232 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Line down on pole A 1025, repairs made, outage restored | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4478 | 41.9555
5L82 | 745993 | CPCC | CPCC585190 | PP | CA | TULELAKE | TULELAKE | TR_013900_1890027164 | 2009 | Before | 2009-08-31 15:12 | 2009-08-31 16:00 | 2 | 96.967 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: found broken cutout, crew on site to replace. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 742705 | CPCC | CPCC593904 | PP | CA | TULELAKE | TULELAKE | Line Cut-38624 | 2009 | Before | 2009-10-15 10:40 | 2009-10-15 11:04 | 490 | 11539.5 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4713 | 41.9535
5L82 | 743590 | CPCC | CPCC583874 | PP | CA | TULELAKE | TULELAKE | TR_014400_1890010667 | 2009 | Before | 2009-08-26 11:15 | 2009-08-26 11:33 | 1 | 17.9 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: bad order connectors at service pole A 6574. Replaced and power back on | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 745590 | CPCC | CPCC595556 | PP | CA | TULELAKE | TULELAKE | TR_085501_1890034322 | 2009 | Before | 2009-10-28 14:57 | 2009-10-28 16:06 | 1 | 69.017 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Wind blew jumpers together on high side on xfmr and blew fuse. Serviceman refused xfmr and customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 759427 | CPCC | CPCC608140 | PP | CA | TULELAKE | TULELAKE | Line Cut-40229 | 2009 | Before | 2009-12-24 11:54 | 2009-12-24 12:32 | 491 | 18658 | 0 | 0 | 1 | Y | N | N | N | Y | 867 - 2009-12-24 to 2009-12-24 CA Tulelake | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Line isolated that may have damage, but at this time (unknown) | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4713 | 41.9537
5L82 | 760247 | CPCC | CPCC625989 | PP | CA | TULELAKE | TULELAKE | Line Cut-42156 | 2010 | Before | 2010-04-02 14:01 | 2010-04-02 15:08 | 493 | 32973.483 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: CB locked out. Serviceman patrolled and found no distribution damage. Wind suspected cause. Cb breaker closed and held @ 15:08. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4713 | 41.9536
5L82 | 757826 | CPCC | CPCC618152 | PP | CA | TULELAKE | TULELAKE | Line Cut-41268 | 2010 | Before | 2010-02-14 07:37 | 2010-02-14 08:41 | 493 | 31149.383 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Breaker tripped open in the substation. Patrolling no cause found | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4714 | 41.9533
5L82 | 755939 | CPCC | CPCC616756 | PP | CA | TULELAKE | TULELAKE | Line Cut-41077 | 2010 | Before | 2010-01-30 11:09 | 2010-01-30 11:41 | 493 | 15989.633 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4713 | 41.9537
5L82 | 755558 | CPCC | CPCC629188 | PP | CA | TULELAKE | TULELAKE | OH_335761_1890076776 | 2010 | Before | 2010-04-21 22:39 | 2010-04-22 03:17 | 11 | 3056.533 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: b/o cut out | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4061 | 41.9612
5L82 | 758726 | CPCC | CPCC614854 | PP | CA | TULELAKE | TULELAKE | TR_257200_1890062781 | 2010 | Before | 2010-01-20 19:45 | 2010-01-20 22:16 | 1 | 151.233 | 0 | 0 | 1 | Y | N | N | N | Y | 880 - 01-19-2010 to 01-25-2010 CA Tulelake | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Associated with outage 614882. Bad connectivity in cadops. Called customer and there power came back on. Blown fuse, refused and customer is back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 755268 | CPCC | CPCC617684 | PP | CA | TULELAKE | TULELAKE | TUL_CB5L82 | 2010 | Before | 2010-02-08 07:12 | 2010-02-08 07:13 | 0 | 0 | 493 | 493 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: loss of transmission CB 3L179 for 1 minute. Corrected ON time in database to 0713. P44577. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4714 | 41.9534
5L82 | 754514 | CPCC | CPCC628866 | PP | CA | TULELAKE | TULELAKE | RC_369161_1890125624 | 2010 | Before | 2010-04-21 04:43 | 2010-04-21 08:47 | 142 | 34683.5 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | SNOW, SLEET AND BLIZZARD | WEATHER | WIND | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Snow and wind storm in area locked out field recloser. Serviceman patrolled line, closed recloser in on test and it held. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4478 | 41.9518
5L82 | 756065 | CPCC | CPCC628775 | PP | CA | TULELAKE | TULELAKE | TR_262202_1890072932 | 2010 | Before | 2010-04-20 16:37 | 2010-04-20 18:51 | 1 | 133.467 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: opq#5425378 | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 755732 | CPCC | CPCC624979 | PP | CA | TULELAKE | TULELAKE | Line Cut-42030 | 2010 | Before | 2010-03-29 13:16 | 2010-03-29 16:15 | 493 | 87803.3 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | OTHER, KNOWN CAUSE |  |  | CIRCUIT BREAKER SUB |  |  |  | PROSPER: patroled, no cause found, outage restored | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4713 | 41.9535
5L82 | 738874 | CPCC | CPCC583013 | PP | CA | TULELAKE | TULELAKE | TR_022002_1890031123 | 2009 | Before | 2009-08-19 13:09 | 2009-08-19 14:18 | 1 | 68.55 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: Per serviceman: B/O cut-out door on x-fmr bank on pole# 022002. Serviceman replaced door. Customer back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 740271 | CPCC | CPCC587609 | PP | CA | TULELAKE | TULELAKE | OH_179201_1890154342 | 2009 | Before | 2009-09-18 06:18 | 2009-09-18 07:56 | 8 | 783.067 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Blown line fuse. Serviceman investigating. will test. No cause found. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4182 | 41.9104
5L82 | 773828 | CPCC | CPCC646269 | PP | CA | TULELAKE | TULELAKE | Line Cut-44161 | 2010 | Before | 2010-07-25 18:58 | 2010-07-25 20:51 | 498 | 56174.4 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE | WEATHER | LIGHTNING | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Verify issue, changed OFF time from 1744 to 1858. P44577. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4714 | 41.9533
5L82 | 775124 | CPCC | CPCC647810 | PP | CA | TULELAKE | TULELAKE | OH_179201_1890154342 | 2010 | Before | 2010-08-01 04:30 | 2010-08-01 10:12 | 8 | 2732 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | INTERFERENCE | VEHICLE ACCIDENT | POLE OH |  |  |  | PROSPER: Car hit pole at County Rd 111A and Hwy 138 Tulelake. Open fuses to change out pole. Crew: Starley, Hilyard, Wilson, Norris. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4182 | 41.9104
5L82 | 776920 | CPCC | CPCC641170 | PP | CA | TULELAKE | TULELAKE | SUB_SW_1890121720 | 2010 | Before | 2010-06-29 19:31 | 2010-06-29 22:31 | 497 | 89526.267 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | TRANSMISSION REQUESTED |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: trouble with T4 in Malin | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4714 | 41.9534
5L82 | 769430 | CPCC | CPCC620112 | PP | CA | TULELAKE | TULELAKE | Line Cut-41570 | 2010 | Before | 2010-03-02 16:00 | 2010-03-02 16:22 | 493 | 10402.3 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE | INTERFERENCE | VEHICLE ACCIDENT | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Car hit pole and tripped a transmission breaker. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4713 | 41.9536
5L82 | 769932 | CPCC | CPCC617871 | PP | CA | TULELAKE | TULELAKE | Line Cut-41225 | 2010 | Before | 2010-02-11 07:12 | 2010-02-11 07:15 | 0 | 0 | 493 | 1059.95 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Back on by SCADA switching | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4713 | 41.9535
5L82 | 768413 | CPCC | CPCC620805 | PP | CA | TULELAKE | TULELAKE | TR_350500_1890030187 | 2010 | Before | 2010-03-08 10:02 | 2010-03-08 11:43 | 1 | 100.9 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: serviceman reported that he located open fuse @ A 2783(190401), patroled, no cause found, refused, power restored | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 770462 | CPCC | CPCC640260 | PP | CA | TULELAKE | TULELAKE | OH_179201_1890154342 | 2010 | Before | 2010-06-25 09:16 | 2010-06-25 10:15 | 8 | 471.6 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman locate open fuse @ FP# 179201(center phase) patroling for cause. Refused and power on | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4182 | 41.9104
5L82 | 767747 | CPCC | CPCC616028 | PP | CA | TULELAKE | TULELAKE | Line Cut-40978 | 2010 | Before | 2010-01-25 12:18 | 2010-01-25 12:21 | 0 | 0 | 493 | 1651.55 | 1 | Y | N | N | N | Y | 880 - 01-19-2010 to 01-25-2010 CA Tulelake | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE | WEATHER | SNOW, SLEET AND BLIZZARD | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4713 | 41.9536
5L82 | 784257 | CPCC | CPCC630737 | PP | CA | TULELAKE | TULELAKE | OH_060202_1890037457 | 2010 | Before | 2010-04-27 10:48 | 2010-04-27 15:15 | 16 | 4266.4 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | CONSTRUCTION |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Bird work in area...This is just pumps on this line | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4571 | 41.9399
5L82 | 785079 | CPCC | CPCC640796 | PP | CA | TULELAKE | TULELAKE | TR_346002_1890075034 | 2010 | Before | 2010-06-28 14:01 | 2010-06-28 14:55 | 1 | 53.783 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: left message: 1404. serviceman located open transformer bank fuses open due to starlings, refused, outage restored | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 781960 | CPCC | CPCC638093 | PP | CA | TULELAKE | TULELAKE | TR_322902_1890076101 | 2010 | Before | 2010-06-07 20:15 | 2010-06-07 22:21 | 1 | 125.55 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: house knob pulled from house service re-hung | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 784717 | CPCC | CPCC643027 | PP | CA | TULELAKE | TULELAKE | Line Cut-43897 | 2010 | Before | 2010-07-09 16:23 | 2010-07-09 18:27 | 497 | 61470.617 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4713 | 41.9535
5L82 | 781597 | CPCC | CPCC637521 | PP | CA | TULELAKE | TULELAKE | OH_182900_1890046370 | 2010 | Before | 2010-06-02 14:03 | 2010-06-02 14:18 | 27 | 395.1 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: crew located 3 phase jumper burned in the clear @ FP# 072001(7576), crew to open fusing @ FP# 182900(8613) to facilitate repairs. repairs made, outage restored | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.3349 | 41.9217
5L82 | 782002 | CPCC | CPCC646541 | PP | CA | TULELAKE | TULELAKE | Line Cut-44200 | 2010 | Before | 2010-07-26 09:37 | 2010-07-26 11:09 | 498 | 45816 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4713 | 41.9536
5L82 | 782781 | CPCC | CPCC646153 | PP | CA | TULELAKE | TULELAKE | Line Cut-44147 | 2010 | Before | 2010-07-25 12:47 | 2010-07-25 17:07 | 497 | 129162.017 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Loss of substaion transformer | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4713 | 41.9535
5L82 | 782805 | CPCC | CPCC646801 | PP | CA | TULELAKE | TULELAKE | Line Cut-44223 | 2010 | Before | 2010-07-26 16:38 | 2010-07-26 18:59 | 498 | 70251.2 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4713 | 41.9535
5L82 | 782046 | CPCC | CPCC637633 | PP | CA | TULELAKE | TULELAKE | TR_186700_1890034976 | 2010 | Before | 2010-06-03 10:08 | 2010-06-03 11:14 | 1 | 66.233 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Blown xfmr fuse. No cause found. Serviceman refused and it held. Customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 766211 | CPCC | CPCC617927 | PP | CA | TULELAKE | TULELAKE | OH_190401_1890037442 | 2010 | Before | 2010-02-11 13:52 | 2010-02-11 14:54 | 3 | 186.65 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: lines slapped together | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4571 | 41.8989
5L82 | 763032 | CPCC | CPCC622315 | PP | CA | TULELAKE | TULELAKE | OH_294301_1890077837 | 2010 | Before | 2010-03-17 13:14 | 2010-03-17 14:41 | 6 | 522.1 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | CONSTRUCTION |  |  | POLE OH |  |  |  | PROSPER: Contacted customers that we were going to cut power to set a pole | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.311 | 41.9698
5L82 | 763914 | CPCC | CPCC629359 | PP | CA | TULELAKE | TULELAKE | TR_257400_1890062765 | 2010 | Before | 2010-04-22 15:38 | 2010-04-22 18:23 | 1 | 164.417 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | SNOW, SLEET AND BLIZZARD | WEATHER | WIND | CUT-OUT B/O OH |  |  |  | PROSPER: Bad order cutout and arrestor caused by storm yesterday...crew needed | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 760446 | CPCC | CPCC625455 | PP | CA | TULELAKE | TULELAKE | OH_060202_1890037457 | 2010 | Before | 2010-03-30 09:37 | 2010-03-30 11:44 | 15 | 1913.75 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: serviceman patroling for trouble, patroled, no cause found, refused, outage restored | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4571 | 41.9399
5L82 | 762794 | CPCC | CPCC626454 | PP | CA | TULELAKE | TULELAKE | OH_060202_1890037457 | 2010 | Before | 2010-04-05 09:42 | 2010-04-05 12:30 | 12 | 2007.8 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman on another job. located open fuses @ FP# 060202(A 1397), patroling for cause. located bird on primary and removed. outage restored | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4571 | 41.9399
5L82 | 766436 | CPCC | CPCC616588 | PP | CA | TULELAKE | TULELAKE | Line Cut-41051 | 2010 | Before | 2010-01-28 10:43 | 2010-01-28 10:45 | 0 | 0 | 493 | 747.717 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4713 | 41.9535
5L82 | 763248 | CPCC | CPCC617848 | PP | CA | TULELAKE | TULELAKE | TR_012901_1890030844 | 2010 | Before | 2010-02-10 16:12 | 2010-02-10 17:06 | 1 | 53.833 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: deteriorated fuse | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 765247 | CPCC | CPCC628172 | PP | CA | TULELAKE | TULELAKE | Line Cut-42378 | 2010 | Before | 2010-04-14 15:11 | 2010-04-14 15:13 | 0 | 0 | 3 | 5.9 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Refused and power on...unk | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4009 | 41.9727
5L82 | 765248 | CPCC | CPCC628176 | PP | CA | TULELAKE | TULELAKE | RC_369301_1890125623 | 2010 | Before | 2010-04-14 15:26 | 2010-04-14 16:32 | 115 | 7605.333 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN | WEATHER | WIND | RECLOSER-NORMAL OPERATION OH (NO CAUSE FOUND) |  |  |  | PROSPER: serviceman reporting FR 456 @ FP# A 1027(369301) has operated & lockedopen, patroling, no cause found, closing reclosure on test(one shot)(16:27), suspect wind caused phases to slap. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4478 | 41.9555
5L82 | 800094 | CPCC | CPCC665050 | PP | CA | TULELAKE | TULELAKE | RC_339001_1890125626 | 2010 | Before | 2010-11-17 10:24 | 2010-11-17 12:10 | 70 | 7443.333 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD SUSPECTED, NO MORTALITY |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Patroling | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.3976 | 41.9507
5L82 | 799377 | CPCC | CPCC656218 | PP | CA | TULELAKE | TULELAKE | TR_032200_1890031828 | 2010 | Before | 2010-09-25 17:59 | 2010-09-25 20:27 | 1 | 148.1 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | PROSPER: B/O sec connectors | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 802193 | CPCC | CPCC664677 | PP | CA | TULELAKE | TULELAKE | RC_369161_1890125624 | 2010 | Before | 2010-11-15 12:45 | 2010-11-15 14:15 | 144 | 12914.4 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Locked out field recloser. Serviceman patrolling. took recloser off line and bypassed and power restored. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4478 | 41.9518
5L82 | 801412 | CPCC | CPCC664573 | PP | CA | TULELAKE | TULELAKE | RC_369161_1890125624 | 2010 | Before | 2010-11-14 08:51 | 2010-11-14 09:52 | 144 | 8882.4 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | RECLOSER-NORMAL OPERATION OH (NO CAUSE FOUND) |  |  |  | PROSPER: Field recloser locked out crew patroling. No cause found closed and held. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4478 | 41.9518
5L82 | 803437 | CPCC | CPCC660430 | PP | CA | TULELAKE | TULELAKE | OH_368400_1890076785 | 2010 | Before | 2010-10-23 19:59 | 2010-10-24 00:24 | 17 | 4504.15 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: Broken jumper | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.3416 | 41.9572
5L82 | 804585 | CPCC | CPCC696665 | PP | CA | TULELAKE | TULELAKE | RC_339001_1890125626 | 2011 | Before | 2011-03-17 13:46 | 2011-03-17 14:17 | 71 | 2219.933 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: serviceman located FR 9015 locked open(targets on A & C), patroled, no cause found, closed on test/returned reclosing on, outage restored. suspects winds due to high winds. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.3976 | 41.9507
5L82 | 800337 | CPCC | CPCC664401 | PP | CA | TULELAKE | TULELAKE | RC_369161_1890125624 | 2010 | Before | 2010-11-12 07:59 | 2010-11-12 10:05 | 144 | 18124.8 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: serviceman verified that FR 357 is locked out/open position, patroling for cause(09:30), no cause found, closing FR 357 on test/reporting(no comment calls from customers(9:59), outage restored 10:04) | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4478 | 41.9518
5L82 | 795231 | CPCC | CPCC653910 | PP | CA | TULELAKE | TULELAKE | RC_369301_1890125623 | 2010 | Before | 2010-09-12 12:58 | 2010-09-12 16:56 | 114 | 27088.3 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | INSULATOR OH |  |  |  | PROSPER: Broken insulators, crew responding | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4478 | 41.9555
5L82 | 793447 | CPCC | CPCC652942 | PP | CA | TULELAKE | TULELAKE | TR_347302_1890077831 | 2010 | Before | 2010-09-04 12:57 | 2010-09-04 15:29 | 1 | 152.067 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VANDALISM OR THEFT |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: service drop shot up, spliced | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 810606 | CPCC | CPCC695449 | PP | CA | TULELAKE | TULELAKE | TR_122500_1890031544 | 2011 | Before | 2011-03-14 15:49 | 2011-03-14 17:08 | 1 | 78.317 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman arrived and found blown fuse, figures cause was high side jumpers touching but not sure. Closed fuse in and it held outage restored. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 807844 | CPCC | CPCC674500 | PP | CA | TULELAKE | TULELAKE | OH_190401_1890037442 | 2011 | Before | 2011-01-04 10:45 | 2011-01-04 12:03 | 3 | 235.25 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: serviceman located open line fuse @ FP# 190401/A 2783, patroling for cause(11:26), none found, refused, outage restored | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4571 | 41.8989
5L82 | 807917 | CPCC | CPCC671674 | PP | CA | TULELAKE | TULELAKE | OH_163002_1890036042 | 2010 | Before | 2010-12-19 20:09 | 2010-12-19 21:54 | 4 | 421.533 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: No cause found | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4116 | 41.9079
5L82 | 809721 | CPCC | CPCC676971 | PP | CA | TULELAKE | TULELAKE | TR_314201_1890075832 | 2011 | Before | 2011-01-21 11:23 | 2011-01-21 11:31 | 2 | 16.867 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 314201 and it held, the cause was wind, pump is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 787264 | CPCC | CPCC633326 | PP | CA | TULELAKE | TULELAKE | TR_331000_1890074559 | 2010 | Before | 2010-05-13 14:55 | 2010-05-13 15:27 | 1 | 31.817 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: left message(15:00), serviceman located open fuse, no cause found, refused, outage restored. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 786163 | CPCC | CPCC642157 | PP | CA | TULELAKE | TULELAKE | OH_294301_1890077837 | 2010 | Before | 2010-07-06 14:00 | 2010-07-06 14:33 | 3 | 100.15 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: on arrival serviceman located center & south(B/C) phase open @ FP# A 6585, patroling for cause, none found, refused, outage restored. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.311 | 41.9698
5L82 | 790126 | CPCC | CPCC651623 | PP | CA | TULELAKE | TULELAKE | TR_342003_1890074922 | 2010 | Before | 2010-08-25 16:19 | 2010-08-25 17:11 | 1 | 52.133 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Starling blew xfmr fuse. Serviceman refused xfmr and customer is back in service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 787027 | CPCC | CPCC641837 | PP | CA | TULELAKE | TULELAKE | TR_027000_1890031089 | 2010 | Before | 2010-07-03 20:21 | 2010-07-03 21:36 | 1 | 75.233 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Trans fuse | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 789824 | CPCC | CPCC655680 | PP | CA | TULELAKE | TULELAKE | TR_127601_1890031584 | 2010 | Before | 2010-09-22 13:53 | 2010-09-22 14:45 | 1 | 52.2 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Blown xfmr fuse. No cause found. Serviceman refused xfmr and customer is back in service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 785908 | CPCC | CPCC642133 | PP | CA | TULELAKE | TULELAKE | TR_047701_1890032126 | 2010 | Before | 2010-07-06 10:18 | 2010-07-06 11:45 | 1 | 87.333 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: responding to outage# 642112, customer describing B/O OH secondary connector, drops sparks when operate pump, repairs made, outage restored | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 785914 | CPCC | CPCC642147 | PP | CA | TULELAKE | TULELAKE | TR_285380_1890077807 | 2010 | Before | 2010-07-06 12:34 | 2010-07-06 14:34 | 1 | 119.3 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: associate to outage# 642157. on arrival serviceman located center & south(B/C) phase open @ FP# A 6585, patroling for cause, none found, refused, outage restored. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 827415 | CPCC | CPCC706122 | PP | CA | TULELAKE | TULELAKE | TR_367702_1890067339 | 2011 | Before | 2011-05-20 13:07 | 2011-05-20 15:25 | 1 | 137.733 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: Serviceman replaced the B/O secondary connections at the weatherhead, customer is back in full sevice. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 827089 | CPCC | CPCC708042 | PP | CA | TULELAKE | TULELAKE | TR_368701_1890073568 | 2011 | Before | 2011-06-09 07:45 | 2011-06-09 08:55 | 1 | 69.983 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Refused at A 7727 and power restored | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 824317 | CPCC | CPCC713838 | PP | CA | TULELAKE | TULELAKE | RC_359200_1890154304 | 2011 | Before | 2011-07-26 07:28 | 2011-07-26 08:07 | 199 | 7751.05 | 0 | 0 | 1 | Y | N | Y | N | N |  | OTHER | UNKNOWN |  |  | RECLOSER-NORMAL OPERATION OH (NO CAUSE FOUND) |  |  |  | PROSPER: serviceman verified FR 0716 operated open, patroling for cause/damage(07:38)(A HOLD had been applied for crew work but not issued) Line patrolled, no cause found. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4689 | 41.9531
5L82 | 824074 | CPCC | CPCC707973 | PP | CA | TULELAKE | TULELAKE | TR_042200_1890032306 | 2011 | Before | 2011-06-08 11:29 | 2011-06-08 12:52 | 2 | 164.5 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: Bad order connector @ weatherhead | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 824496 | CPCC | CPCC706613 | PP | CA | TULELAKE | TULELAKE | OH_030000_1890031854 | 2011 | Before | 2011-05-26 03:14 | 2011-05-26 04:42 | 27 | 2367 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Blown fuse svcmn patrolling line. No cause found. Svcmn refuesed and circuit is holding | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.397 | 41.936
5L82 | 825309 | CPCC | CPCC706816 | PP | CA | TULELAKE | TULELAKE | TR_217300_1890076622 | 2011 | Before | 2011-05-28 12:52 | 2011-05-28 13:56 | 1 | 63.883 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Transformer fuse blew due to damaged service wire | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 827749 | CPCC | CPCC706995 | PP | CA | TULELAKE | TULELAKE | TR_162700_1890035935 | 2011 | Before | 2011-05-31 08:01 | 2011-05-31 09:28 | 3 | 261.3 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: Jumper pulled out of bottom of cut-out at xfmr bank. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 824204 | CPCC | CPCC705068 | PP | CA | TULELAKE | TULELAKE | TR_013700_1890030824 | 2011 | Before | 2011-05-12 10:08 | 2011-05-12 11:28 | 1 | 80.617 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: serviceman located open fuse @ FP# A 8371, investigated for cause/damage, none found, refused, outage restored, suspects wind slap during winter storm season | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 820242 | CPCC | CPCC685926 | PP | CA | TULELAKE | TULELAKE | TR_088900_1890034302 | 2011 | Before | 2011-03-01 03:06 | 2011-03-01 05:23 | 1 | 136.717 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: secondary wire arced and blew the fuse. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 820267 | CPCC | CPCC687396 | PP | CA | TULELAKE | TULELAKE | OH_070200_1890037468 | 2011 | Before | 2011-03-09 11:30 | 2011-03-09 11:40 | 6 | 60 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Associate to 687373...another fuse open on same pole but not blown and needed to be refused. Full power restored | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.457 | 41.9251
5L82 | 819579 | CPCC | CPCC696460 | PP | CA | TULELAKE | TULELAKE | Line Cut-48907 | 2011 | Before | 2011-03-16 16:58 | 2011-03-16 20:35 | 4 | 867.867 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: responseman reporting deteriorated jumper has failed, requesting 3 man crew/2 flaggers, dispatched/enroute(18:41) | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4182 | 41.9118
5L82 | 820784 | CPCC | CPCC686079 | PP | CA | TULELAKE | TULELAKE | OH_294301_1890077837 | 2011 | Before | 2011-03-01 14:14 | 2011-03-01 18:23 | 8 | 1997.333 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | INTERFERENCE | VEHICLE ACCIDENT | POLE OH |  |  |  | PROSPER: Crew opened a set of fuses to replace a pole that was hit by a vehicle. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.311 | 41.9698
5L82 | 820007 | CPCC | CPCC687373 | PP | CA | TULELAKE | TULELAKE | OH_070200_1890037468 | 2011 | Before | 2011-03-09 08:53 | 2011-03-09 10:14 | 6 | 487 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: serviceman located open tap line fuse @ FP# A 7051, patroling for cause/dmage(09:37) | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.457 | 41.9251
5L82 | 820073 | CPCC | CPCC678195 | PP | CA | TULELAKE | TULELAKE | RC_339001_1890125626 | 2011 | Before | 2011-02-03 07:34 | 2011-02-03 10:38 | 71 | 13040.333 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | RECLOSER-NORMAL OPERATION OH (NO CAUSE FOUND) |  |  |  | PROSPER: Field recloser locked out. Serviceman patrolling. No cause found. Serviceman closed recloser in on test and it held. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.3976 | 41.9507
5L82 | 822975 | CPCC | CPCC715683 | PP | CA | TULELAKE | TULELAKE | TR_078301_1890033922 | 2011 | Before | 2011-08-01 07:49 | 2011-08-01 12:01 | 1 | 251.533 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | PROSPER: B/O xfmr. Crew to replace. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 832124 | CPCC | CPCC712016 | PP | CA | TULELAKE | TULELAKE | TR_183900_1890035002 | 2011 | Before | 2011-07-10 09:20 | 2011-07-10 11:27 | 1 | 127 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: fuse blown, cause unknown | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 832912 | CPCC | CPCC712345 | PP | CA | TULELAKE | TULELAKE | TR_325901_1890076079 | 2011 | Before | 2011-07-13 08:57 | 2011-07-13 10:35 | 1 | 98.467 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Refused and power back on | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 830156 | CPCC | CPCC711213 | PP | CA | TULELAKE | TULELAKE | TR_062500_1890033440 | 2011 | Before | 2011-07-03 06:07 | 2011-07-03 10:28 | 1 | 261.1 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: replaced broken cut-out | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 830371 | CPCC | CPCC705887 | PP | CA | TULELAKE | TULELAKE | OH_262001_1890073044 | 2011 | Before | 2011-05-17 16:32 | 2011-05-17 18:37 | 4 | 500 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Crew opened tap line fused cutouts to make repairs to wire down. Closed tap line fuses ok. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.3718 | 41.9651
5L82 | 833985 | CPCC | CPCC710003 | PP | CA | TULELAKE | TULELAKE | TR_322900_1890076118 | 2011 | Before | 2011-06-22 09:34 | 2011-06-22 10:27 | 1 | 52.65 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Blown xfmr fuse. No cause found. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 831251 | CPCC | CPCC711811 | PP | CA | TULELAKE | TULELAKE | TR_332700_1890074648 | 2011 | Before | 2011-07-07 19:57 | 2011-07-07 22:34 | 1 | 157.417 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 816553 | CPCC | CPCC677904 | PP | CA | TULELAKE | TULELAKE | OH_190401_1890037442 | 2011 | Before | 2011-01-31 09:44 | 2011-01-31 10:48 | 3 | 192 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Blown line fuse. Serviceman patrolling. no cause found, refused, closed on test, holding, outage restored | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.4571 | 41.8989
5L82 | 844483 | CPCC | CPCC718385 | PP | CA | TULELAKE | TULELAKE | OH_182900_1890046370 | 2011 | Before | 2011-08-23 23:58 | 2011-08-24 01:11 | 27 | 1971.45 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: blown fuse svcmn patrolling line | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.3349 | 41.9217
5L82 | 847456 | CPCC | CPCC724371 | PP | CA | TULELAKE | TULELAKE | Line Cut-52547 | 2011 | Before | 2011-10-05 02:32 | 2011-10-05 03:37 | 492 | 32021 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Loss of transmission line, patrolling | DISTRIBUTION | DEVICE | AUTO | 2011-10-05 06:00 | COMPLETED |  | 2011-10-05 02:38 | 2011-10-05 03:43 | 2011-10-05 04:04 | -121.4714 | 41.9533
5L82 | 843913 | CPCC | CPCC721242 | PP | CA | TULELAKE | TULELAKE | TR_117800_1890031398 | 2011 | Before | 2011-09-09 10:59 | 2011-09-09 14:21 | 1 | 201.617 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: Serviceman found deteriorated primary jumper on xfmr. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 838410 | CPCC | CPCC720093 | PP | CA | TULELAKE | TULELAKE | TR_126800_1890031562 | 2011 | Before | 2011-09-01 21:20 | 2011-09-01 23:48 | 1 | 147.533 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Replaced fuse, no cause | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 841043 | CPCC | CPCC720376 | PP | CA | TULELAKE | TULELAKE | TR_303400_1890075639 | 2011 | Before | 2011-09-04 13:38 | 2011-09-04 14:48 | 2 | 139.167 | 0 | 0 | 1 | Y | N | N | N | N |  | ENVIRONMENT | FIRE/SMOKE (NOT DUE TO FAULTS) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Burn't up meter base disconnected bad service and re-energized transformer. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5L82 | 838772 | CPCC | CPCC717658 | PP | CA | TULELAKE | TULELAKE | RC_339001_1890125626 | 2011 | Before | 2011-08-18 12:41 | 2011-08-18 13:25 | 71 | 3075.483 | 0 | 0 | 1 | Y | N | Y | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: No cause found. Seriveman patrolled line, closed in on test and it held. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -121.3976 | 41.9507
5L82 | 871867 | CPCC | CPCC738551 | PP | CA | TULELAKE | TULELAKE | OH_073901_1890034153 | 2012 | Before | 2012-01-02 15:35 | 2012-01-02 19:38 | 30 | 7297.5 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: poplar limb tore down primary | DISTRIBUTION | DEVICE | MANUAL | 2012-01-02 20:15 | COMPLETED |  | 2012-01-02 15:36 | 2012-01-02 19:38 | 2012-01-02 20:11 | -121.4494 | 41.9363
5L82 | 871931 | CPCC | CPCC738622 | PP | CA | TULELAKE | TULELAKE | TR_183900_1890035002 | 2012 | Before | 2012-01-03 09:08 | 2012-01-03 09:59 | 1 | 51.683 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Wind pulled secondary lead off of bushing on xfmr. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-01-03 12:15 | COMPLETED |  | 2012-01-03 09:08 | 2012-01-03 09:59 | 2012-01-03 10:06 | -121.4512 | 41.9217
5L82 | 872804 | CPCC | CPCC739035 | PP | CA | TULELAKE | TULELAKE | Line Cut-56130 | 2012 | Before | 2012-01-07 07:57 | 2012-01-07 11:13 | 70 | 13713 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: jumper broken svcmn to repair. Crew made repairs | DISTRIBUTION | DEVICE | AUTO | 2012-01-07 11:30 | COMPLETED |  | 2012-01-07 08:19 | 2012-01-07 11:13 | 2012-01-07 11:15 | -121.4478 | 41.9569
5L82 | 879127 | CPCC | CPCC745219 | PP | CA | TULELAKE | TULELAKE | TR_078200_1890033942 | 2012 | Before | 2012-01-27 15:32 | 2012-01-27 15:36 | 0 | 0 | 1 | 4.083 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown fuse. No cause found. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-01-27 18:45 | COMPLETED |  | 2012-01-27 15:32 | 2012-01-27 15:36 | 2012-01-27 17:01 | -121.4402 | 41.9255
5L82 | 872805 | CPCC | CPCC739037 | PP | CA | TULELAKE | TULELAKE | RC_369301_1890125623 | 2012 | Before | 2012-01-07 09:06 | 2012-01-07 11:13 | 40 | 5045.333 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | B/O EQUIPMENT | CONNECTOR OH |  |  |  | SOURCE: recloser opened to repair jumper from outage 739035 | DISTRIBUTION | DEVICE | AUTO | 2012-01-07 12:15 | COMPLETED |  | 2012-01-07 09:06 | 2012-01-09 13:23 | 2012-01-07 11:15 | -121.4478 | 41.9555
5L82 | 872834 | CPCC | CPCC739051 | PP | CA | TULELAKE | TULELAKE | TR_369601_1890067366 | 2012 | Before | 2012-01-07 12:37 | 2012-01-07 13:23 | 1 | 46.383 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: broken fuse serviceman replaced. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-01-07 15:45 | COMPLETED |  | 2012-01-07 12:37 | 2012-01-09 13:24 | 2012-01-07 13:25 | -121.4478 | 41.9601
5L82 | 882302 | CPCC | CPCC747313 | PP | CA | TULELAKE | TULELAKE | TR_040100_1890032381 | 2012 | Before | 2012-02-15 11:37 | 2012-02-15 13:31 | 1 | 114.533 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: B/o cutout at transformer | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-02-15 14:45 | COMPLETED |  | 2012-02-15 11:37 | 2012-02-15 13:32 | 2012-02-15 14:46 | -121.4178 | 41.9373
5L82 | 874449 | CPCC | CPCC739935 | PP | CA | TULELAKE | TULELAKE | Line Cut-56438 | 2012 | Before | 2012-01-16 13:05 | 2012-01-16 16:06 | 4 | 724.933 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: Deteriroated jumper that is broke and and arcing in wind causing momentaries and frequent outages. Crew to make repairs. | DISTRIBUTION | DEVICE | MANUAL | 2012-01-16 17:30 | COMPLETED |  | 2012-01-16 13:05 | 2012-01-16 16:06 | 2012-01-16 16:27 | -121.4186 | 41.912
5L82 | 872806 | CPCC | CPCC739036 | PP | CA | TULELAKE | TULELAKE | TR_335700_1890074594 | 2012 | Before | 2012-01-07 08:20 | 2012-01-07 11:13 | 2 | 344.767 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: customer experiencing part power due to outage 739035 | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-01-07 11:30 | COMPLETED |  | 2012-01-07 08:20 | 2012-01-07 11:13 | 2012-01-07 11:15 | -121.4058 | 41.9612
5L82 | 885411 | CPCC | CPCC749881 | PP | CA | TULELAKE | TULELAKE | OH_073901_1890034153 | 2012 | Before | 2012-02-24 18:28 | 2012-02-24 20:36 | 30 | 3832.5 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: patrolled, nothing found. refused and held. | DISTRIBUTION | DEVICE | AUTO | 2012-02-24 21:30 | COMPLETED |  | 2012-02-24 18:28 | 2012-02-24 20:36 | 2012-02-25 01:15 | -121.4494 | 41.9363
5L82 | 897912 | CPCC | CPCC764530 | PP | CA | TULELAKE | TULELAKE | RC_369301_1890125623 | 2012 | Before | 2012-04-07 13:21 | 2012-04-07 17:45 | 112 | 29579.2 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | POLE OH |  |  |  |  | DISTRIBUTION | DEVICE | MANUAL | 2012-04-07 19:00 | COMPLETED |  | 2012-04-07 13:48 | 2012-04-07 17:45 | 2012-04-07 18:00 | -121.4478 | 41.9555
5L82 | 899711 | CPCC | CPCC765618 | PP | CA | TULELAKE | TULELAKE | TR_209503_1890035161 | 2012 | Before | 2012-04-16 11:03 | 2012-04-16 11:10 | 1 | 7 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: B/O secondary connectors. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2012-04-16 11:03 | 2012-04-16 11:10 | 2012-04-16 11:30 | -121.4194 | 41.9002
5L82 | 900801 | CPCC | CPCC766136 | PP | CA | TULELAKE | TULELAKE | TUL_CB5L82 | 2012 | Before | 2012-04-21 21:06 | 2012-04-21 23:10 | 496 | 61388.267 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Loss of transmission line caused outage, patroling | DISTRIBUTION | DEVICE | AUTO | 2012-04-22 00:15 | COMPLETED |  | 2012-04-21 21:08 | 2012-04-21 23:20 | 2012-04-22 01:27 | -121.4714 | 41.9534
5L82 | 894973 | CPCC | CPCC761522 | PP | CA | TULELAKE | TULELAKE | CB_5L82 | 2012 | Before | 2012-03-28 02:07 | 2012-03-28 03:30 | 495 | 41200.5 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Cb open at the substation, patrolling no cause found | DISTRIBUTION | DEVICE | MANUAL | 2012-03-28 06:45 | COMPLETED |  | 2012-03-28 02:36 | 2012-03-29 14:29 | 2012-03-28 05:36 | -121.4714 | 41.9534
5L82 | 906117 | CPCC | CPCC769479 | PP | CA | TULELAKE | TULELAKE | OH_334900_1890074682 | 2012 | Before | 2012-05-14 19:25 | 2012-05-14 20:26 | 49 | 2974.3 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: wind blew phases together | DISTRIBUTION | DEVICE | AUTO | 2012-05-14 23:00 | COMPLETED |  | 2012-05-14 19:48 | 2012-05-14 20:26 | 2012-05-14 21:14 | -121.4067 | 41.9648
5L82 | 918574 | CPCC | CPCC776335 | PP | CA | TULELAKE | TULELAKE | TR_024900_1890031031 | 2012 | Before | 2012-07-02 05:44 | 2012-07-02 07:59 | 3 | 406.65 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown fuse...nothing found wrong so refused and holding | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-07-02 08:45 | COMPLETED |  | 2012-07-02 05:44 | 2012-07-02 07:59 | 2012-07-02 08:32 | -121.3698 | 41.9501
5L82 | 920421 | CPCC | CPCC777043 | PP | CA | TULELAKE | TULELAKE | OH_060202_1890037457 | 2012 | Before | 2012-07-08 07:54 | 2012-07-08 13:18 | 15 | 4861.5 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Line down needs crew | DISTRIBUTION | DEVICE | AUTO | 2012-07-08 11:00 | COMPLETED |  | 2012-07-08 07:54 | 2012-07-08 13:18 | 2012-07-08 14:56 | -121.4571 | 41.9399
5L82 | 918909 | CPCC | CPCC776464 | PP | CA | TULELAKE | TULELAKE | TR_087200_1890034460 | 2012 | Before | 2012-07-03 09:29 | 2012-07-03 10:19 | 1 | 50 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: blown xfmr fuse. No cause found. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-07-03 12:30 | COMPLETED |  | 2012-07-03 09:29 | 2012-07-03 10:20 | 2012-07-03 11:12 | -121.4229 | 41.9252
5L82 | 1304043 | CPCC | CPCC785724 | PP | CA | TULELAKE | TULELAKE | OH_070200_1890037468 | 2012 | Before | 2012-08-24 14:06 | 2012-08-25 01:50 | 6 | 3801.933 | 0 | 0 | 2 | Y | N | N | N | N |  | INTERFERENCE | OTHER UTILITY/CONTRACTOR |  |  | POLE OH |  |  |  | SOURCE: Pole down and line fuses blown due to a guy wire being snagged by a tractor. Crew to make repairs. | DISTRIBUTION | DEVICE | MANUAL | 2012-08-25 02:47 | COMPLETED |  | 2012-08-24 14:06 | 2012-08-25 01:50 | 2012-08-25 01:56 | -121.457 | 41.9251
5L82 | 1302609 | CPCC | CPCC785042 | PP | CA | TULELAKE | TULELAKE | TR_230501_1890029956 | 2012 | Before | 2012-08-19 11:58 | 2012-08-19 13:32 | 2 | 188.4 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: refused | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-08-19 15:00 | COMPLETED |  | 2012-08-19 11:58 | 2012-08-19 13:32 | 2012-08-19 14:01 | -121.4957 | 41.9008
5L82 | 1360756 | CPCC | CPCC829253 | PP | CA | TULELAKE | TULELAKE | TR_019305_1890027772 | 2013 | Before | 2013-04-29 09:16 | 2013-04-29 10:39 | 1 | 83.717 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Secondary line pulled down by equipment. Serviceman re-attched service wire caused by pulled apart connetors. Serviceman resqueesing wire connector with no damage. | DISTRIBUTION | CUSTOMER | AUTO | 2013-04-29 12:15 | COMPLETED |  | 2013-04-29 09:16 | 2013-04-29 10:39 | 2013-04-29 10:45 | -121.4579 | 41.9411
5L82 | 1374511 | CPCC | CPCC838039 | PP | CA | TULELAKE | TULELAKE | TR_268002_1890072982 | 2013 | Before | 2013-06-21 21:24 | 2013-06-21 23:41 | 1 | 136.75 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: refused | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-06-22 00:30 | COMPLETED |  | 2013-06-21 21:24 | 2013-06-24 14:06 | 2013-06-22 02:50 | -121.3599 | 41.9652
5L82 | 1361992 | CPCC | CPCC829873 | PP | CA | TULELAKE | TULELAKE | TR_180700_1890044665 | 2013 | Before | 2013-05-03 17:57 | 2013-05-03 19:14 | 1 | 77.5 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | SOURCE: burnt jumper to cut out | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-05-03 21:00 | COMPLETED |  | 2013-05-03 17:57 | 2013-05-03 19:14 | 2013-05-03 21:50 | -121.3378 | 41.9181
5L82 | 1363862 | CPCC | CPCC831692 | PP | CA | TULELAKE | TULELAKE | Line Cut-74774 | 2013 | Before | 2013-05-09 18:47 | 2013-05-09 18:54 | 494 | 3425.067 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  |  | DISTRIBUTION | DEVICE | AUTO | 2013-05-09 22:00 | COMPLETED |  | 2013-05-09 18:47 | 2013-05-09 19:24 | 2013-05-09 20:47 | -121.4713 | 41.9535
5L82 | 1361931 | CPCC | CPCC829842 | PP | CA | TULELAKE | TULELAKE | TR_349001_1890074968 | 2013 | Before | 2013-05-03 12:25 | 2013-05-03 15:03 | 1 | 157.783 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | CONSTRUCTION |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman reports transformer cut-outs open. He will close cut-outs and report. He has closed back in and power is restored. Pacificorp contractors left cut-outs open after they had completed their work. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-05-03 15:30 | COMPLETED |  | 2013-05-03 12:25 | 2013-05-03 15:03 | 2013-05-03 15:30 | -121.3784 | 41.9507
5L82 | 1360586 | CPCC | CPCC829156 | PP | CA | TULELAKE | TULELAKE | TR_357403_1890065855 | 2013 | Before | 2013-04-28 07:46 | 2013-04-28 08:58 | 1 | 71.75 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | SOURCE: sec connectors replaced | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-04-28 11:00 | COMPLETED |  | 2013-04-28 07:46 | 2013-04-28 08:58 | 2013-04-28 10:10 | -121.4719 | 41.9568
5L82 | 1387841 | CPCC | CPCC844477 | PP | CA | TULELAKE | TULELAKE | TR_352902_1890073280 | 2013 | Before | 2013-08-02 09:44 | 2013-08-02 10:44 | 1 | 59.483 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown x-fmr fuse, no cause found, Serviceman replaced fuse and it held. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-08-02 12:45 | COMPLETED |  | 2013-08-02 09:44 | 2013-08-02 10:44 | 2013-08-02 10:47 | -121.372 | 41.9646
5L82 | 1395909 | CPCC | CPCC847826 | PP | CA | TULELAKE | TULELAKE | OH_190401_1890037442 | 2013 | Before | 2013-08-22 09:21 | 2013-08-22 12:30 | 3 | 566.9 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Crew needed to make repairs to the overhead primary that is down due to lightning. | DISTRIBUTION | DEVICE | AUTO | 2013-08-22 12:30 | COMPLETED |  | 2013-08-22 09:21 | 2013-08-22 12:30 | 2013-08-22 13:53 | -121.4571 | 41.8989
5L82 | 1395954 | CPCC | CPCC847829 | PP | CA | TULELAKE | TULELAKE | TR_060205_1890033478 | 2013 | Before | 2013-08-22 09:28 | 2013-08-22 14:08 | 2 | 560.633 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | TRANSFORMER OH |  |  |  | SOURCE: District to assign crew replaced transformers | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-08-22 12:30 | COMPLETED |  | 2013-08-22 09:28 | 2013-08-22 14:08 | 2013-08-22 15:02 | -121.4571 | 41.9401
5L82 | 1400794 | CPCC | CPCC853376 | PP | CA | TULELAKE | TULELAKE | TR_181800_1890044762 | 2013 | Before | 2013-09-06 13:09 | 2013-09-06 14:18 | 3 | 207.85 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman refused transformer and power is on. No cause found. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-09-06 16:15 | COMPLETED |  | 2013-09-06 13:09 | 2013-09-06 14:18 | 2013-09-06 15:11 | -121.3371 | 41.9194
5L82 | 1385550 | CPCC | CPCC843547 | PP | CA | TULELAKE | TULELAKE | TUL_CB5L82 | 2013 | Before | 2013-07-25 21:27 | 2013-07-25 23:45 | 495 | 68103.75 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE | WEATHER | LIGHTNING | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Broken transmission insulator. | DISTRIBUTION | DEVICE | MANUAL | 2013-07-26 01:30 | COMPLETED |  | 2013-07-25 21:27 | 2013-07-25 23:47 | 2013-07-26 00:02 | -121.4714 | 41.9534
5L82 | 1387662 | CPCC | CPCC844427 | PP | CA | TULELAKE | TULELAKE | TR_134700_1890037516 | 2013 | Before | 2013-08-01 17:15 | 2013-08-01 18:39 | 1 | 84.333 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: District Lineman refused transformer ok. Cause is unknown. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-08-01 20:15 | COMPLETED |  | 2013-08-01 17:15 | 2013-08-02 10:18 | 2013-08-01 18:42 | -121.35 | 41.9184
5L82 | 1418143 | CPCC | CPCC864559 | PP | CA | TULELAKE | TULELAKE | RC_339001_1890125626 | 2013 | Before | 2013-10-29 20:31 | 2013-10-30 00:50 | 72 | 18699.6 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (PROTECTED SPECIES) (BMTS) |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: heron | DISTRIBUTION | DEVICE | AUTO | 2013-10-29 23:45 | COMPLETED |  | 2013-10-29 20:42 | 2013-10-30 00:50 | 2013-10-30 06:24 | -121.3976 | 41.9507
5L82 | 1456692 | CPCC | CPCC892696 | PP | CA | TULELAKE | TULELAKE | Line Cut-84564 | 2014 | After | 2014-04-10 14:15 | 2014-04-10 14:35 | 487 | 7398.284 | 0 | 0 | 2 | Y | N | Y | Y | N |  | OPERATIONAL | PACIFICORP EMPLOYEE - FIELD |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Tie hit a brace bolt with holds on recloser and sub which opened up both. | DISTRIBUTION | DEVICE | AUTO | 2014-04-10 17:30 | COMPLETED |  | 2014-04-10 14:23 | 2014-04-10 14:35 | 2014-04-10 15:59 | -121.4714 | 41.9533
5L82 | 1459186 | CPCC | CPCC894026 | PP | CA | TULELAKE | TULELAKE | RC_369161_1890125624 | 2014 | After | 2014-04-21 14:28 | 2014-04-21 14:43 | 72 | 1059.6 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Recloser 357 opened when CB 5L82 closed, so serviceman is patroling again. These 72 customers never on and associate to 894006 | DISTRIBUTION | DEVICE | AUTO | 2014-04-21 17:30 | COMPLETED |  | 2014-04-21 14:28 | 2014-04-21 14:43 | 2014-04-21 15:23 | -121.4478 | 41.9518
5L82 | 1462786 | CPCC | CPCC895734 | PP | CA | TULELAKE | TULELAKE | TR_326200_1890076274 | 2014 | After | 2014-04-30 15:17 | 2014-04-30 16:49 | 1 | 91.917 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: Serviceman repaired B/O connectors, power restored | DISTRIBUTION | CUSTOMER | AUTO | 2014-04-30 18:30 | COMPLETED |  | 2014-04-30 15:17 | 2014-04-30 16:49 | 2014-04-30 16:54 | -121.4235 | 41.9541
5L82 | 1458644 | CPCC | CPCC893737 | PP | CA | TULELAKE | TULELAKE | OH_060202_1890037457 | 2014 | After | 2014-04-18 09:35 | 2014-04-18 11:00 | 13 | 1107.383 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Patroled line and will close in on test @ pole A 1397 Sw 9106 | DISTRIBUTION | DEVICE | AUTO | 2014-04-18 12:45 | COMPLETED |  | 2014-04-18 09:35 | 2014-04-18 11:00 | 2014-04-18 11:29 | -121.4571 | 41.9399
5L82 | 1456373 | CPCC | CPCC892579 | PP | CA | TULELAKE | TULELAKE | TR_062302_1890033615 | 2014 | After | 2014-04-09 09:48 | 2014-04-09 11:56 | 1 | 127.75 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | OTHER INTERFERING OBJECT |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman reports uknown object snagged service, repairs made, power restored | DISTRIBUTION | CUSTOMER | AUTO | 2014-04-09 13:00 | COMPLETED |  | 2014-04-09 09:48 | 2014-04-09 11:56 | 2014-04-09 12:38 | -121.4523 | 41.9404
5L82 | 1458044 | CPCC | CPCC893419 | PP | CA | TULELAKE | TULELAKE | TR_257900_1890062548 | 2014 | After | 2014-04-15 17:32 | 2014-04-15 19:25 | 3 | 338.85 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Deteriorated xfmr fuses. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-04-15 20:45 | COMPLETED |  | 2014-04-15 17:32 | 2014-04-15 19:25 | 2014-04-15 22:08 | -121.4526 | 41.9789
5L82 | 1459204 | CPCC | CPCC894006 | PP | CA | TULELAKE | TULELAKE | Line Cut-84915 | 2014 | After | 2014-04-21 13:06 | 2014-04-21 15:24 | 489 | 38438.127 | 0 | 0 | 3 | Y | N | Y | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Excavator took down lines with hold on circuit PROSPER: Bad modeling. Added 1customer to CPCC894006. | DISTRIBUTION | DEVICE | MANUAL | 2014-04-21 17:00 | COMPLETED |  | 2014-04-21 13:15 | 2014-04-22 08:31 | 2014-04-21 15:53 | -121.4713 | 41.9533
5L82 | 1480382 | CPCC | CPCC905149 | PP | CA | TULELAKE | TULELAKE | TR_107201_1890032914 | 2014 | After | 2014-07-06 18:25 | 2014-07-06 19:54 | 1 | 88.267 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: Replaced bad service connector | DISTRIBUTION | CUSTOMER | AUTO | 2014-07-06 21:30 | COMPLETED |  | 2014-07-06 18:25 | 2014-07-06 19:54 | 2014-07-06 21:03 | -121.3838 | 41.9256
5L82 | 1491082 | CPCC | CPCC911485 | PP | CA | TULELAKE | TULELAKE | OH_052901_1890033219 | 2014 | After | 2014-08-06 09:06 | 2014-08-06 10:16 | 2 | 140.067 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Lightning caused fuse to blow serviceman refused and restored service. | DISTRIBUTION | DEVICE | AUTO | 2014-08-06 12:15 | COMPLETED |  | 2014-08-06 09:06 | 2014-08-06 10:16 | 2014-08-06 13:59 | -121.4331 | 41.9502
5L82 | 1490781 | CPCC | CPCC911416 | PP | CA | TULELAKE | TULELAKE | TR_043900_1890152696 | 2014 | After | 2014-08-05 16:52 | 2014-08-05 18:24 | 1 | 92.083 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: refused | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-08-05 20:00 | COMPLETED |  | 2014-08-05 16:52 | 2014-08-05 18:24 | 2014-08-05 19:34 | -121.412 | 41.9501
5L82 | 1475372 | CPCC | CPCC902448 | PP | CA | TULELAKE | TULELAKE | TR_054901_1890033174 | 2014 | After | 2014-06-18 11:41 | 2014-06-18 12:17 | 2 | 73.5 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman reports fuse blown on transformer, caused by starling, refused and it held, power restored | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-06-18 14:45 | COMPLETED |  | 2014-06-18 11:41 | 2014-06-18 12:17 | 2014-06-18 14:03 | -121.4279 | 41.9498
5L82 | 1479436 | CPCC | CPCC904732 | PP | CA | TULELAKE | TULELAKE | RC_369301_1890125623 | 2014 | After | 2014-07-02 18:20 | 2014-07-02 19:28 | 115 | 7848.75 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: limb cleared from primary | DISTRIBUTION | DEVICE | AUTO | 2014-07-02 22:00 | COMPLETED |  | 2014-07-02 18:58 | 2014-07-02 19:28 | 2014-07-02 23:59 | -121.4478 | 41.9555
5L82 | 1491919 | CPCC | CPCC912058 | PP | CA | TULELAKE | TULELAKE | TR_063901_1890044127 | 2014 | After | 2014-08-09 13:18 | 2014-08-09 15:39 | 1 | 140.683 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | SOURCE: B/O secondary connector | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-08-09 16:30 | COMPLETED |  | 2014-08-09 13:18 | 2014-08-09 15:39 | 2014-08-09 15:43 | -121.3325 | 41.9499
5L82 | 1476887 | CPCC | CPCC903344 | PP | CA | TULELAKE | TULELAKE | RC_369161_1890125624 | 2014 | After | 2014-06-24 10:18 | 2014-06-24 11:51 | 144 | 13440 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | LIGHTNING ARRESTER OH |  |  |  | SOURCE: Serviceman bypassed FR 9015 due to a b/o lightning arrestor and verified FR 0357 is open. At 11:51 serviceman has closed FR 0357 on test and it held. | DISTRIBUTION | DEVICE | AUTO | 2014-06-24 13:45 | COMPLETED |  | 2014-06-24 10:34 | 2014-06-24 11:54 | 2014-06-24 12:48 | -121.4478 | 41.9518
5L82 | 1499207 | CPCC | CPCC916954 | PP | CA | TULELAKE | TULELAKE | OH_249500_1890189289 | 2014 | After | 2014-09-03 12:58 | 2014-09-03 15:14 | 2 | 271.5 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | SOURCE: Serviceman reports blown line fuse, patrolling Line, found, down guy that had been hit by vehichke, causing phases to slap together, which blew fuse,,,,unknown perp. | DISTRIBUTION | DEVICE | AUTO | 2014-09-03 16:00 | COMPLETED |  | 2014-09-03 12:58 | 2014-09-03 15:14 | 2014-09-03 16:13 | -121.4586 | 41.9002
5L82 | 1539958 | CPCC | CPCC952037 | PP | CA | TULELAKE | TULELAKE | TR_331000_1890074559 | 2015 | After | 2015-02-19 13:49 | 2015-02-19 14:58 | 1 | 69.117 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Serviceman found a broken cutout; will give info to GF to schedule to repair at a later time. Okay'd with customer. Doesn't need power for awhile. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-02-19 17:00 | COMPLETED |  | 2015-02-19 13:50 | 2015-02-19 15:09 | 2015-02-19 15:14 | -121.4137 | 41.9505
5L82 | 1538256 | CPCC | CPCC950553 | PP | CA | TULELAKE | TULELAKE | TR_311402_1890077471 | 2015 | After | 2015-02-09 14:14 | 2015-02-09 16:00 | 3 | 319.95 | 0 | 0 | 1 | Y | N | N | N | Y | 2015/02/05 CA | TREES | TREE - NON-PREVENTABLE |  |  | CUT-OUT B/O OH |  |  |  |  | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-02-09 17:15 | COMPLETED |  | 2015-02-09 14:14 | 2015-02-10 14:30 | 2015-02-10 14:33 | -121.3367 | 41.9575
5L82 | 1540998 | CPCC | CPCC952573 | PP | CA | TULELAKE | TULELAKE | TR_086901_1890034272 | 2015 | After | 2015-02-24 17:43 | 2015-02-24 19:27 | 2 | 208.2 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: refused | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-02-24 20:45 | COMPLETED |  | 2015-02-24 17:43 | 2015-02-24 19:27 | 2015-02-24 19:28 | -121.4248 | 41.9358
5L82 | 1530124 | CPCC | CPCC942872 | PP | CA | TULELAKE | TULELAKE | TR_320060_1890076222 | 2015 | After | 2015-01-04 16:54 | 2015-01-04 21:12 | 1 | 257.5 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  |  | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-01-04 20:00 | COMPLETED |  | 2015-01-04 16:54 | 2015-01-05 04:29 | 2015-01-05 04:33 | -121.435 | 41.9507
5L82 | 1527646 | CPCC | CPCC941614 | PP | CA | TULELAKE | TULELAKE | TR_063900_1890044139 | 2014 | After | 2014-12-24 12:04 | 2014-12-24 14:02 | 1 | 117.583 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  |  | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-12-24 15:15 | COMPLETED |  | 2014-12-24 12:05 | 2014-12-24 15:37 | 2014-12-24 15:43 | -121.3327 | 41.9502
5L82 | 1526431 | CPCC | CPCC940232 | PP | CA | TULELAKE | TULELAKE | TR_155900_1890035607 | 2014 | After | 2014-12-19 12:10 | 2014-12-19 14:02 | 2 | 222.633 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman replaced blown transformer fuse, no cause found | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-12-19 15:15 | COMPLETED |  | 2014-12-19 12:11 | 2014-12-19 14:48 | 2014-12-19 14:53 | -121.3886 | 41.922
5L82 | 1537264 | CPCC | CPCC949487 | PP | CA | TULELAKE | TULELAKE | RC_359200_1890154304 | 2015 | After | 2015-02-09 00:01 | 2015-02-09 05:35 | 197 | 58516.817 | 0 | 0 | 2 | Y | N | N | N | Y | 2015/02/05 CA | WEATHER | WIND |  |  | CROSS ARM OH |  |  |  | SOURCE: broken cross arm Rd 102 | DISTRIBUTION | DEVICE | AUTO | 2015-02-09 04:30 | COMPLETED |  | 2015-02-09 01:29 | 2015-02-09 06:29 | 2015-02-09 06:33 | -121.4689 | 41.9531
5L82 | 1538029 | CPCC | CPCC949481 | PP | CA | TULELAKE | TULELAKE | TR_314900_1890075977 | 2015 | After | 2015-02-09 01:02 | 2015-02-09 05:36 | 1 | 274.35 | 0 | 0 | 1 | Y | N | N | N | Y | 2015/02/05 CA | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  |  | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-02-09 04:15 | COMPLETED |  | 2015-02-09 01:02 | 2015-02-10 12:51 | 2015-02-10 12:53 | -121.44 | 41.9647
5L82 | 1538038 | CPCC | CPCC949514 | PP | CA | TULELAKE | TULELAKE | OH_073901_1890034153 | 2015 | After | 2015-02-09 06:15 | 2015-02-09 11:20 | 29 | 8824.7 | 0 | 0 | 1 | Y | N | N | N | Y | 2015/02/05 CA | WEATHER | WIND |  |  | POLE OH |  |  |  | SOURCE: Wind caused broken pole, wire on ground, crew made repairs | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2015-02-09 06:15 | 2015-02-10 12:56 | 2015-02-10 12:58 | -121.4494 | 41.9363
5L82 | 1559696 | CPCC | CPCC964140 | PP | CA | TULELAKE | TULELAKE | SB_173900_1890037386 | 2015 | After | 2015-05-12 21:30 | 2015-05-12 22:41 | 125 | 8837.5 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | INTERFERENCE | VEHICLE ACCIDENT | POLE OH |  |  |  | SOURCE: Opened line to replace pole hit by a tractor. | DISTRIBUTION | DEVICE | MANUAL | 2015-05-12 23:00 | COMPLETED |  | 2015-05-12 21:30 | 2015-05-13 00:28 | 2015-05-13 00:33 | -121.4314 | 41.9218
5L82 | 1549069 | CPCC | CPCC957790 | PP | CA | TULELAKE | TULELAKE | TUL_CB5L82 | 2015 | After | 2015-04-02 14:41 | 2015-04-02 17:31 | 492 | 25330.4 | 0 | 0 | 2 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Crop Duster clipped overhead line knocking conductor down, causing CB 5L82 to lock out, crew isolated down line and closed Cb picking up all customers but 2, crew to make repairs | DISTRIBUTION | DEVICE | AUTO | 2015-04-02 18:00 | COMPLETED |  | 2015-04-02 14:48 | 2015-04-02 17:32 | 2015-04-02 17:33 | -121.4714 | 41.9533
5L82 | 1578505 | CPCC | CPCC975722 | PP | CA | TULELAKE | TULELAKE | TR_329902_1890182415 | 2015 | After | 2015-07-10 05:33 | 2015-07-10 09:15 | 1 | 221.817 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Trans fuse | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2015-07-10 09:45 | COMPLETED |  | 2015-07-10 05:33 | 2015-07-10 09:34 | 2015-07-10 09:38 | -121.4179 | 41.9648
5L82 | 1576299 | CPCC | CPCC973970 | PP | CA | TULELAKE | TULELAKE | TR_181800_1890044762 | 2015 | After | 2015-07-05 18:11 | 2015-07-05 21:57 | 3 | 676.7 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown xfmr fuse due to lightning. Serviceman refused and it held. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-07-05 21:15 | COMPLETED |  | 2015-07-05 18:12 | 2015-07-05 23:42 | 2015-07-05 23:43 | -121.3371 | 41.9194
5L82 | 1578402 | CPCC | CPCC975680 | PP | CA | TULELAKE | TULELAKE | TR_311404_1890077461 | 2015 | After | 2015-07-09 19:41 | 2015-07-09 20:40 | 1 | 58.65 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: refused | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-07-09 22:45 | COMPLETED |  | 2015-07-09 19:41 | 2015-07-09 22:00 | 2015-07-09 22:03 | -121.3362 | 41.9569
5L82 | 1578538 | CPCC | CPCC975748 | PP | CA | TULELAKE | TULELAKE | TR_226202_1890076822 | 2015 | After | 2015-07-10 08:59 | 2015-07-10 10:00 | 2 | 122.933 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman found blown transformer fuse, tested transformer, good. Closed on test and it held. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-07-10 12:00 | COMPLETED |  | 2015-07-10 08:59 | 2015-07-10 10:54 | 2015-07-10 10:58 | -121.383 | 41.9831
5L82 | 1567865 | CPCC | CPCC968872 | PP | CA | TULELAKE | TULELAKE | TR_337300_1890074702 | 2015 | After | 2015-06-10 16:21 | 2015-06-10 17:31 | 1 | 69.733 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Line fuse | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-06-10 19:30 | COMPLETED |  | 2015-06-10 16:21 | 2015-06-10 18:36 | 2015-06-10 18:38 | -121.4015 | 41.9559
5L82 | 1582100 | CPCC | CPCC979129 | PP | CA | TULELAKE | TULELAKE | Line Cut-97156 | 2015 | After | 2015-07-21 16:44 | 2015-07-21 17:56 | 493 | 35380.967 | 0 | 0 | 1 | Y | N | N | N | Y | CA Tulelake/Alturas 07-20-2015 | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE | WEATHER | LIGHTNING | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Loss of transmission | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2015-07-21 16:51 | 2015-07-21 19:26 | 2015-07-21 19:28 | -121.4713 | 41.9537
5L82 | 1567486 | CPCC | CPCC968490 | PP | CA | TULELAKE | TULELAKE | Line Cut-96138 | 2015 | After | 2015-06-09 16:40 | 2015-06-09 21:30 | 493 | 142764.583 | 0 | 0 | 1 | Y | N | N | N | Y | CA Tulelake/Alturas 06-09-2015 | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: PROSPER: see outage TRAN1567609 | DISTRIBUTION | DEVICE | AUTO | 2015-06-09 20:00 | COMPLETED |  | 2015-06-09 16:50 | 2015-06-15 14:31 | 2015-06-09 22:08 | -121.4713 | 41.9536
5L82 | 1582166 | CPCC | CPCC979214 | PP | CA | TULELAKE | TULELAKE | OH_249500_1890189289 | 2015 | After | 2015-07-21 20:55 | 2015-07-21 23:12 | 2 | 274.767 | 0 | 0 | 1 | Y | N | N | N | Y | CA Tulelake/Alturas 07-20-2015 | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | POLE FIRE | POLE OH |  |  |  | SOURCE: Serviceman de-energized tap line to put out a pole fire. Line will stay de-energized for the night so crew can assess damage during daylight | DISTRIBUTION | DEVICE | AUTO | 2015-07-22 | COMPLETED |  | 2015-07-21 20:55 | 2015-07-22 04:44 | 2015-07-22 04:48 | -121.4586 | 41.9002
5L82 | 1581775 | CPCC | CPCC978775 | PP | CA | TULELAKE | TULELAKE | Line Cut-97119 | 2015 | After | 2015-07-20 20:25 | 2015-07-20 20:54 | 493 | 14477.767 | 0 | 0 | 1 | Y | N | N | N | Y | CA Tulelake/Alturas 07-20-2015 | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE | WEATHER | LIGHTNING | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: isolated opened 3L173 at Austin Tap and tested | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2015-07-20 20:28 | 2015-07-20 21:21 | 2015-07-20 21:23 | -121.4713 | 41.9537
5L82 | 1578501 | CPCC | CPCC975724 | PP | CA | TULELAKE | TULELAKE | OH_311400_1890077841 | 2015 | After | 2015-07-10 05:34 | 2015-07-10 08:52 | 9 | 1778.85 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Line fuse blown crew patroled and found nothing Lightning in the area. | DISTRIBUTION | DEVICE | AUTO | 2015-07-10 09:45 | COMPLETED |  | 2015-07-10 05:37 | 2015-07-10 09:13 | 2015-07-10 09:18 | -121.3358 | 41.9576
5L82 | 1566756 | CPCC | CPCC968016 | PP | CA | TULELAKE | TULELAKE | TR_226202_1890076822 | 2015 | After | 2015-06-07 18:42 | 2015-06-07 21:44 | 2 | 363.8 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: refused | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-06-07 21:45 | COMPLETED |  | 2015-06-07 18:42 | 2015-06-08 02:14 | 2015-06-08 02:18 | -121.383 | 41.9831
5L82 | 1566886 | CPCC | CPCC968076 | PP | CA | TULELAKE | TULELAKE | TR_226202_1890076822 | 2015 | After | 2015-06-08 09:56 | 2015-06-08 12:20 | 1 | 143.95 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | SOURCE: Serviceman repaired secondary connections | DISTRIBUTION | CUSTOMER | AUTO | 2015-06-08 13:00 | COMPLETED |  | 2015-06-08 09:56 | 2015-06-08 12:32 | 2015-06-08 12:33 | -121.383 | 41.9831
5L82 | 1590091 | CPCC | CPCC984158 | PP | CA | TULELAKE | TULELAKE | TR_054901_1890033174 | 2015 | After | 2015-08-17 09:26 | 2015-08-17 10:46 | 1 | 79.367 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Starling, Serviceman re-fused and holding, Customers restored | DISTRIBUTION | CUSTOMER | AUTO | 2015-08-17 12:30 | COMPLETED |  | 2015-08-17 09:28 | 2015-08-17 10:52 | 2015-08-17 10:54 | -121.4279 | 41.9498
5L82 | 1598631 | CPCC | CPCC989594 | PP | CA | TULELAKE | TULELAKE | TR_303400_1890075639 | 2015 | After | 2015-09-16 08:57 | 2015-09-16 10:31 | 1 | 93.4 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: Serviceman made repairs to bad connections at xfmr | DISTRIBUTION | CUSTOMER | AUTO | 2015-09-16 12:00 | COMPLETED |  | 2015-09-16 08:58 | 2015-09-16 10:31 | 2015-09-16 10:33 | -121.4407 | 41.9716
5L82 | 1602824 | CPCC | CPCC992386 | PP | CA | TULELAKE | TULELAKE | TR_070900_1890044471 | 2015 | After | 2015-10-03 18:21 | 2015-10-04 | 2 | 679.8 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: responding to outage 992387(20:23). located open fuse, investigated, no cause or damage found, refused & restored | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-10-03 21:30 | COMPLETED |  | 2015-10-03 18:21 | 2015-10-04 00:14 | 2015-10-04 00:18 | -121.3392 | 41.936
5L82 | 1603594 | CPCC | CPCC993188 | PP | CA | TULELAKE | TULELAKE | TR_139400_1890029853 | 2015 | After | 2015-10-07 10:01 | 2015-10-07 10:35 | 3 | 102.05 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown xfmr fuse. No cause found. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-10-07 13:00 | COMPLETED |  | 2015-10-07 10:01 | 2015-10-07 10:35 | 2015-10-07 10:38 | -121.4574 | 41.914
5L82 | 1608662 | CPCC | CPCC996603 | PP | CA | TULELAKE | TULELAKE | TR_086901_1890034272 | 2015 | After | 2015-10-30 18:53 | 2015-10-30 19:58 | 2 | 130.133 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown fuse on transformer caused by bird | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2015-10-30 18:53 | 2015-10-30 22:33 | 2015-10-30 22:38 | -121.4248 | 41.9358
5L82 | 1595044 | CPCC | CPCC987515 | PP | CA | TULELAKE | TULELAKE | TR_226202_1890076822 | 2015 | After | 2015-09-01 17:54 | 2015-09-01 22:19 | 2 | 529.533 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | SOURCE: b/o xfrmr | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-09-01 21:00 | COMPLETED |  | 2015-09-01 17:56 | 2015-09-01 22:26 | 2015-09-01 22:28 | -121.383 | 41.9831
5L82 | 1622267 | CPCC | CPCC1012094 | PP | CA | TULELAKE | TULELAKE | TR_255100_1890072662 | 2015 | After | 2015-12-14 13:08 | 2015-12-14 20:13 | 1 | 425.933 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | SNOW, SLEET AND BLIZZARD |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: No outage. Customer called in primary neutral wire down between 255900 and 255801. | DISTRIBUTION | CUSTOMER | AUTO | 2015-12-14 16:15 | COMPLETED |  | 2015-12-14 13:08 | 2015-12-15 04:50 | 2015-12-15 04:54 | -121.3476 | 41.9678
5L82 | 1612259 | CPCC | CPCC998747 | PP | CA | TULELAKE | TULELAKE | RC_359200_1890154304 | 2015 | After | 2015-11-15 09:15 | 2015-11-15 10:33 | 193 | 14951.067 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: suspect FR 716 open, response dispatched to patrol from recloser(09:37), no cause, close for test(10:32) | DISTRIBUTION | DEVICE | AUTO | 2015-11-15 12:30 | COMPLETED |  | 2015-11-15 09:16 | 2015-11-15 10:48 | 2015-11-15 10:49 | -121.4689 | 41.9531
5L82 | 1615052 | CPCC | CPCC1001660 | PP | CA | TULELAKE | TULELAKE | RC_359200_1890154304 | 2015 | After | 2015-11-24 08:37 | 2015-11-24 11:05 | 193 | 28628.333 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | SNOW, SLEET AND BLIZZARD |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: nothing found will test | DISTRIBUTION | DEVICE | AUTO | 2015-11-24 12:00 | COMPLETED |  | 2015-11-24 08:37 | 2015-11-24 11:27 | 2015-11-24 11:33 | -121.4689 | 41.9531
5L82 | 1652511 | CPCC | CPCC1036686 | PP | CA | TULELAKE | TULELAKE | TUL_CB5L82 | 2016 | After | 2016-04-10 17:59 | 2016-04-10 18:31 | 471 | 14703.05 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Alturas-Hornet-Malin 69 kV line relayed and tested no good. | DISTRIBUTION | DEVICE | AUTO | 2016-04-10 21:15 | COMPLETED |  | 2016-04-10 18:14 | 2016-04-11 10:48 | 2016-04-10 22:37 | -121.4713 | 41.9536
5L82 | 1657775 | CPCC | CPCC1042656 | PP | CA | TULELAKE | TULELAKE | OH_032001_1890031845 | 2016 | After | 2016-04-28 10:17 | 2016-04-28 11:12 | 3 | 164.45 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown fuses at 032001. Cause unknown. Re-fused and holding | DISTRIBUTION | DEVICE | AUTO | 2016-04-28 13:30 | COMPLETED |  | 2016-04-28 10:17 | 2016-04-28 11:13 | 2016-04-28 11:17 | -121.3932 | 41.936
5L82 | 1638814 | CPCC | CPCC1025294 | PP | CA | TULELAKE | TULELAKE | RC_359200_1890154304 | 2016 | After | 2016-02-17 20:32 | 2016-02-18 00:54 | 190 | 49818 | 0 | 0 | 1 | Y | N | N | N | Y | CA Tulelake/Alturas 02-17-2016 | OTHER | OTHER, KNOWN CAUSE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: located open FR 716 clsoeing for test, no hazrd calls, restored, suspect on ging line slap issue during inclemmet weather | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2016-02-17 20:48 | 2016-02-18 01:20 | 2016-02-18 01:23 | -121.4689 | 41.9531
5L82 | 1638815 | CPCC | CPCC1025290 | PP | CA | TULELAKE | TULELAKE | RC_369301_1890125623 | 2016 | After | 2016-02-17 20:34 | 2016-02-18 00:40 | 106 | 26026.533 | 0 | 0 | 1 | Y | N | N | N | Y | CA Tulelake/Alturas 02-17-2016 | OTHER | OTHER, KNOWN CAUSE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: suspect open FR 1456, froze outage to model(23:30), FR 1456 is open, patroling(00:20), no cause found, close for test & report(00:35), colded & restored; suspect line slap | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2016-02-17 20:41 | 2016-02-18 01:20 | 2016-02-18 01:23 | -121.4478 | 41.9555
5L82 | 1675057 | CPCC | CPCC1051693 | PP | CA | TULELAKE | TULELAKE | TUL_CB5L82 | 2016 | After | 2016-06-18 03:49 | 2016-06-18 04:09 | 470 | 9039.667 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Loss of transmission | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2016-06-18 03:49 | 2016-06-20 09:33 | 2016-06-18 17:39 | -121.4714 | 41.9532
5L82 | 1661136 | CPCC | CPCC1043485 | PP | CA | TULELAKE | TULELAKE | TR_139901_1890037479 | 2016 | After | 2016-05-04 16:12 | 2016-05-04 20:07 | 1 | 234.117 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | SOURCE: B/O xfmr | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2016-05-04 19:15 | COMPLETED |  | 2016-05-04 16:13 | 2016-05-05 02:27 | 2016-05-05 02:28 | -121.3397 | 41.9219
5L82 | 1664149 | CPCC | CPCC1044848 | PP | CA | TULELAKE | TULELAKE | RC_359200_1890154304 | 2016 | After | 2016-05-12 13:50 | 2016-05-12 16:35 | 190 | 31305.667 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | INTERFERENCE | VEHICLE ACCIDENT | POLE OH |  |  |  | SOURCE: STATED HIS TOW HITCH ON TRUCK HIT THE POLE AND SNAPPED IT IN HALF, HE STATED WIRES ARE STILL UP 300-400 FT FROM TULELAKE EXIT OFF OF HIGHWAY 139 pole A 4933 needs changing | DISTRIBUTION | DEVICE | MANUAL | 2016-05-12 17:00 | COMPLETED |  | 2016-05-12 13:50 | 2016-05-12 18:09 | 2016-05-12 18:13 | -121.4689 | 41.9531
5L82 | 1702515 | CPCC | CPCC1070488 | PP | CA | TULELAKE | TULELAKE | TR_107201_1890032914 | 2016 | After | 2016-09-19 09:26 | 2016-09-19 11:11 | 1 | 104.967 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: Burnt up secondary connector | DISTRIBUTION | CUSTOMER | AUTO | 2016-09-19 12:30 | COMPLETED |  | 2016-09-19 09:26 | 2016-09-19 12:32 | 2016-09-19 12:33 | -121.3838 | 41.9256
5L82 | 1690449 | CPCC | CPCC1061504 | PP | CA | TULELAKE | TULELAKE | OH_179201_1890154342 | 2016 | After | 2016-08-05 10:15 | 2016-08-05 19:07 | 7 | 564.802 | 0 | 0 | 2 | Y | N | N | N | N |  | OTHER | OTHER, KNOWN CAUSE |  |  | POLE OH |  |  |  | SOURCE: 1907 - Gary Fields reports custs back on. PROSPER: change time to first out 08/05/2016 10:14:50, was 08/05/2016 9:47:19 | DISTRIBUTION | DEVICE | AUTO | 2016-08-05 13:00 | COMPLETED |  | 2016-08-05 09:48 | 2016-08-12 15:51 | 2016-08-05 22:53 | -121.4182 | 41.9104
5L82 | 1694355 | CPCC | CPCC1064833 | PP | CA | TULELAKE | TULELAKE | TR_196300_1890070513 | 2016 | After | 2016-08-18 06:40 | 2016-08-18 10:21 | 1 | 221.4 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: service drop rubbed thru will replace PROSPER: power out | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2016-08-18 09:45 | COMPLETED |  | 2016-08-18 06:40 | 2016-08-19 08:18 | 2016-08-18 18:03 | -121.4355 | 41.9847
5L82 | 1719577 | CPCC | CPCC1083523 | PP | CA | TULELAKE | TULELAKE | TUL_CB5L82 | 2016 | After | 2016-11-20 14:31 | 2016-11-20 15:33 | 468 | 28867.8 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  |  | DISTRIBUTION | DEVICE | AUTO | 2016-11-20 17:45 | COMPLETED |  | 2016-11-20 14:37 | 2016-11-21 11:01 | 2016-11-20 16:38 | -121.4713 | 41.9532
5L82 | 1708681 | CPCC | CPCC1073765 | PP | CA | TULELAKE | TULELAKE | TR_361401_1890073466 | 2016 | After | 2016-10-09 11:39 | 2016-10-09 12:23 | 1 | 44.383 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown fuse, cause unknown | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2016-10-09 14:45 | COMPLETED |  | 2016-10-09 11:39 | 2016-10-09 14:43 | 2016-10-09 14:48 | -121.3545 | 41.9571
5L82 | 1732419 | CPCC | CPCC1097397 | PP | CA | TULELAKE | TULELAKE | TUL_CB5L82 | 2017 | After | 2017-01-03 23:00 | 2017-01-03 23:26 | 467 | 12274.317 | 0 | 0 | 1 | Y | N | N | N | Y | CA California 01-03-2017 | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE | WEATHER | SNOW, SLEET AND BLIZZARD | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | SOURCE: Loss of Transmission Malin 69kV CB 3L179 Open, suspect storm related issue due to snow and trees | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2017-01-03 23:07 | 2017-01-04 11:06 | 2017-01-04 03:49 | -121.4713 | 41.9534
5L82 | 1747331 | CPCC | CPCC1114698 | PP | CA | TULELAKE | TULELAKE | TR_029901_1890031229 | 2017 | After | 2017-02-15 13:42 | 2017-02-15 14:48 | 1 | 66.017 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: NO cause found | DISTRIBUTION | CUSTOMER | AUTO |  | COMPLETED |  | 2017-02-15 13:43 | 2017-02-15 15:21 | 2017-02-15 15:23 | -121.3601 | 41.9499
5L82 | 1758512 | CPCC | CPCC1123560 | PP | CA | TULELAKE | TULELAKE | TR_183900_1890035002 | 2017 | After | 2017-03-28 08:18 | 2017-03-28 09:19 | 1 | 60.933 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (PROTECTED SPECIES) (BMTS) | ANIMALS | ANIMALS | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Line fuse open at A-7051, Svcman patrolling. Back in service. Bird strike | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2017-03-28 11:30 | COMPLETED |  | 2017-03-28 08:18 | 2017-03-28 09:20 | 2017-03-28 09:23 | -121.4512 | 41.9217
5L82 | 1779228 | CPCC | CPCC1143278 | PP | CA | TULELAKE | TULELAKE | TR_014900_1890027255 | 2017 | After | 2017-05-30 13:50 | 2017-05-30 14:44 | 1 | 54.033 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: secondary connectors | DISTRIBUTION | CUSTOMER | AUTO | 2017-05-30 17:00 | COMPLETED |  | 2017-05-30 13:50 | 2017-05-30 14:51 | 2017-05-30 14:53 | -121.4676 | 41.9489
5L82 | 1784526 | CPCC | CPCC1146326 | PP | CA | TULELAKE | TULELAKE | TR_311402_1890077471 | 2017 | After | 2017-06-14 17:15 | 2017-06-14 19:02 | 1 | 107.2 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown xmfr fuse, cause uknown | DISTRIBUTION | CUSTOMER | AUTO |  | COMPLETED |  | 2017-06-14 17:15 | 2017-06-14 21:42 | 2017-06-14 21:43 | -121.3367 | 41.9575
5L82 | 1780292 | CPCC | CPCC1143895 | PP | CA | TULELAKE | TULELAKE | TR_085501_1890034322 | 2017 | After | 2017-06-02 17:14 | 2017-06-02 18:19 | 1 | 64.45 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: blown xfmr fuses. no cause. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2017-06-02 17:15 | 2017-06-02 18:22 | 2017-06-02 18:28 | -121.4273 | 41.9294
5L82 | 1788241 | CPCC | CPCC1148575 | PP | CA | TULELAKE | TULELAKE | TR_078301_1890033922 | 2017 | After | 2017-06-26 06:14 | 2017-06-26 10:12 | 1 | 237.683 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: BO Cut out | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2017-06-26 10:31 | COMPLETED |  | 2017-06-26 06:14 | 2017-06-26 12:37 | 2017-06-26 12:43 | -121.4409 | 41.9275
5L82 | 1790361 | CPCC | CPCC1149920 | PP | CA | TULELAKE | TULELAKE | TR_054901_1890033174 | 2017 | After | 2017-07-01 11:59 | 2017-07-01 13:16 | 2 | 154 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Deteriorated fuse | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2017-07-01 15:00 | COMPLETED |  | 2017-07-01 11:59 | 2017-07-01 17:45 | 2017-07-01 17:48 | -121.4279 | 41.9498
5L82 | 1798134 | CPCC | CPCC1154485 | PP | CA | TULELAKE | TULELAKE | TUL_CB5L82 | 2017 | After | 2017-07-24 19:10 | 2017-07-24 19:22 | 468 | 5506.8 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: | DISTRIBUTION | DEVICE | AUTO | 2017-07-24 22:15 | COMPLETED |  | 2017-07-24 19:15 | 2017-07-25 09:48 | 2017-07-25 02:28 | -121.4713 | 41.9535
5L82 | 1798551 | CPCC | CPCC1155065 | PP | CA | TULELAKE | TULELAKE | TR_100561_1890032958 | 2017 | After | 2017-07-25 18:18 | 2017-07-25 20:05 | 1 | 107.017 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: blown fuse due to lightning | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2017-07-25 21:30 | COMPLETED |  | 2017-07-25 18:18 | 2017-07-25 21:06 | 2017-07-25 21:08 | -121.3985 | 41.9292
5L82 | 1823070 | CPCC | CPCC1169067 | PP | CA | TULELAKE | TULELAKE | OH_163002_1890036042 | 2017 | After | 2017-10-20 08:27 | 2017-10-20 09:35 | 4 | 270.267 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - TRIMMABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: removed tree: tree company fell tree into line PROSPER: power out | DISTRIBUTION | DEVICE | AUTO | 2017-10-20 11:00 | COMPLETED |  | 2017-10-20 08:27 | 2017-10-23 15:37 | 2017-10-20 13:09 | -121.4116 | 41.9079
5L82 | 1851952 | CPCC | CPCC1191879 | PP | CA | TULELAKE | TULELAKE | TUL_CB5L82 | 2018 | After | 2018-03-01 18:23 | 2018-03-01 18:31 | 468 | 3744 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE | WEATHER | SNOW, SLEET AND BLIZZARD | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Loss of trasmission. Snow in area. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2018-03-01 19:02 | 2018-03-06 13:43 | 2018-03-01 22:29 | -121.4713 | 41.9535
5L82 | 1851950 | CPCC | CPCC1191911 | PP | CA | TULELAKE | TULELAKE | RC_359200_1890154304 | 2018 | After | 2018-03-01 19:46 | 2018-03-01 19:57 | 191 | 2123.283 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | SNOW, SLEET AND BLIZZARD |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: | DISTRIBUTION | DEVICE | AUTO | 2018-03-01 22:30 | COMPLETED |  | 2018-03-01 19:50 | 2018-03-01 22:26 | 2018-03-01 22:29 | -121.4689 | 41.9531
5L82 | 1854580 | CPCC | CPCC1193867 | PP | CA | TULELAKE | TULELAKE | TR_209503_1890035161 | 2018 | After | 2018-03-12 10:31 | 2018-03-12 12:05 | 1 | 93.483 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Replaced B/O fused cutout. PROSPER: power out | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2018-03-12 13:15 | COMPLETED |  | 2018-03-12 10:31 | 2018-03-19 16:16 | 2018-03-12 17:43 | -121.4194 | 41.9002
5L82 | 1859116 | CPCC | CPCC1196169 | PP | CA | TULELAKE | TULELAKE | OH_060202_1890037457 | 2018 | After | 2018-03-29 10:43 | 2018-03-29 14:00 | 12 | 2359.8 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD SUSPECTED, NO MORTALITY |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Associate with 1196167 | DISTRIBUTION | DEVICE | MANUAL | 2018-03-29 16:30 | COMPLETED |  | 2018-03-29 10:43 | 2018-03-29 14:20 | 2018-03-29 14:21 | -121.4571 | 41.9399
5L82 | 1863991 | CPCC | CPCC1198970 | PP | CA | TULELAKE | TULELAKE | TR_257200_1890062781 | 2018 | After | 2018-04-18 10:16 | 2018-04-18 10:55 | 1 | 39.5 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: | DISTRIBUTION | CUSTOMER | AUTO | 2018-04-18 12:30 | COMPLETED |  | 2018-04-18 10:16 | 2018-04-18 14:07 | 2018-04-18 14:10 | -121.4527 | 41.9682
5L82 | 1865339 | CPCC | CPCC1199634 | PP | CA | TULELAKE | TULELAKE | OH_311400_1890077841 | 2018 | After | 2018-04-25 10:45 | 2018-04-25 12:42 | 4 | 468.067 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown line fuse, no cause found | DISTRIBUTION | DEVICE | MANUAL | 2018-04-25 15:00 | COMPLETED |  | 2018-04-25 10:45 | 2018-04-25 14:42 | 2018-04-25 14:45 | -121.3358 | 41.9576
5L82 | 1866083 | CPCC | CPCC1200109 | PP | CA | TULELAKE | TULELAKE | TUL_CB5L82 | 2018 | After | 2018-04-29 04:46 | 2018-04-29 05:34 | 468 | 22479.6 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE | INTERFERENCE | VEHICLE ACCIDENT | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: | DISTRIBUTION | DEVICE | AUTO | 2018-04-29 07:00 | COMPLETED |  | 2018-04-29 04:47 | 2018-04-30 09:52 | 2018-04-29 16:10 | -121.4713 | 41.9535
5L82 | 1870181 | CPCC | CPCC1202857 | PP | CA | TULELAKE | TULELAKE | TR_107700_1890032892 | 2018 | After | 2018-05-19 13:05 | 2018-05-19 14:11 | 2 | 132.633 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown Transformer fuse. no cause found | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2018-05-19 15:30 | COMPLETED |  | 2018-05-19 13:05 | 2018-05-19 15:51 | 2018-05-19 15:55 | -121.3843 | 41.9327
5L82 | 1870488 | CPCC | CPCC1202950 | PP | CA | TULELAKE | TULELAKE | TR_272802_1890076460 | 2018 | After | 2018-05-21 08:03 | 2018-05-21 09:31 | 1 | 88.85 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: | DISTRIBUTION | CUSTOMER | AUTO | 2018-05-21 10:30 | COMPLETED |  | 2018-05-21 08:03 | 2018-05-21 13:52 | 2018-05-21 13:55 | -121.3914 | 41.9774
5L82 | 1871837 | CPCC | CPCC1203940 | PP | CA | TULELAKE | TULELAKE | TR_230501_1890029956 | 2018 | After | 2018-05-27 08:39 | 2018-05-27 14:51 | 1 | 371.883 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD NEST (BMTS) |  |  | TRANSFORMER OH |  |  |  | SOURCE: Inactive bird nest blew around and got into xfmr. xmfr needs replaced. Called for standby crew 10:30 | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2018-05-27 16:45 | COMPLETED |  | 2018-05-27 08:39 | 2018-05-27 18:15 | 2018-05-27 18:20 | -121.4957 | 41.9008
5L82 | 1873397 | CPCC | CPCC1204720 | PP | CA | TULELAKE | TULELAKE | OH_179901_1890034899 | 2018 | After | 2018-06-03 16:19 | 2018-06-03 22:42 | 27 | 4933.366 | 0 | 0 | 2 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Blown fuse, wire down caused by down tree. | DISTRIBUTION | DEVICE | MANUAL | 2018-06-03 23:15 | COMPLETED |  | 2018-06-03 16:34 | 2018-06-04 05:34 | 2018-06-04 05:35 | -121.4182 | 41.9211
5L82 | 1873421 | CPCC | CPCC1204771 | PP | CA | TULELAKE | TULELAKE | OH_179901_1890034899 | 2018 | After | 2018-06-04 07:05 | 2018-06-04 08:02 | 22 | 1261.7 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown fuse at 179901, cause unknown PROSPER: add 1 from CPCC1204777 | DISTRIBUTION | DEVICE | AUTO | 2018-06-04 09:45 | COMPLETED |  | 2018-06-04 07:05 | 2018-06-07 09:38 | 2018-06-04 08:10 | -121.4182 | 41.9211
5L82 | 1888732 | CPCC | CPCC1218405 | PP | CA | TULELAKE | TULELAKE | TR_285500_1890179693 | 2018 | After | 2018-07-28 05:56 | 2018-07-28 07:21 | 1 | 84.517 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2018-07-28 08:30 | COMPLETED |  | 2018-07-28 05:57 | 2018-07-28 17:11 | 2018-07-28 17:15 | -121.2898 | 41.9728
5L82 | 1889419 | CPCC | CPCC1218735 | PP | CA | TULELAKE | TULELAKE | TR_285500_1890179693 | 2018 | After | 2018-07-31 08:53 | 2018-07-31 10:18 | 1 | 84.6 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown fuse, caused by bird | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2018-07-31 11:30 | COMPLETED |  | 2018-07-31 08:53 | 2018-07-31 12:41 | 2018-07-31 12:45 | -121.2898 | 41.9728
5L82 | 1892427 | CPCC | CPCC1220393 | PP | CA | TULELAKE | TULELAKE | TR_285500_1890179693 | 2018 | After | 2018-08-11 09:31 | 2018-08-11 10:39 | 1 | 67.683 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD SUSPECTED, NO MORTALITY |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown fuse; suspected bird. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2018-08-11 12:00 | COMPLETED |  | 2018-08-11 09:31 | 2018-08-11 18:21 | 2018-08-11 18:25 | -121.2894 | 41.9728
5L82 | 1894406 | CPCC | CPCC1221570 | PP | CA | TULELAKE | TULELAKE | TR_285380_1890077807 | 2018 | After | 2018-08-19 11:08 | 2018-08-19 12:35 | 1 | 86.683 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: | DISTRIBUTION | CUSTOMER | AUTO | 2018-08-19 13:30 | COMPLETED |  | 2018-08-19 11:08 | 2018-08-19 18:19 | 2018-08-19 18:20 | -121.2888 | 41.9702
5L82 | 1895663 | CPCC | CPCC1221963 | PP | CA | TULELAKE | TULELAKE | TR_285500_1890179693 | 2018 | After | 2018-08-23 06:50 | 2018-08-23 10:26 | 1 | 215.633 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: starling | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2018-08-23 11:00 | COMPLETED |  | 2018-08-23 06:51 | 2018-08-23 15:58 | 2018-08-23 16:00 | -121.2894 | 41.9728
5L82 | 1900724 | CPCC | CPCC1227577 | PP | CA | TULELAKE | TULELAKE | SB_286400_1890189277 | 2018 | After | 2018-09-15 10:44 | 2018-09-15 13:00 | 2 | 271.8 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown fuse on an isolation bank for ug. No cause found | DISTRIBUTION | DEVICE | MANUAL | 2018-09-15 14:00 | COMPLETED |  | 2018-09-15 12:46 | 2018-09-15 14:53 | 2018-09-15 14:55 | -121.2874 | 41.9721
5L82 | 1903975 | CPCC | CPCC1231380 | PP | CA | TULELAKE | TULELAKE | SB_256203_1890076497 | 2018 | After | 2018-09-30 11:19 | 2018-09-30 11:35 | 55 | 877.25 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | POLE FIRE | POLE OH |  |  |  | SOURCE: Opened line fuses to restore feeder to normal | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2018-09-30 11:34 | 2018-09-30 15:51 | 2018-09-30 15:55 | -121.3459 | 41.9691
5L82 | 1903976 | CPCC | CPCC1231339 | PP | CA | TULELAKE | TULELAKE | SB_334061_1890074459 | 2018 | After | 2018-09-30 04:01 | 2018-09-30 11:38 | 114 | 26288.033 | 0 | 0 | 4 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | POLE OH |  |  |  | SOURCE: Pole fire at 336060. Arcos initiated for 4 man crew and 2 flaggers | DISTRIBUTION | DEVICE | MANUAL | 2018-09-30 15:00 | COMPLETED |  | 2018-09-30 04:01 | 2018-09-30 15:51 | 2018-09-30 15:55 | -121.4067 | 41.9507
5L82 | 1903914 | CPCC | CPCC1231347 | PP | CA | TULELAKE | TULELAKE | RC__1890125624 | 2018 | After | 2018-09-30 06:35 | 2018-09-30 07:18 | 26 | 1120.6 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | POLE OH |  |  |  | SOURCE: Recloser 0357 open due to Pole fire, isolated at sw 2520, closed recloser 0357 | DISTRIBUTION | DEVICE | AUTO | 2018-09-30 09:15 | COMPLETED |  | 2018-09-30 06:35 | 2018-09-30 11:49 | 2018-09-30 11:50 | -121.4478 | 41.952
5L82 | 1903860 | CPCC | CPCC1231283 | PP | CA | TULELAKE | TULELAKE | TUL_CB5L82 | 2018 | After | 2018-09-30 02:08 | 2018-09-30 03:04 | 469 | 26264 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Loss of Malin CB 3L179 | DISTRIBUTION | DEVICE | AUTO | 2018-09-30 03:15 | COMPLETED |  | 2018-09-30 02:12 | 2018-10-03 16:24 | 2018-09-30 05:50 | -121.4713 | 41.9534
5L82 | 1905547 | CPCC | CPCC1232260 | PP | CA | TULELAKE | TULELAKE | TR_118500_1890031376 | 2018 | After | 2018-10-06 09:50 | 2018-10-06 10:52 | 2 | 124.633 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: District Lineman refused O/H transformer bank ok. Cause is unknown. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2018-10-06 12:30 | COMPLETED |  | 2018-10-06 09:50 | 2018-10-06 13:14 | 2018-10-06 13:15 | -121.3622 | 41.9295
5L82 | 1910841 | CPCC | CPCC1235772 | PP | CA | TULELAKE | TULELAKE | TR_047000_1890037375 | 2018 | After | 2018-10-31 14:51 | 2018-10-31 15:56 | 1 | 65.3 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman reports tree through customer's service. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2018-10-31 17:30 | COMPLETED |  | 2018-10-31 14:51 | 2018-10-31 18:41 | 2018-10-31 18:45 | -121.4032 | 41.9359
5L82 | 1920921 | CPCC | CPCC1248941 | PP | CA | TULELAKE | TULELAKE | RC__1890125624 | 2018 | After | 2018-12-14 12:52 | 2018-12-14 18:44 | 140 | 49303.333 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  |  | DISTRIBUTION | DEVICE | MANUAL |  | COMPLETED |  | 2018-12-14 12:52 | 2018-12-17 10:20 | 2018-12-17 10:25 | -121.4478 | 41.952
5L82 | 1924714 | CPCC | CPCC1252867 | PP | CA | TULELAKE | TULELAKE | OH_249500_1890189289 | 2019 | After | 2019-01-02 11:35 | 2019-01-02 12:32 | 1 | 56.75 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CROSS ARM OH |  |  |  | SOURCE: Emergency damage for split cross arm | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2019-01-02 11:35 | 2019-01-02 15:16 | 2019-01-02 15:20 | -121.4587 | 41.9001
5L82 | 1926758 | CPCC | CPCC1255720 | PP | CA | TULELAKE | TULELAKE | TUL_CB5L82 | 2019 | After | 2019-01-10 04:01 | 2019-01-10 04:45 | 469 | 20636 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Loss of Malin CB 3L179 | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2019-01-10 04:15 | 2019-01-10 09:59 | 2019-01-10 06:40 | -121.4713 | 41.9537
5L82 | 1938679 | PROS | PROS1938679 | PP | CA | TULELAKE | TULELAKE |  | 2019 | After | 2019-02-25 11:43 | 2019-02-25 11:47 | 0 | 0 | 469 | 1852.55 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | NO DISTRIBUTION DAMAGE |  |  |  |  | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2019-02-25 13:49 | 2019-02-25 13:49 | 2019-02-25 13:49
5L82 | 1939566 | CPCC | CPCC1268734 | PP | CA | TULELAKE | TULELAKE | TR_183701_1890044548 | 2019 | After | 2019-02-26 10:20 | 2019-02-26 12:28 | 1 | 128.783 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2019-02-26 13:30 | COMPLETED |  | 2019-02-26 10:20 | 2019-02-26 22:18 | 2019-02-26 22:20 | -121.3338 | 41.9182
5L82 | 1939540 | CPCC | CPCC1268431 | PP | CA | TULELAKE | TULELAKE | OH_073901_1890034153 | 2019 | After | 2019-02-26 04:48 | 2019-02-26 07:27 | 28 | 4451.067 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Blown line fuses patrolling for cause | DISTRIBUTION | DEVICE | MANUAL | 2019-02-26 09:00 | COMPLETED |  | 2019-02-26 04:58 | 2019-02-26 22:11 | 2019-02-26 22:15 | -121.4495 | 41.9364
5L82 | 1939551 | CPCC | CPCC1268699 | PP | CA | TULELAKE | TULELAKE | RC_339001_1890125626 | 2019 | After | 2019-02-26 09:37 | 2019-02-26 10:52 | 69 | 5187.65 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2019-02-26 09:37 | 2019-02-26 22:15 | 2019-02-26 22:20 | -121.3977 | 41.9507
5L82 | 1939562 | CPCC | CPCC1268725 | PP | CA | TULELAKE | TULELAKE | OH_182900_1890046370 | 2019 | After | 2019-02-26 09:49 | 2019-02-26 12:28 | 24 | 3818.8 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: | DISTRIBUTION | DEVICE | AUTO | 2019-02-26 13:00 | COMPLETED |  | 2019-02-26 10:10 | 2019-02-26 22:17 | 2019-02-26 22:20 | -121.335 | 41.922
5L82 | 1939582 | CPCC | CPCC1269354 | PP | CA | TULELAKE | TULELAKE | TR_155900_1890035607 | 2019 | After | 2019-02-26 16:02 | 2019-02-26 19:55 | 1 | 233.65 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Tree through service | DISTRIBUTION | CUSTOMER | MANUAL | 2019-02-26 21:00 | COMPLETED |  | 2019-02-26 16:02 | 2019-02-26 22:27 | 2019-02-26 22:30 | -121.3887 | 41.9219
5L82 | 1939548 | CPCC | CPCC1268616 | PP | CA | TULELAKE | TULELAKE | TR_155900_1890035607 | 2019 | After | 2019-02-26 08:21 | 2019-02-26 11:57 | 1 | 215.533 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: | DISTRIBUTION | CUSTOMER | MANUAL | 2019-02-26 15:45 | COMPLETED |  | 2019-02-26 08:22 | 2019-02-26 22:15 | 2019-02-26 22:20 | -121.3887 | 41.9219
5L82 | 1939560 | CPCC | CPCC1268718 | PP | CA | TULELAKE | TULELAKE | TR_135900_1890037746 | 2019 | After | 2019-02-26 09:59 | 2019-02-26 12:28 | 1 | 148.467 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2019-02-26 13:00 | COMPLETED |  | 2019-02-26 10:00 | 2019-02-26 22:17 | 2019-02-26 22:20 | -121.349 | 41.922
5L82 | 1939565 | CPCC | CPCC1268733 | PP | CA | TULELAKE | TULELAKE | TR_134700_1890037516 | 2019 | After | 2019-02-26 10:20 | 2019-02-26 12:28 | 1 | 128.3 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2019-02-26 13:30 | COMPLETED |  | 2019-02-26 10:20 | 2019-02-26 22:18 | 2019-02-26 22:20 | -121.35 | 41.9185
5P23 | 621360 | CPCC | CPCC423151 | PP | OR | PORTLAND | ALDERWOOD 115/12.5 | TR_169202_8830316 | 2007 | Before | 2007-06-21 15:46 | 2007-06-21 18:41 | 1 | 175.85 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VANDALISM OR THEFT |  |  | SECONDARY CABLE UG |  |  |  | PROSPER: Appears someone trying to steal neutral.repaired secondary hot leg and neutral also conduit | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5P23 | 641376 | ORSD | ORSD486370 | PP | OR | PORTLAND | ALDERWOOD 115/12.5 |  | 2007 | Before | 2007-06-17 20:08 | 2007-06-17 20:12 | 0 | 0 | 88 | 352 | 1 | Y | Y | Y | N | N |  | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  |  | 375 |  |  |  | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5P23 | 680716 | CPCC | CPCC507776 | PP | OR | PORTLAND | ALDERWOOD 115/12.5 | ADW_CB5P23 | 2008 | Before | 2008-06-25 14:35 | 2008-06-25 14:35 | 0 | 0 | 87 | 7.25 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: T&R | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -122.5583 | 45.5673
5P23 | 680717 | CPCC | CPCC507777 | PP | OR | PORTLAND | ALDERWOOD 115/12.5 | ADW_CB5P23 | 2008 | Before | 2008-06-25 14:35 | 2008-06-25 15:30 | 87 | 4721.2 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: plumbing company has unloaded a back hoe and it has hit the guy wire. He requests that we try, trouble clear. Closed CB 5P23. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -122.5583 | 45.5673
5P23 | 724543 | CPCC | CPCC577637 | PP | OR | PORTLAND | ALDERWOOD 115/12.5 | TR_093180_927140368 | 2009 | Before | 2009-07-27 16:25 | 2009-07-27 18:05 | 2 | 200.9 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | OVERLOAD |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Per serviceman: Blown bayonet fuses in padmount x-fmr due to overload. Serviceman replaced fuses and fuses held. Customer back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5P23 | 713532 | CPCC | CPCC559363 | PP | OR | PORTLAND | ALDERWOOD 115/12.5 | ADW_CB5P23 | 2009 | Before | 2009-04-03 12:51 | 2009-04-03 12:51 | 0 | 0 | 91 | 7.583 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: T & R | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -122.5583 | 45.5673
5P23 | 844461 | CPCC | CPCC717951 | PP | OR | PORTLAND | ALDERWOOD 115/12.5 | Line Cut-51359 | 2011 | Before | 2011-08-19 10:49 | 2011-08-20 00:32 | 1 | 822.433 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: Blown dip fuses due to B/O ug primary. Crew to make repairs. This was orginally called in on non-customer call# 1718957. See that call for swerviceman response times. Repairs complete | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -122.5573 | 45.5669
5P23 | 844255 | CPCC | CPCC717836 | PP | OR | PORTLAND | ALDERWOOD 115/12.5 | ADW_CB5P23 | 2011 | Before | 2011-08-19 09:39 | 2011-08-19 09:39 | 0 | 0 | 96 | 8 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: T&R due to b/o ug primary. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -122.5583 | 45.5673
5P23 | 841178 | CPCC | CPCC717545 | PP | OR | PORTLAND | ALDERWOOD 115/12.5 | ADW_CB5P23 | 2011 | Before | 2011-08-17 12:26 | 2011-08-17 12:26 | 0 | 0 | 114 | 9.5 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: feeder operation | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -122.5583 | 45.5673
5W150 | 602357 | CPCC | CPCC399924 | PP | WA | WALLA WALLA | BOWMAN | TR_062980_20410472 | 2007 | Before | 2007-02-18 08:49 | 2007-02-18 14:20 | 1 | 330.483 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | LOAD BREAK ELBOW UG |  |  |  | PROSPER: bad order underground | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 599984 | CPCC | CPCC393745 | PP | WA | WALLA WALLA | BOWMAN | TR_231000_593050156 | 2007 | Before | 2007-01-11 19:15 | 2007-01-11 20:41 | 1 | 86.15 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Squirell caused outage. Refused transformer | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 621269 | CPCC | CPCC421757 | PP | WA | WALLA WALLA | BOWMAN | TR_229000_593050279 | 2007 | Before | 2007-06-12 08:57 | 2007-06-12 14:49 | 1 | 352.55 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | POLE OH |  |  |  | PROSPER: Associate to outage# 421758. B/O connectivity in cadops, mapping change made. Crew is enroute to change out a pole# 230100. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 621270 | CPCC | CPCC421758 | PP | WA | WALLA WALLA | BOWMAN | OH_239260_593050183 | 2007 | Before | 2007-06-12 08:53 | 2007-06-12 10:12 | 38 | 2997.567 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | POLE OH |  |  |  | PROSPER: Associate to outage# 421766. Serviceman did not know the tapline fuse was open at pole# 239260. Pole fire was isolated and these customers are back in full service. Crew is enroute to change out pole# 230100. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.3905 | 46.0678
5W150 | 622039 | CPCC | CPCC421523 | PP | WA | WALLA WALLA | BOWMAN | TR_329804_1540031592 | 2007 | Before | 2007-06-10 09:28 | 2007-06-10 10:44 | 1 | 75.7 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Starling into uncovered conductor on top of service transformers, chenged out to covered wire. No more starling problems. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 622486 | CPCC | CPCC423481 | PP | WA | WALLA WALLA | BOWMAN | TR_344600_636330463 | 2007 | Before | 2007-06-25 07:56 | 2007-06-25 09:11 | 2 | 149.067 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 344600 and it held, the cause was a starling, Customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 620973 | CPCC | CPCC421390 | PP | WA | WALLA WALLA | BOWMAN | TR_329800_636330255 | 2007 | Before | 2007-06-08 14:55 | 2007-06-08 17:08 | 1 | 132.917 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | LIGHTNING ARRESTER OH |  |  |  | PROSPER: Crew replacing lightning arrestors. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 621359 | CPCC | CPCC423150 | PP | WA | WALLA WALLA | BOWMAN | TR_329800_636330255 | 2007 | Before | 2007-06-21 15:36 | 2007-06-21 16:35 | 1 | 59.167 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 329700 and it held, the cause was a starling, Pump is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 618231 | CPCC | CPCC419795 | PP | WA | WALLA WALLA | BOWMAN | TR_293200_1540151840 | 2007 | Before | 2007-05-29 12:19 | 2007-05-29 14:26 | 1 | 127.55 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: svcman reports he replaced a blown trf cutout fuse and customer is back in full service. cause is unknown. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 621822 | CPCC | CPCC422170 | PP | WA | WALLA WALLA | BOWMAN | TR_362602_1540370063 | 2007 | Before | 2007-06-14 18:59 | 2007-06-14 20:33 | 1 | 93.9 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD NEST (BMTS) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Appears that Osprey are attempting to construct a nest at this site, will have to make remedial repairs. Serviceman will submit a BTMS report. Pump has been refused and currently holding. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 618680 | CPCC | CPCC422728 | PP | WA | WALLA WALLA | BOWMAN | OH_265961_1540117656 | 2007 | Before | 2007-06-19 06:51 | 2007-06-19 07:19 | 23 | 634.8 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused the transformer fuse and the tapline fuse at pole# 265961 and they both held, the cause was a squirrel. Customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.3979 | 46.0628
5W150 | 621526 | CPCC | CPCC421766 | PP | WA | WALLA WALLA | BOWMAN | LINECUT-23613 | 2007 | Before | 2007-06-12 08:45 | 2007-06-12 14:49 | 3 | 1093.5 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | POLE OH |  |  |  | PROSPER: Associate to outage# 421758. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.4082 | 46.0652
5W150 | 621545 | CPCC | CPCC422012 | PP | WA | WALLA WALLA | BOWMAN | TR_251105_209420364 | 2007 | Before | 2007-06-14 07:10 | 2007-06-14 08:05 | 11 | 603.167 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 251105 and it held, the cause was a squirrel, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 615674 | CPCC | CPCC417653 | PP | WA | WALLA WALLA | BOWMAN | TR_263480_302080345 | 2007 | Before | 2007-05-13 16:04 | 2007-05-13 19:15 | 1 | 190.833 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTORS UG |  |  |  | PROSPER: Bad connections in pad mount. Crew enroute. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 616956 | CPCC | CPCC416675 | PP | WA | WALLA WALLA | BOWMAN | OH_252100_209420349 | 2007 | Before | 2007-05-05 10:11 | 2007-05-05 16:14 | 28 | 9366 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: Found bad section of underground, repaired same. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.3844 | 46.0508
5W150 | 616590 | CPCC | CPCC419327 | PP | WA | WALLA WALLA | BOWMAN | TR_261102_302080323 | 2007 | Before | 2007-05-25 09:30 | 2007-05-25 10:07 | 2 | 72.267 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer on pole# 261102 and it held, the cause was a squirrel, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 614649 | CPCC | CPCC418031 | PP | WA | WALLA WALLA | BOWMAN | TR_269101_302080406 | 2007 | Before | 2007-05-17 10:34 | 2007-05-17 11:38 | 1 | 63.617 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: svcman replaced connections at the weatherhead. he told the customer if she has further problems to contact an electricain. customer back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 617521 | CPCC | CPCC416993 | PP | WA | WALLA WALLA | BOWMAN | TR_263402_302080346 | 2007 | Before | 2007-05-08 13:31 | 2007-05-08 14:16 | 1 | 44.533 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: Serviceman changed out a B/O connection at the weatherhead, customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 615112 | CPCC | CPCC417229 | PP | WA | WALLA WALLA | BOWMAN | TR_230100_593050161 | 2007 | Before | 2007-05-09 13:41 | 2007-05-09 15:00 | 1 | 78.2 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: bad connections | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 617139 | CPCC | CPCC419449 | PP | WA | WALLA WALLA | BOWMAN | TR_364701_649900145 | 2007 | Before | 2007-05-27 07:07 | 2007-05-27 08:35 | 1 | 88 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman found tree in line removed same. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 627257 | CPCC | CPCC430843 | PP | WA | WALLA WALLA | BOWMAN | TR_251105_209420364 | 2007 | Before | 2007-07-20 06:29 | 2007-07-20 07:07 | 11 | 417.633 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Squirrel blew transformer fuse. Refused and customer is back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 630399 | CPCC | CPCC428603 | PP | WA | WALLA WALLA | BOWMAN | TR_289200_636330428 | 2007 | Before | 2007-07-13 10:18 | 2007-07-13 11:29 | 4 | 284.2 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: squirrel caused the trf cutout fuse to blow. squirrel cleared, trf cutout fuse replaced and customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 605742 | CPCC | CPCC409076 | PP | WA | WALLA WALLA | BOWMAN | TR_278180_636330308 | 2007 | Before | 2007-03-01 17:28 | 2007-03-01 18:44 | 1 | 75.983 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: squirrel | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 607416 | CPCC | CPCC410546 | PP | WA | WALLA WALLA | BOWMAN | TR_262901_302080299 | 2007 | Before | 2007-03-17 07:36 | 2007-03-17 09:56 | 3 | 419.9 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: refuse transformer fuse; squirrrel | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 609059 | CPCC | CPCC411230 | PP | WA | WALLA WALLA | BOWMAN | TR_250800_209420295 | 2007 | Before | 2007-03-22 13:42 | 2007-03-22 14:56 | 1 | 73.35 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: svcman replaced b/o secondary connectors that caused service wire to burn down. customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 648104 | CPCC | CPCC452031 | PP | WA | WALLA WALLA | BOWMAN | TR_247300_593050277 | 2007 | Before | 2007-11-06 15:54 | 2007-11-06 16:30 | 1 | 36.267 | 0 | 0 | 1 | Y | N | Y | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Associate to outage# 452023. the cause is unknown | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 648105 | CPCC | CPCC452032 | PP | WA | WALLA WALLA | BOWMAN | TR_360800_456710520 | 2007 | Before | 2007-11-06 16:04 | 2007-11-06 16:36 | 1 | 32.283 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Associate to outage# 452023. the cause is unknwon. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 644943 | CPCC | CPCC445980 | PP | WA | WALLA WALLA | BOWMAN | TR_323900_636330388 | 2007 | Before | 2007-10-10 13:39 | 2007-10-10 14:30 | 1 | 51.033 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: svcman replaced a blown trf fuse and the pump is back in full service. cause was a starling. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 647069 | CPCC | CPCC450885 | PP | WA | WALLA WALLA | BOWMAN | TR_264404_302080352 | 2007 | Before | 2007-10-28 14:41 | 2007-10-28 15:26 | 2 | 91.4 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: blown transformer fuse. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 649127 | CPCC | CPCC457888 | PP | WA | WALLA WALLA | BOWMAN | TR_269509_302080231 | 2007 | Before | 2007-11-30 08:37 | 2007-11-30 09:27 | 1 | 50.333 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: Serviceman replaced the B/O secondary connections at the weatherhead, customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 648366 | CPCC | CPCC452034 | PP | WA | WALLA WALLA | BOWMAN | TR_251305_209420386 | 2007 | Before | 2007-11-06 16:10 | 2007-11-06 16:33 | 1 | 23.467 | 0 | 0 | 1 | Y | N | Y | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Associate to outage# 452023. the cause is unknown. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 646791 | CPCC | CPCC450855 | PP | WA | WALLA WALLA | BOWMAN | TR_053600_20410456 | 2007 | Before | 2007-10-28 09:35 | 2007-10-28 10:28 | 1 | 52.183 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Power was part of outage from 5W50 from Prospect point. bad connectivityHold on that circuit, power restored. no cause found | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 649248 | CPCC | CPCC456424 | PP | WA | WALLA WALLA | BOWMAN | OH_360901_456710508 | 2007 | Before | 2007-11-21 14:30 | 2007-11-21 18:53 | 17 | 4380.617 | 0 | 0 | 2 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | TERMINATION UG |  |  |  | PROSPER: Potheads blown due to squirrel | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.3872 | 46.0491
5W150 | 642895 | CPCC | CPCC443554 | PP | WA | WALLA WALLA | BOWMAN | TR_243200_593050252 | 2007 | Before | 2007-09-25 09:34 | 2007-09-25 11:10 | 4 | 386.667 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | PROSPER: Serviceman refused transformer# 243200 and it held, the cause was a squirrel, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 638809 | CPCC | CPCC437471 | PP | WA | WALLA WALLA | BOWMAN | TR_314001_636330364 | 2007 | Before | 2007-08-29 17:34 | 2007-08-29 21:40 | 1 | 246.8 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | PROSPER: Found bad order transformer, need 3 man crew to replace. Replaced transformer and customers are back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 643382 | CPCC | CPCC442780 | PP | WA | WALLA WALLA | BOWMAN | TR_277502_1050461559 | 2007 | Before | 2007-09-20 12:04 | 2007-09-20 13:10 | 1 | 65.483 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: Serviceman replaced a B/O secondary connector at the customers secondary pole, customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 637800 | CPCC | CPCC440624 | PP | WA | WALLA WALLA | BOWMAN | TR_268100_1540196545 | 2007 | Before | 2007-09-02 10:26 | 2007-09-02 11:46 | 7 | 562.217 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: squirrel, replaced transformer fuse | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 656442 | CPCC | CPCC465373 | PP | WA | WALLA WALLA | BOWMAN | TR_251802_209420292 | 2007 | Before | 2007-12-09 13:40 | 2007-12-09 13:58 | 5 | 88.5 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: hold on feeder bad UG outage # 465341 bad ug primary | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 652209 | CPCC | CPCC459431 | PP | WA | WALLA WALLA | BOWMAN | TR_041900_20410239 | 2007 | Before | 2007-12-02 14:08 | 2007-12-02 20:37 | 1 | 389 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: Crew needed to make repairs to the B/O underground primary cable. Customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 656486 | CPCC | CPCC472493 | PP | WA | WALLA WALLA | BOWMAN | TR_267508_302080235 | 2008 | Before | 2008-01-04 11:21 | 2008-01-06 13:04 | 1 | 2982.55 | 0 | 0 | 1 | Y | N | N | N | Y | 706 - 2008-01-04 to 2008-01-05 WA Walla Walla | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: outbound calling | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 655640 | CPCC | CPCC472179 | PP | WA | WALLA WALLA | BOWMAN | TR_250401_302080369 | 2008 | Before | 2008-01-04 10:16 | 2008-01-06 13:02 | 5 | 15229.417 | 0 | 0 | 1 | Y | N | N | N | Y | 706 - 2008-01-04 to 2008-01-05 WA Walla Walla | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: outbound calling | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 655649 | CPCC | CPCC472236 | PP | WA | WALLA WALLA | BOWMAN | TR_194305_825860500 | 2008 | Before | 2008-01-04 10:26 | 2008-01-06 13:02 | 15 | 45543 | 0 | 0 | 1 | Y | N | N | N | Y | 706 - 2008-01-04 to 2008-01-05 WA Walla Walla | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: outbound calling | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 655654 | CPCC | CPCC472268 | PP | WA | WALLA WALLA | BOWMAN | TR_315761_636330337 | 2008 | Before | 2008-01-04 10:32 | 2008-01-06 13:02 | 1 | 3030.383 | 0 | 0 | 1 | Y | N | N | N | Y | 706 - 2008-01-04 to 2008-01-05 WA Walla Walla | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: outbound calling | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 651897 | CPCC | CPCC456422 | PP | WA | WALLA WALLA | BOWMAN | TR_360800_456710520 | 2007 | Before | 2007-11-21 14:24 | 2007-11-21 18:50 | 1 | 265.967 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | FREEZING FOG & FROST |  |  | TERMINATION UG |  |  |  | PROSPER: Pot heads went bad from tracking | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 654945 | CPCC | CPCC467226 | PP | WA | WALLA WALLA | BOWMAN | TR_247300_593050277 | 2007 | Before | 2007-12-20 13:14 | 2007-12-20 13:21 | 1 | 7.567 | 0 | 0 | 1 | Y | N | Y | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Associate to the earlier breaker outage caused from an unknown cause, there was a saftey hold on the breaker. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 655360 | CPCC | CPCC472073 | PP | WA | WALLA WALLA | BOWMAN | TR_311180_636330277 | 2008 | Before | 2008-01-04 10:06 | 2008-01-06 13:02 | 1 | 3056.35 | 0 | 0 | 1 | Y | N | N | N | Y | 706 - 2008-01-04 to 2008-01-05 WA Walla Walla | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: outbound calling | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 655365 | CPCC | CPCC472090 | PP | WA | WALLA WALLA | BOWMAN | TR_267901_302080270 | 2008 | Before | 2008-01-04 10:07 | 2008-01-06 13:02 | 1 | 3055.35 | 0 | 0 | 1 | Y | N | N | N | Y | 706 - 2008-01-04 to 2008-01-05 WA Walla Walla | WEATHER | WIND |  |  | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | PROSPER: outbound calling | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 655367 | CPCC | CPCC472101 | PP | WA | WALLA WALLA | BOWMAN | TR_050803_20410459 | 2008 | Before | 2008-01-04 10:09 | 2008-01-06 13:02 | 1 | 3053.617 | 0 | 0 | 1 | Y | N | N | N | Y | 706 - 2008-01-04 to 2008-01-05 WA Walla Walla | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: outbound calling | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 655369 | CPCC | CPCC472120 | PP | WA | WALLA WALLA | BOWMAN | TR_367000_649900176 | 2008 | Before | 2008-01-04 10:10 | 2008-01-06 13:02 | 1 | 3052.35 | 0 | 0 | 1 | Y | N | N | N | Y | 706 - 2008-01-04 to 2008-01-05 WA Walla Walla | WEATHER | WIND |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: outbound calling | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 656243 | CPCC | CPCC473304 | PP | WA | WALLA WALLA | BOWMAN | TR_340500_636330468 | 2008 | Before | 2008-01-04 17:10 | 2008-01-06 13:10 | 1 | 2639.367 | 0 | 0 | 1 | Y | N | N | N | Y | 706 - 2008-01-04 to 2008-01-05 WA Walla Walla | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: outbound calling | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 656708 | CPCC | CPCC465374 | PP | WA | WALLA WALLA | BOWMAN | TR_361800_456710500 | 2007 | Before | 2007-12-09 13:41 | 2007-12-09 14:06 | 8 | 194.8 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: hold on feeder bad UG outage # 465341 bad ug primary | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 656709 | CPCC | CPCC465377 | PP | WA | WALLA WALLA | BOWMAN | TR_264161_302080351 | 2007 | Before | 2007-12-09 13:30 | 2007-12-09 14:06 | 4 | 146.333 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: hold on feeder bad UG outage # 465341 bad ug primary | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 656710 | CPCC | CPCC465379 | PP | WA | WALLA WALLA | BOWMAN | TR_334000_636330448 | 2007 | Before | 2007-12-09 13:33 | 2007-12-09 14:07 | 1 | 34.033 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: hold on feeder bad UG outage # 465341 bad ug primary | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 653770 | CPCC | CPCC465341 | PP | WA | WALLA WALLA | BOWMAN | BOW_CB5W150 | 2007 | Before | 2007-12-09 13:11 | 2007-12-09 18:27 | 1762 | 42549.533 | 0 | 0 | 2 | Y | N | Y | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER PADMOUNT/SUBMERSIBLE UG |  |  |  | PROSPER: crew had hot line hold on circuit Bad primary underground transformer | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.3614 | 46.0679
5W150 | 652500 | CPCC | CPCC459729 | PP | WA | WALLA WALLA | BOWMAN | TR_329080_636330405 | 2007 | Before | 2007-12-02 14:08 | 2007-12-02 20:38 | 2 | 780.833 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: Crew made repairs to the underground primary cable. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 656768 | CPCC | CPCC472621 | PP | WA | WALLA WALLA | BOWMAN | OH_289300_636330233 | 2008 | Before | 2008-01-04 11:58 | 2008-01-06 15:49 | 16 | 48629.033 | 0 | 0 | 2 | Y | N | N | N | Y | 706 - 2008-01-04 to 2008-01-05 WA Walla Walla | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.43 | 46.0536
5W150 | 656770 | CPCC | CPCC472642 | PP | WA | WALLA WALLA | BOWMAN | TR_310880_1540815303 | 2008 | Before | 2008-01-04 12:03 | 2008-01-06 13:20 | 1 | 2957.15 | 0 | 0 | 1 | Y | N | N | N | Y | 706 - 2008-01-04 to 2008-01-05 WA Walla Walla | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: outbound calling | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 655081 | CPCC | CPCC471980 | PP | WA | WALLA WALLA | BOWMAN | OH_277101_636330275 | 2008 | Before | 2008-01-04 09:05 | 2008-01-06 13:40 | 44 | 138808.267 | 0 | 0 | 1 | Y | N | N | N | Y | 706 - 2008-01-04 to 2008-01-05 WA Walla Walla | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.4141 | 46.0519
5W150 | 655085 | CPCC | CPCC471998 | PP | WA | WALLA WALLA | BOWMAN | TR_310603_636330354 | 2008 | Before | 2008-01-04 09:55 | 2008-01-06 13:02 | 4 | 12271.2 | 0 | 0 | 1 | Y | N | N | N | Y | 706 - 2008-01-04 to 2008-01-05 WA Walla Walla | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: outbound calling | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 655086 | CPCC | CPCC472021 | PP | WA | WALLA WALLA | BOWMAN | TR_250200_302080373 | 2008 | Before | 2008-01-04 09:59 | 2008-01-06 12:01 | 1 | 3001.917 | 0 | 0 | 1 | Y | N | N | N | Y | 706 - 2008-01-04 to 2008-01-05 WA Walla Walla | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 655088 | CPCC | CPCC472044 | PP | WA | WALLA WALLA | BOWMAN | TR_250103_302080377 | 2008 | Before | 2008-01-04 10:01 | 2008-01-06 13:02 | 1 | 3060.9 | 0 | 0 | 1 | Y | N | N | N | Y | 706 - 2008-01-04 to 2008-01-05 WA Walla Walla | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: outbound calling | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 655091 | CPCC | CPCC472049 | PP | WA | WALLA WALLA | BOWMAN | OH_250303_302080360 | 2008 | Before | 2008-01-04 10:03 | 2008-01-06 12:04 | 42 | 126021.7 | 0 | 0 | 1 | Y | N | N | N | Y | 706 - 2008-01-04 to 2008-01-05 WA Walla Walla | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.3885 | 46.0537
5W150 | 655919 | CPCC | CPCC472287 | PP | WA | WALLA WALLA | BOWMAN | TR_250210_209420383 | 2008 | Before | 2008-01-04 10:26 | 2008-01-06 13:02 | 1 | 3036.067 | 0 | 0 | 1 | Y | N | N | N | Y | 706 - 2008-01-04 to 2008-01-05 WA Walla Walla | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: outbound calling | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 655923 | CPCC | CPCC472323 | PP | WA | WALLA WALLA | BOWMAN | TR_268701_302080244 | 2008 | Before | 2008-01-04 10:41 | 2008-01-06 13:02 | 1 | 3021.167 | 0 | 0 | 1 | Y | N | N | N | Y | 706 - 2008-01-04 to 2008-01-05 WA Walla Walla | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: outbound calling | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 655928 | CPCC | CPCC472340 | PP | WA | WALLA WALLA | BOWMAN | TR_250201_302080374 | 2008 | Before | 2008-01-04 10:43 | 2008-01-06 13:18 | 1 | 3035.483 | 0 | 0 | 1 | Y | N | N | N | Y | 706 - 2008-01-04 to 2008-01-05 WA Walla Walla | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 655931 | CPCC | CPCC472352 | PP | WA | WALLA WALLA | BOWMAN | OH_239260_593050183 | 2008 | Before | 2008-01-04 10:01 | 2008-01-06 13:26 | 83 | 81141.85 | 0 | 0 | 2 | Y | N | N | N | Y | 706 - 2008-01-04 to 2008-01-05 WA Walla Walla | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: outbound calling | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.3905 | 46.0678
5W150 | 653433 | CPCC | CPCC473164 | PP | WA | WALLA WALLA | BOWMAN | TR_250300_302080371 | 2008 | Before | 2008-01-04 16:19 | 2008-01-06 13:09 | 1 | 2690.65 | 0 | 0 | 1 | Y | N | N | N | Y | 706 - 2008-01-04 to 2008-01-05 WA Walla Walla | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: outbound calling | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 634175 | CPCC | CPCC436245 | PP | WA | WALLA WALLA | BOWMAN | OH_310861_636330350 | 2007 | Before | 2007-08-20 16:30 | 2007-08-21 01:10 | 47 | 24432.95 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | POLE OH |  |  |  | PROSPER: Crew enroute to change out pole# 310861 that caught fire. Changed pole out and customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.4908 | 46.0466
5W150 | 634178 | CPCC | CPCC436252 | PP | WA | WALLA WALLA | BOWMAN | TR_050803_20410459 | 2007 | Before | 2007-08-20 17:31 | 2007-08-21 01:10 | 7 | 3216.15 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | POLE OH |  |  |  | PROSPER: Associated with outage 436245. Bad connectivity in CADOPS. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 634181 | CPCC | CPCC436262 | PP | WA | WALLA WALLA | BOWMAN | TR_054880_20410455 | 2007 | Before | 2007-08-20 18:37 | 2007-08-21 01:10 | 1 | 393.367 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | POLE OH |  |  |  | PROSPER: Associated with outage 436245. Bad connectivity in CADOPS. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 636477 | CPCC | CPCC439094 | PP | WA | WALLA WALLA | BOWMAN | TR_266100_302080193 | 2007 | Before | 2007-08-31 19:38 | 2007-08-31 20:18 | 2 | 79.067 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer bank on pole# 266100 and it held, the cause was lightning, Pump is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 634885 | CPCC | CPCC434670 | PP | WA | WALLA WALLA | BOWMAN | TR_280200_636330407 | 2007 | Before | 2007-08-11 20:58 | 2007-08-12 00:40 | 1 | 222.083 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: Found 2 blown cutouts, need 2 more journeymen to make repairs. Weimer & Saffer called to assist. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 635771 | CPCC | CPCC435504 | PP | WA | WALLA WALLA | BOWMAN | TR_263600_302080283 | 2007 | Before | 2007-08-16 09:20 | 2007-08-16 11:39 | 1 | 139 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused transformer# 276201 and it held, the cause is unknown, pump is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 636188 | CPCC | CPCC438862 | PP | WA | WALLA WALLA | BOWMAN | OH_269100_302080365 | 2007 | Before | 2007-08-31 17:04 | 2007-08-31 19:24 | 87 | 12119.1 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused the tapline fuses on pole# 269100 and it held, the cause was the lightning storm, customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.3889 | 46.0516
5W150 | 675747 | CPCC | CPCC505138 | PP | WA | WALLA WALLA | BOWMAN | TR_261102_302080323 | 2008 | Before | 2008-06-06 12:09 | 2008-06-06 12:59 | 2 | 98.267 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Refused transformer due to squirrel. All power restored | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 676176 | CPCC | CPCC501886 | PP | WA | WALLA WALLA | BOWMAN | TR_282100_636330415 | 2008 | Before | 2008-05-15 20:28 | 2008-05-15 21:20 | 1 | 51.917 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: Associated to outage 501893. Bad connectivity in CADOPS. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 676177 | CPCC | CPCC501887 | PP | WA | WALLA WALLA | BOWMAN | TR_329080_636330405 | 2008 | Before | 2008-05-15 20:27 | 2008-05-15 21:20 | 1 | 53.25 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: Associated to outage 501893. Bad connectivity in CADOPS. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 676178 | CPCC | CPCC501888 | PP | WA | WALLA WALLA | BOWMAN | TR_348800_636330459 | 2008 | Before | 2008-05-15 20:37 | 2008-05-15 21:20 | 1 | 43.033 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: Associated to outage 501893. Bad connectivity in CADOPS. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 673411 | CPCC | CPCC496783 | PP | WA | WALLA WALLA | BOWMAN | OH_239305_593050178 | 2008 | Before | 2008-04-19 08:26 | 2008-04-19 09:25 | 31 | 1844.5 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: FP 239305 center & roadside phase fuses open 140T's. Patrolled found nothing. Refused, holding. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.3887 | 46.0683
5W150 | 671430 | CPCC | CPCC501294 | PP | WA | WALLA WALLA | BOWMAN | OH_364901_649900155 | 2008 | Before | 2008-05-14 05:41 | 2008-05-14 08:17 | 22 | 3428.333 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD SUSPECTED, NO MORTALITY |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: Blown fuse, cutouts need to be replaced. Crew to install inew cutouts, cross arm cause ins unknown. Found no visible signs of bird. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.5046 | 46.0478
5W150 | 673062 | CPCC | CPCC501189 | PP | WA | WALLA WALLA | BOWMAN | OH_294161_636330486 | 2008 | Before | 2008-05-13 01:14 | 2008-05-13 05:33 | 7 | 1810.783 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused the tapline fuse at pole# 294161 and it held, the cause is unknown, cutomers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.4615 | 46.051
5W150 | 674674 | CPCC | CPCC499287 | PP | WA | WALLA WALLA | BOWMAN | Line Cut-28987 | 2008 | Before | 2008-05-09 10:18 | 2008-05-09 13:00 | 3 | 483.9 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused the tapline fuse at pole# 358800 and it held, the cause is unknown, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.5153 | 46.047
5W150 | 675429 | CPCC | CPCC498962 | PP | WA | WALLA WALLA | BOWMAN | TR_251105_209420364 | 2008 | Before | 2008-05-06 07:47 | 2008-05-06 08:44 | 11 | 622.233 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 251105 and it held, the cause was a squirrel, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 675169 | CPCC | CPCC498950 | PP | WA | WALLA WALLA | BOWMAN | OH_364901_649900155 | 2008 | Before | 2008-05-06 00:32 | 2008-05-06 02:38 | 21 | 2639.35 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (PROTECTED SPECIES) (BMTS) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Blown line fuse. Serviceman patrolling. Goose on line. Refused and customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.5046 | 46.0478
5W150 | 673219 | CPCC | CPCC498810 | PP | WA | WALLA WALLA | BOWMAN | OH_364901_649900155 | 2008 | Before | 2008-05-03 22:07 | 2008-05-04 00:15 | 21 | 2704.45 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: 2 blown line fuses. Serviceman is patrolling. No cause found. Refused and customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.5046 | 46.0478
5W150 | 672445 | CPCC | CPCC499135 | PP | WA | WALLA WALLA | BOWMAN | TR_268102_302080410 | 2008 | Before | 2008-05-07 22:37 | 2008-05-08 03:46 | 1 | 309.317 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | PROSPER: replaced transformer | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 676033 | CPCC | CPCC505187 | PP | WA | WALLA WALLA | BOWMAN | OH_289300_636330233 | 2008 | Before | 2008-06-07 04:30 | 2008-06-07 06:19 | 13 | 1420.467 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Blown line fuse, Patrolled line and found a section of primary that was hanging a little low in a field. Believes that a Combine might hit it. Refused and customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.43 | 46.0536
5W150 | 676441 | CPCC | CPCC501889 | PP | WA | WALLA WALLA | BOWMAN | TR_329900_636330450 | 2008 | Before | 2008-05-15 20:46 | 2008-05-15 21:20 | 1 | 33.717 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: Associated to outage 501893. Bad connectivity in CADOPS. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 676442 | CPCC | CPCC501890 | PP | WA | WALLA WALLA | BOWMAN | TR_330200_636330457 | 2008 | Before | 2008-05-15 20:53 | 2008-05-15 21:20 | 1 | 27.033 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: Associated to outage 501893. Bad connectivity in CADOPS. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 676444 | CPCC | CPCC501892 | PP | WA | WALLA WALLA | BOWMAN | TR_334000_636330448 | 2008 | Before | 2008-05-15 21:06 | 2008-05-15 21:20 | 1 | 14.167 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: Associated to outage 501893. Bad connectivity in CADOPS. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 676445 | CPCC | CPCC501893 | PP | WA | WALLA WALLA | BOWMAN | OH_280360_636330418 | 2008 | Before | 2008-05-15 21:16 | 2008-05-15 21:21 | 0 | 0 | 30 | 142 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: Stirrup burnt in the clear. Openend line fuse and made repairs and customers are back on. Arrival times are on outage 501886. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.4506 | 46.0541
5W150 | 674913 | CPCC | CPCC499149 | PP | WA | WALLA WALLA | BOWMAN | OH_364901_649900155 | 2008 | Before | 2008-05-08 09:18 | 2008-05-08 11:34 | 14 | 1912.633 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused the tapline fuse on pole# 364901 and it held, the cause is unknown, customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.5046 | 46.0478
5W150 | 674917 | CPCC | CPCC499155 | PP | WA | WALLA WALLA | BOWMAN | TR_361302_649900179 | 2008 | Before | 2008-05-08 09:35 | 2008-05-08 11:35 | 1 | 119.883 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Associate to outage# 499149. Serviceman refused the tapline fuse on pole# 364901 and it held, the cause is unknown, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 673765 | CPCC | CPCC498444 | PP | WA | WALLA WALLA | BOWMAN | OH_364901_649900155 | 2008 | Before | 2008-04-30 08:51 | 2008-04-30 12:12 | 14 | 2817.267 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (PROTECTED SPECIES) (BMTS) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused the B phase tapline fuse at pole# 364901 and it held, the cuase was a red tailed Hawk that was hard to find but the bird was located at pole# 364705, customers are back in full service. The hawk was buried at the scene. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.5046 | 46.0478
5W150 | 666489 | CPCC | CPCC488848 | PP | WA | WALLA WALLA | BOWMAN | OH_245301_593050274 | 2008 | Before | 2008-02-13 12:19 | 2008-02-13 15:47 | 26 | 1286.5 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | PROSPER: crew needed to change out transformer. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.3781 | 46.0687
5W150 | 669074 | CPCC | CPCC491832 | PP | WA | WALLA WALLA | BOWMAN | RC_263404_1540836522 | 2008 | Before | 2008-03-10 15:37 | 2008-03-10 17:20 | 432 | 44719.2 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | PROSPER: Serviceman reports patrol found nothing. No targets on field recloser 5W697. Gave ok to close on test. 14:24 reports test was bad B&C phase target. Will continue patrol. Recloser is bad order, Field recloser is bypassed with 100T's. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.4026 | 46.0564
5W150 | 669488 | CPCC | CPCC494412 | PP | WA | WALLA WALLA | BOWMAN | TR_277000_649900239 | 2008 | Before | 2008-03-31 15:13 | 2008-03-31 16:18 | 2 | 129.433 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused the transformer on pole# 277000 and it held, the cause was a B/O fuse, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 668463 | CPCC | CPCC490614 | PP | WA | WALLA WALLA | BOWMAN | OH_245301_593050274 | 2008 | Before | 2008-03-02 11:51 | 2008-03-02 12:27 | 27 | 973.8 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Line fuse blown, serviceman is patrolling. No cause found. Refused and customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.3781 | 46.0687
5W150 | 679411 | CPCC | CPCC505551 | PP | WA | WALLA WALLA | BOWMAN | TR_261404_302080307 | 2008 | Before | 2008-06-10 05:42 | 2008-06-10 06:40 | 1 | 58.083 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Transformer fuse is open. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 679824 | CPCC | CPCC503184 | PP | WA | WALLA WALLA | BOWMAN | OH_294161_636330486 | 2008 | Before | 2008-05-23 03:31 | 2008-05-23 03:33 | 0 | 0 | 5 | 10.167 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.4615 | 46.051
5W150 | 681866 | CPCC | CPCC509481 | PP | WA | WALLA WALLA | BOWMAN | TR_344600_636330463 | 2008 | Before | 2008-06-30 07:15 | 2008-06-30 09:21 | 1 | 125.9 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: Serviceman replaced the B/O secondary connections at the weatherhead, customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 677397 | CPCC | CPCC504962 | PP | WA | WALLA WALLA | BOWMAN | OH_320300_636330398 | 2008 | Before | 2008-06-04 21:25 | 2008-06-04 22:21 | 22 | 1222.467 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD SUSPECTED, NO MORTALITY |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.471 | 46.0404
5W150 | 677398 | CPCC | CPCC504963 | PP | WA | WALLA WALLA | BOWMAN | TR_053700_20410457 | 2008 | Before | 2008-06-04 21:38 | 2008-06-04 22:43 | 1 | 65.1 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD SUSPECTED, NO MORTALITY |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 677819 | CPCC | CPCC502512 | PP | WA | WALLA WALLA | BOWMAN | OH_239260_593050183 | 2008 | Before | 2008-05-19 12:01 | 2008-05-19 15:10 | 57 | 3194.916 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | LIGHTNING ARRESTER OH |  |  |  | PROSPER: Found blown lightning arrestor pole # 233100. Found north phase (c phase) blown pole 239 250. Will cut arrestor in the clear and re-fuse @ 140T. 1253 Refused ok up to open dip fuse 233100 | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.3905 | 46.0678
5W150 | 680282 | CPCC | CPCC510477 | PP | WA | WALLA WALLA | BOWMAN | TR_291101_636330485 | 2008 | Before | 2008-07-04 07:42 | 2008-07-04 09:22 | 2 | 198.133 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 291101 and it held, the cause was a starling, pump is back in full service. Serviceman added additional guarding to prevent this from happening again in the future. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 681111 | CPCC | CPCC510595 | PP | WA | WALLA WALLA | BOWMAN | OH_319900_636330342 | 2008 | Before | 2008-07-05 06:16 | 2008-07-05 07:32 | 35 | 2643.083 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | OTHER INTERFERING OBJECT |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Balloons; removed no damage | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.472 | 46.0478
5W150 | 679082 | CPCC | CPCC504978 | PP | WA | WALLA WALLA | BOWMAN | OH_358800_1540858501 | 2008 | Before | 2008-06-05 06:49 | 2008-06-05 07:50 | 3 | 185.05 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused the tapline fuse at pole# 358800 and it held, the cause is unknown, customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.5153 | 46.0469
5W150 | 681943 | CPCC | CPCC510762 | PP | WA | WALLA WALLA | BOWMAN | OH_310861_636330350 | 2008 | Before | 2008-07-06 20:19 | 2008-07-06 22:53 | 23 | 3542.767 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Patroled & Refused at pole 310861 | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.4908 | 46.0466
5W150 | 680789 | CPCC | CPCC510134 | PP | WA | WALLA WALLA | BOWMAN | TR_291101_636330485 | 2008 | Before | 2008-07-02 12:07 | 2008-07-02 13:38 | 2 | 182.033 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Reports 2 blown fuses. Will investigate and refuse if no problem found. Found 2 starlings at base of pole. Refused all power restored. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 679595 | CPCC | CPCC504561 | PP | WA | WALLA WALLA | BOWMAN | OH_294161_636330486 | 2008 | Before | 2008-06-01 10:52 | 2008-06-01 11:47 | 7 | 381.5 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (PROTECTED SPECIES) (BMTS) |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: open line fuses to repair center phase. installed a dozen bird reflectors. will monitor. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.4615 | 46.051
5W150 | 677990 | CPCC | CPCC505261 | PP | WA | WALLA WALLA | BOWMAN | TR_337900_636330432 | 2008 | Before | 2008-06-08 06:20 | 2008-06-08 07:57 | 1 | 97.45 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (PROTECTED SPECIES) (BMTS) |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: white pellican, serviceman is filling out forms, wire down, crew to repair, | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 677991 | CPCC | CPCC505262 | PP | WA | WALLA WALLA | BOWMAN | OH_289200_636330257 | 2008 | Before | 2008-06-08 07:21 | 2008-06-08 12:20 | 10 | 2988.167 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (PROTECTED SPECIES) (BMTS) |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: white pellican, serviceman is filling out forms, wire down, crew to repair, | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.43 | 46.0528
5W150 | 680458 | CPCC | CPCC508154 | PP | WA | WALLA WALLA | BOWMAN | TR_293200_1540151840 | 2008 | Before | 2008-06-28 08:11 | 2008-06-28 11:06 | 1 | 175 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: refuse transformer | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 678426 | CPCC | CPCC503170 | PP | WA | WALLA WALLA | BOWMAN | TR_295002_1540128216 | 2008 | Before | 2008-05-22 23:37 | 2008-05-23 03:33 | 1 | 236.067 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 680070 | CPCC | CPCC506335 | PP | WA | WALLA WALLA | BOWMAN | TR_251105_209420364 | 2008 | Before | 2008-06-17 07:51 | 2008-06-17 08:41 | 11 | 549.267 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: open c/o at pole 735/251105 - due to squirrel | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 679324 | CPCC | CPCC504478 | PP | WA | WALLA WALLA | BOWMAN | OH_320300_636330398 | 2008 | Before | 2008-06-01 03:48 | 2008-06-01 06:33 | 22 | 3582.7 | 0 | 0 | 2 | Y | N | N | N | N |  | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: b/o anchor - replace anchor & repulled guy wire. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.471 | 46.0404
5W150 | 682600 | CPCC | CPCC506742 | PP | WA | WALLA WALLA | BOWMAN | OH_320300_636330398 | 2008 | Before | 2008-06-20 05:20 | 2008-06-20 06:43 | 27 | 2237.85 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Blown line fuse, serviceman patrolling. Fuse melted out, refused and customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.471 | 46.0404
5W150 | 681798 | CPCC | CPCC507680 | PP | WA | WALLA WALLA | BOWMAN | TR_291101_636330485 | 2008 | Before | 2008-06-24 15:25 | 2008-06-24 18:11 | 1 | 165.617 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Blown transformer fuse, no cause found. Refused and customer is back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 681807 | CPCC | CPCC507872 | PP | WA | WALLA WALLA | BOWMAN | TR_291101_636330485 | 2008 | Before | 2008-06-26 14:30 | 2008-06-26 15:42 | 1 | 72.767 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Starling blew transformer fuse. Re fastned bird guard and refused customer is back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 677342 | CPCC | CPCC503784 | PP | WA | WALLA WALLA | BOWMAN | TR_295002_1540128216 | 2008 | Before | 2008-05-25 21:44 | 2008-05-25 23:49 | 1 | 124.783 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: blown fuse no cause found | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 679391 | CPCC | CPCC505371 | PP | WA | WALLA WALLA | BOWMAN | TR_358901_369970318 | 2008 | Before | 2008-06-09 17:21 | 2008-06-09 18:56 | 1 | 94.65 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: limb damage sec nuetral. Made repairs and customers are back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 661610 | CPCC | CPCC474419 | PP | WA | WALLA WALLA | BOWMAN | OH_359902_369970321 | 2008 | Before | 2008-01-04 09:48 | 2008-01-05 21:25 | 101 | 215821.85 | 0 | 0 | 1 | Y | N | N | N | Y | 706 - 2008-01-04 to 2008-01-05 WA Walla Walla | WEATHER | WIND |  |  | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | PROSPER: repair and refuse | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.3892 | 46.0491
5W150 | 657853 | CPCC | CPCC474776 | PP | WA | WALLA WALLA | BOWMAN | TR_319509_636330242 | 2008 | Before | 2008-01-06 09:17 | 2008-01-07 19:08 | 1 | 2030.5 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 659525 | CPCC | CPCC476127 | PP | WA | WALLA WALLA | BOWMAN | TR_192201_825860476 | 2008 | Before | 2008-01-07 08:55 | 2008-01-07 15:50 | 10 | 4146.833 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | CONNECTOR OH |  |  |  | PROSPER: Customer has partial power. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 660360 | CPCC | CPCC476416 | PP | WA | WALLA WALLA | BOWMAN | TR_288201_636330427 | 2008 | Before | 2008-01-07 11:41 | 2008-01-07 17:28 | 1 | 346.683 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 661629 | CPCC | CPCC475205 | PP | WA | WALLA WALLA | BOWMAN | TR_262101_302080325 | 2008 | Before | 2008-01-06 16:23 | 2008-01-06 21:02 | 1 | 279.15 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 661642 | CPCC | CPCC477997 | PP | WA | WALLA WALLA | BOWMAN | TR_232202_593050131 | 2008 | Before | 2008-01-09 09:42 | 2008-01-09 12:56 | 1 | 194.217 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: remove tree limb from service | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 659555 | CPCC | CPCC478850 | PP | WA | WALLA WALLA | BOWMAN | TR_239300_593050222 | 2008 | Before | 2008-01-12 21:32 | 2008-01-12 22:34 | 2 | 123.733 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Re-fused transformer. Per serviceman weak fuse. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 659963 | CPCC | CPCC474869 | PP | WA | WALLA WALLA | BOWMAN | TR_356902_369970313 | 2008 | Before | 2008-01-06 11:03 | 2008-01-06 14:09 | 1 | 185.883 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 657056 | CPCC | CPCC472730 | PP | WA | WALLA WALLA | BOWMAN | TR_269503_302080215 | 2008 | Before | 2008-01-04 12:37 | 2008-01-06 13:08 | 1 | 2911.417 | 0 | 0 | 1 | Y | N | N | N | Y | 706 - 2008-01-04 to 2008-01-05 WA Walla Walla | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: outbound calling | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 660003 | CPCC | CPCC476236 | PP | WA | WALLA WALLA | BOWMAN | TR_360900_456710519 | 2008 | Before | 2008-01-07 10:30 | 2008-01-07 17:07 | 1 | 397.7 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 661344 | CPCC | CPCC475143 | PP | WA | WALLA WALLA | BOWMAN | TR_192201_825860476 | 2008 | Before | 2008-01-06 14:58 | 2008-01-07 08:41 | 1 | 1063.133 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 660510 | CPCC | CPCC474938 | PP | WA | WALLA WALLA | BOWMAN | TR_251305_209420386 | 2008 | Before | 2008-01-06 12:29 | 2008-01-06 20:59 | 1 | 509.067 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 657629 | CPCC | CPCC473058 | PP | WA | WALLA WALLA | BOWMAN | TR_192201_825860476 | 2008 | Before | 2008-01-04 15:26 | 2008-01-06 12:06 | 10 | 26798.333 | 0 | 0 | 1 | Y | N | N | N | Y | 706 - 2008-01-04 to 2008-01-05 WA Walla Walla | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 699970 | CPCC | CPCC531790 | PP | WA | WALLA WALLA | BOWMAN | TR_329900_636330450 | 2008 | Before | 2008-11-14 19:56 | 2008-11-14 21:16 | 1 | 79.933 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 701198 | CPCC | CPCC527185 | PP | WA | WALLA WALLA | BOWMAN | OH_266465_302080368 | 2008 | Before | 2008-10-15 15:03 | 2008-10-15 16:18 | 49 | 3674.183 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | POLE OH |  |  |  | PROSPER: Refused pole #266465 A & C phase due to car hit pole at 1220 Campbell Rd. Isolated at pole# 262302. See related ouatage # 527189 | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.3953 | 46.0552
5W150 | 701199 | CPCC | CPCC527189 | PP | WA | WALLA WALLA | BOWMAN | Line Cut-31565 | 2008 | Before | 2008-10-15 15:06 | 2008-10-15 23:08 | 23 | 11085.233 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | POLE OH |  |  |  | PROSPER: Serviceman lifted jumpers pole 262302 due to wire down 1220 Campbell Rd. See related outage # 527185. Pole repalced and customers are back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.4032 | 46.0545
5W150 | 696337 | CPCC | CPCC525810 | PP | WA | WALLA WALLA | BOWMAN | TR_235264_593050192 | 2008 | Before | 2008-10-06 11:48 | 2008-10-06 12:47 | 5 | 294.25 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused transformer# 235264 and it held, the cause is unknown, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 697571 | CPCC | CPCC525051 | PP | WA | WALLA WALLA | BOWMAN | TR_243200_593050252 | 2008 | Before | 2008-10-02 16:03 | 2008-10-02 16:49 | 4 | 186 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Refused transformer due to squirrel. Power restored | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 699230 | CPCC | CPCC525944 | PP | WA | WALLA WALLA | BOWMAN | OH_320300_636330398 | 2008 | Before | 2008-10-07 15:12 | 2008-10-07 17:03 | 31 | 3433.25 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Tree limb in OH primary. Power restored | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.471 | 46.0404
5W150 | 700937 | CPCC | CPCC527184 | PP | WA | WALLA WALLA | BOWMAN | TR_264302_302080310 | 2008 | Before | 2008-10-15 15:04 | 2008-10-15 16:16 | 1 | 71.567 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | POLE OH |  |  |  | PROSPER: Connectivity error. This transformer should be on C phase not B phase. Part of outage # 527185. Mapping changes made. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 702162 | CPCC | CPCC531571 | PP | WA | WALLA WALLA | BOWMAN | OH_280360_636330418 | 2008 | Before | 2008-11-13 05:18 | 2008-11-13 08:09 | 28 | 4787.533 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused the tapline fuse at pole# 280360 and it held, the cause was wind, customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.4506 | 46.0541
5W150 | 700253 | CPCC | CPCC531874 | PP | WA | WALLA WALLA | BOWMAN | TR_069801_20410251 | 2008 | Before | 2008-11-16 06:42 | 2008-11-16 07:51 | 3 | 209.1 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | PROSPER: Bad connector. Replaced. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 690929 | CPCC | CPCC517044 | PP | WA | WALLA WALLA | BOWMAN | TR_348801_636330460 | 2008 | Before | 2008-08-14 10:03 | 2008-08-14 10:48 | 1 | 45.15 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused transformer# 348801 and it held, the cause was a B/O fuse, customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 690140 | CPCC | CPCC518062 | PP | WA | WALLA WALLA | BOWMAN | TR_360800_456710520 | 2008 | Before | 2008-08-19 05:19 | 2008-08-19 05:56 | 1 | 36.967 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Lightning blew transformer fuse. Refused and customer is back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 692641 | CPCC | CPCC517994 | PP | WA | WALLA WALLA | BOWMAN | Line Cut-30565 | 2008 | Before | 2008-08-18 18:52 | 2008-08-19 00:18 | 75 | 24455 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | WEATHER | LIGHTNING | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: Associate to outage# 518002. Crew needed to make repairs to the overhead primary jumpers that was burnt down due to a lightning strike. Repairs made and customers back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.3884 | 46.0508
5W150 | 692643 | CPCC | CPCC518002 | PP | WA | WALLA WALLA | BOWMAN | Line Cut-30563 | 2008 | Before | 2008-08-18 18:52 | 2008-08-19 00:18 | 91 | 29725.15 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: Crew needed to make repairs to the overhead primary jumpers that burnt down due to a lightning strike. Repairs made and customer is back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.3885 | 46.0508
5W150 | 692644 | CPCC | CPCC518004 | PP | WA | WALLA WALLA | BOWMAN | TR_250103_302080377 | 2008 | Before | 2008-08-18 18:59 | 2008-08-18 19:27 | 6 | 163.9 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 250103 and it held the cause was lightning, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 692341 | CPCC | CPCC517477 | PP | WA | WALLA WALLA | BOWMAN | TR_234102_593050148 | 2008 | Before | 2008-08-16 10:46 | 2008-08-16 10:50 | 0 | 0 | 1 | 4.517 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: same as outage # 517466 | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 692413 | CPCC | CPCC519661 | PP | WA | WALLA WALLA | BOWMAN | TR_237001_593050204 | 2008 | Before | 2008-08-25 12:29 | 2008-08-25 18:25 | 1 | 356.45 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | TRANSFORMER OH |  |  |  | PROSPER: Bad transformer. Need crew to repair. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 692077 | CPCC | CPCC517466 | PP | WA | WALLA WALLA | BOWMAN | OH_235161_593050199 | 2008 | Before | 2008-08-16 08:50 | 2008-08-16 11:21 | 23 | 3493.317 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: replaced fuse on pole 235161 | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.3978 | 46.0653
5W150 | 692078 | CPCC | CPCC517469 | PP | WA | WALLA WALLA | BOWMAN | TR_234102_593050148 | 2008 | Before | 2008-08-16 09:02 | 2008-08-16 10:37 | 1 | 95.8 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: same as outage # 517466 | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 703844 | CPCC | CPCC548489 | PP | WA | WALLA WALLA | BOWMAN | TR_264160_302080305 | 2009 | Before | 2009-01-10 16:52 | 2009-01-10 17:37 | 2 | 90.833 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Squirrel blew transformer fuse. Refused and customer is back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 705852 | CPCC | CPCC555398 | PP | WA | WALLA WALLA | BOWMAN | OH_230240_593050166 | 2009 | Before | 2009-03-02 11:18 | 2009-03-02 18:00 | 2 | 803.6 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: Crew to make repairs. They are currently working a job and will head here when they get done. Replaced primary and customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.408 | 46.0676
5W150 | 707142 | CPCC | CPCC553827 | PP | WA | WALLA WALLA | BOWMAN | TR_241461_593050243 | 2009 | Before | 2009-02-21 09:36 | 2009-02-21 10:53 | 3 | 231.2 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 705644 | CPCC | CPCC556592 | PP | WA | WALLA WALLA | BOWMAN | TR_251101_209420369 | 2009 | Before | 2009-03-11 19:45 | 2009-03-11 21:00 | 1 | 74.383 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 684312 | CPCC | CPCC508061 | PP | WA | WALLA WALLA | BOWMAN | TR_281100_636330416 | 2008 | Before | 2008-06-27 10:39 | 2008-06-27 12:26 | 1 | 106.467 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: Replaced B/O connectors at transformer. Voltage good power restored | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 688995 | CPCC | CPCC517710 | PP | WA | WALLA WALLA | BOWMAN | Line Cut-30536 | 2008 | Before | 2008-08-17 18:14 | 2008-08-17 23:12 | 2 | 596.033 | 0 | 0 | 1 | Y | N | N | N | N |  | ENVIRONMENT | FIRE/SMOKE (NOT DUE TO FAULTS) |  |  | POLE OH |  |  |  | PROSPER: Field on fire and it caught our pole on fire, burnt down 2 poles. Repairs made and customers are back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.5342 | 46.0502
5W150 | 689416 | CPCC | CPCC520288 | PP | WA | WALLA WALLA | BOWMAN | Line Cut-30846 | 2008 | Before | 2008-08-29 09:40 | 2008-08-29 09:40 | 0 | 0 | 12 | 2 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: T & R | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.5219 | 46.05
5W150 | 689417 | CPCC | CPCC520297 | PP | WA | WALLA WALLA | BOWMAN | Line Cut-30848 | 2008 | Before | 2008-08-29 10:46 | 2008-08-29 10:46 | 0 | 0 | 2 | 0.8 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: T & R | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.5173 | 46.0497
5W150 | 685785 | CPCC | CPCC513730 | PP | WA | WALLA WALLA | BOWMAN | TR_266404_302080389 | 2008 | Before | 2008-07-25 06:18 | 2008-07-25 06:47 | 1 | 29.333 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Squirrel blew transformer fuse. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 683768 | CPCC | CPCC507943 | PP | WA | WALLA WALLA | BOWMAN | Line Cut-29766 | 2008 | Before | 2008-06-27 06:29 | 2008-06-27 07:58 | 1766 | 157174 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF SUBSTATION | ANIMALS | ANIMALS | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: squirrel on main bus | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.3614 | 46.068
5W150 | 684180 | CPCC | CPCC511679 | PP | WA | WALLA WALLA | BOWMAN | OH_250201_302080361 | 2008 | Before | 2008-07-10 06:40 | 2008-07-10 07:29 | 152 | 7377.067 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Squirell blown transformer fuse caused blown line fuse | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.3885 | 46.0529
5W150 | 684181 | CPCC | CPCC511683 | PP | WA | WALLA WALLA | BOWMAN | TR_252203_209420379 | 2008 | Before | 2008-07-10 07:31 | 2008-07-10 10:45 | 10 | 1940.667 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | TRANSFORMER OH |  |  |  | PROSPER: Crew needed to change out the cutout and transformer on pole# 252203 that was damaged by a squirrel. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 727603 | CPCC | CPCC564312 | PP | WA | WALLA WALLA | BOWMAN | OH_319900_636330342 | 2009 | Before | 2009-05-07 01:47 | 2009-05-07 07:43 | 45 | 16049.25 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Recreated outage, original is 564308; SMoyer | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.472 | 46.0478
5W150 | 727606 | CPCC | CPCC564829 | PP | WA | WALLA WALLA | BOWMAN | OH_312700_1540918583 | 2009 | Before | 2009-05-12 15:27 | 2009-05-12 16:35 | 39 | 2682.55 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Tree through primary. Crew to make repairs. Serviceman isolated the irrigation bank that was not being used and refused the tapline, customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.4883 | 46.046
5W150 | 727666 | CPCC | CPCC571756 | PP | WA | WALLA WALLA | BOWMAN | OH_320300_636330398 | 2009 | Before | 2009-06-18 23:34 | 2009-06-19 02:44 | 24 | 4577.6 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Blown line fuse. Patrolling line. Could not find a cause. Refused and customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.471 | 46.0404
5W150 | 723407 | CPCC | CPCC561447 | PP | WA | WALLA WALLA | BOWMAN | TR_251105_209420364 | 2009 | Before | 2009-04-18 07:57 | 2009-04-18 08:41 | 10 | 442.667 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: replaced transformer fuse | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 727847 | CPCC | CPCC571443 | PP | WA | WALLA WALLA | BOWMAN | TR_250200_302080373 | 2009 | Before | 2009-06-16 09:32 | 2009-06-16 10:39 | 1 | 67.3 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: per serviceman: b/o secondary connector at the pole. Serviceman replaced and customer back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 723566 | CPCC | CPCC564313 | PP | WA | WALLA WALLA | BOWMAN | OH_319900_636330342 | 2009 | Before | 2009-05-07 05:17 | 2009-05-07 07:43 | 6 | 877.2 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | B/O EQUIPMENT | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Recreated outage, original is 564309; SMoyer | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.472 | 46.0478
5W150 | 724434 | CPCC | CPCC567773 | PP | WA | WALLA WALLA | BOWMAN | TR_275700_636330288 | 2009 | Before | 2009-06-01 08:59 | 2009-06-01 12:10 | 1 | 190.55 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | TRANSFORMER OH |  |  |  | PROSPER: See outage 567758 for crew and outage times. Racoon damaged bushings on xfmr and blew fuse. Crew to repalce xfmr and cut-out. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 719581 | CPCC | CPCC565189 | PP | WA | WALLA WALLA | BOWMAN | TR_358800_1540752741 | 2009 | Before | 2009-05-15 07:32 | 2009-05-15 08:37 | 1 | 64.75 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused the transformer and it held, the cause was a B/O fuse, customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 718001 | CPCC | CPCC533372 | PP | WA | WALLA WALLA | BOWMAN | OH_250201_302080361 | 2008 | Before | 2008-11-30 14:54 | 2008-11-30 16:00 | 151 | 10041.5 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: suspect fuse melted out on pole 359105, due to added load after feeder tie switching same as outage 533380 | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.3885 | 46.0529
5W150 | 718003 | CPCC | CPCC533382 | PP | WA | WALLA WALLA | BOWMAN | TR_251303_209420387 | 2008 | Before | 2008-11-30 15:01 | 2008-11-30 15:47 | 1 | 46.317 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: suspect fuse melted out on pole 359105, due to added load after feeder tie switching sama as outage 533380 | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 718868 | CPCC | CPCC544200 | PP | WA | WALLA WALLA | BOWMAN | BOW_CB5W150 | 2008 | Before | 2008-12-29 13:03 | 2008-12-29 14:47 | 1773 | 184657.95 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | POLE FIRE | POLE OH |  |  |  | PROSPER: crew on site CB open at sub | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.3614 | 46.0679
5W150 | 718472 | CPCC | CPCC533528 | PP | WA | WALLA WALLA | BOWMAN | TR_251105_209420364 | 2008 | Before | 2008-12-02 11:23 | 2008-12-02 11:57 | 11 | 379.317 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 251105 and it held, the cause was a squirrel, customers are back in full service. Serviceman installed a guard to prevent this from happening again in the future. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 719378 | CPCC | CPCC565977 | PP | WA | WALLA WALLA | BOWMAN | BOW_CB5W150 | 2009 | Before | 2009-05-21 13:43 | 2009-05-21 13:44 | 0 | 0 | 1784 | 416.267 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: T & R due to a squirrel that got into the top of a transformer. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.3614 | 46.0679
5W150 | 719380 | CPCC | CPCC565983 | PP | WA | WALLA WALLA | BOWMAN | TR_251202_209420371 | 2009 | Before | 2009-05-21 13:44 | 2009-05-21 16:05 | 8 | 1130.533 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | TRANSFORMER OH |  |  |  | PROSPER: Crew needed to change out the transformer and cutout on pole# 251202 that was damaged by a squirrel. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 719781 | CPCC | CPCC570392 | PP | WA | WALLA WALLA | BOWMAN | OH_280360_636330418 | 2009 | Before | 2009-06-09 01:53 | 2009-06-09 04:56 | 29 | 5294.433 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: replaced fuse, no cause | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.4506 | 46.0541
5W150 | 721449 | CPCC | CPCC563041 | PP | WA | WALLA WALLA | BOWMAN | TR_319961_636330341 | 2009 | Before | 2009-05-02 02:32 | 2009-05-02 05:37 | 1 | 184.85 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Part of outage 563041 Blown line fuses, patrolling line nothing found | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 721451 | CPCC | CPCC563043 | PP | WA | WALLA WALLA | BOWMAN | OH_319900_636330342 | 2009 | Before | 2009-05-02 03:41 | 2009-05-02 05:35 | 51 | 5807.2 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Blown line fuses, patrolling line nothing found | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.472 | 46.0478
5W150 | 721935 | CPCC | CPCC570304 | PP | WA | WALLA WALLA | BOWMAN | OH_320300_636330398 | 2009 | Before | 2009-06-08 04:56 | 2009-06-08 07:20 | 28 | 4031.533 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Blown line fuse, no cause found. Refused and customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.471 | 46.0404
5W150 | 715817 | CPCC | CPCC534478 | PP | WA | WALLA WALLA | BOWMAN | TR_347701_1540118162 | 2008 | Before | 2008-12-09 14:32 | 2008-12-09 17:53 | 1 | 201.067 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | TRANSFORMER OH |  |  |  | PROSPER: fuse is melted out @ 347701- b/o 10 kva xfmr. leaking oil changed out pot | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 718690 | CPCC | CPCC544464 | PP | WA | WALLA WALLA | BOWMAN | OH_360901_456710508 | 2008 | Before | 2008-12-30 12:25 | 2008-12-30 15:44 | 16 | 1098.067 | 0 | 0 | 2 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | LIGHTNING ARRESTER OH |  |  |  | PROSPER: replace b/o lightning arrestor | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.3872 | 46.0491
5W150 | 721977 | CPCC | CPCC563262 | PP | WA | WALLA WALLA | BOWMAN | OH_357901_302080000 | 2009 | Before | 2009-05-02 15:53 | 2009-05-02 17:36 | 27 | 2764.35 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.3928 | 46.0493
5W150 | 721978 | CPCC | CPCC563263 | PP | WA | WALLA WALLA | BOWMAN | OH_269100_302080365 | 2009 | Before | 2009-05-02 15:49 | 2009-05-02 17:24 | 67 | 6365 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: line fuse | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.3889 | 46.0516
5W150 | 721179 | CPCC | CPCC564301 | PP | WA | WALLA WALLA | BOWMAN | TR_278501_636330328 | 2009 | Before | 2009-05-06 22:48 | 2009-05-07 01:48 | 1 | 179.9 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 721180 | CPCC | CPCC564302 | PP | WA | WALLA WALLA | BOWMAN | OH_277502_636330291 | 2009 | Before | 2009-05-06 23:20 | 2009-05-07 01:48 | 15 | 2217 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.4146 | 46.0566
5W150 | 721192 | CPCC | CPCC564966 | PP | WA | WALLA WALLA | BOWMAN | OH_358800_1540858501 | 2009 | Before | 2009-05-13 05:37 | 2009-05-13 06:54 | 5 | 387.583 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Blown line fuse, patrolled line and did not find a cause. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.5153 | 46.0469
5W150 | 733195 | CPCC | CPCC574148 | PP | WA | WALLA WALLA | BOWMAN | TR_269101_302080406 | 2009 | Before | 2009-07-04 15:10 | 2009-07-04 16:51 | 1 | 100.367 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Customers breaker was tripped. Serviceman also noticed that the neutral was almost burnt in two. Made repairs to neutral. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 729229 | CPCC | CPCC566450 | PP | WA | WALLA WALLA | BOWMAN | TR_275700_636330288 | 2009 | Before | 2009-05-26 07:56 | 2009-05-26 09:11 | 1 | 75.533 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused transformer# 275700 and it held, the cause is unknown, pump is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 729627 | CPCC | CPCC570802 | PP | WA | WALLA WALLA | BOWMAN | TR_365960_649900129 | 2009 | Before | 2009-06-12 16:55 | 2009-06-12 18:25 | 1 | 89.133 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Part of outage 570820 Blown line fuse, no cause found | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 729628 | CPCC | CPCC570804 | PP | WA | WALLA WALLA | BOWMAN | TR_344500_636330464 | 2009 | Before | 2009-06-12 16:56 | 2009-06-12 18:25 | 1 | 88.8 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Part of outage 570820 Blown line fuse, no cause found | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 729633 | CPCC | CPCC570820 | PP | WA | WALLA WALLA | BOWMAN | Line Cut-35591 | 2009 | Before | 2009-06-12 16:54 | 2009-06-12 18:22 | 179 | 15650.567 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Blown line, patrolling line, nothing found | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.4291 | 46.0538
5W150 | 729634 | CPCC | CPCC570822 | PP | WA | WALLA WALLA | BOWMAN | TR_347700_636330462 | 2009 | Before | 2009-06-12 17:25 | 2009-06-12 18:25 | 1 | 59.217 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Part of outage 570820 Blown line fuse, no cause found | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 729635 | CPCC | CPCC570823 | PP | WA | WALLA WALLA | BOWMAN | TR_310881_1540815594 | 2009 | Before | 2009-06-12 17:34 | 2009-06-12 18:25 | 1 | 50.55 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Part of outage 570820 Blown line fuse, no cause found | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 729264 | CPCC | CPCC562688 | PP | WA | WALLA WALLA | BOWMAN | OH_320300_636330398 | 2009 | Before | 2009-04-28 03:15 | 2009-04-28 06:26 | 29 | 5567.033 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: 2 blown line fuses crew to patrol no cause found | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.471 | 46.0404
5W150 | 730536 | CPCC | CPCC561840 | PP | WA | WALLA WALLA | BOWMAN | TR_289000_636330409 | 2009 | Before | 2009-04-21 14:01 | 2009-04-21 15:22 | 1 | 81.617 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused transformer# 289000 and it held, the cause is unknown, pump is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 732178 | CPCC | CPCC566210 | PP | WA | WALLA WALLA | BOWMAN | TR_246300_593050276 | 2009 | Before | 2009-05-24 11:29 | 2009-05-24 13:03 | 1 | 94.883 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 730639 | CPCC | CPCC573283 | PP | WA | WALLA WALLA | BOWMAN | TR_367960_649900128 | 2009 | Before | 2009-06-30 13:15 | 2009-06-30 15:59 | 1 | 164.033 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Per serviceman: Tree branch fell and took down o/h service and primary neutral on pole# 367960. Crew repaired service and primary neutral. All customers back in service. associated outage #573305 | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 730642 | CPCC | CPCC573305 | PP | WA | WALLA WALLA | BOWMAN | TR_367960_649900128 | 2009 | Before | 2009-06-30 15:15 | 2009-06-30 15:59 | 3 | 130.65 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | TREES | TREE - NON-PREVENTABLE | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Associated outage # 573283. Crew had to de-energize x-fmr to make repairs to o/h service wire (see associated outage). Repairs made and all customers back in service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 734716 | CPCC | CPCC576754 | PP | WA | WALLA WALLA | BOWMAN | TR_363700_649900125 | 2009 | Before | 2009-07-21 07:41 | 2009-07-21 09:54 | 1 | 133.05 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: refused 25 t's at 734/364901 | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 730334 | CPCC | CPCC570599 | PP | WA | WALLA WALLA | BOWMAN | OH_320300_636330398 | 2009 | Before | 2009-06-11 00:54 | 2009-06-11 03:36 | 28 | 4530.867 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD SUSPECTED, NO MORTALITY |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: blown fuse may have been a bird has happened some in this area | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.471 | 46.0404
5W150 | 731135 | CPCC | CPCC570691 | PP | WA | WALLA WALLA | BOWMAN | TR_277206_636330324 | 2009 | Before | 2009-06-11 20:06 | 2009-06-11 21:27 | 1 | 81.2 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 731509 | CPCC | CPCC571261 | PP | WA | WALLA WALLA | BOWMAN | TR_250200_302080373 | 2009 | Before | 2009-06-13 17:29 | 2009-06-13 19:41 | 1 | 132.817 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Service leg broken in a tree replaced service.Crew completed replacing secondary service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 714307 | CPCC | CPCC546967 | PP | WA | WALLA WALLA | BOWMAN | TR_358901_369970318 | 2009 | Before | 2009-01-04 14:48 | 2009-01-04 16:50 | 18 | 2189.4 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: replaced transformer fuse | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 709495 | CPCC | CPCC550544 | PP | WA | WALLA WALLA | BOWMAN | OH_289300_636330233 | 2009 | Before | 2009-01-26 19:22 | 2009-01-26 21:29 | 9 | 1147.05 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Blown line fuse. Patrolled line and all the wire is up. Outage 550551 has a bad transformer which cause fuse to blow. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.43 | 46.0536
5W150 | 709500 | CPCC | CPCC550551 | PP | WA | WALLA WALLA | BOWMAN | TR_289101_636330258 | 2009 | Before | 2009-01-26 21:29 | 2009-01-27 02:09 | 1 | 279.5 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | PROSPER: Associated with outage 550544. Transformer fuse was blown. Bad order transformer crew needed. Replaced transformer and customers are back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 714777 | CPCC | CPCC555879 | PP | WA | WALLA WALLA | BOWMAN | OH_320300_636330398 | 2009 | Before | 2009-03-05 09:15 | 2009-03-05 10:52 | 14 | 1362.2 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: blown line fuse, serviceman found no cause so he refused and it held. All customers back in service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.471 | 46.0404
5W150 | 711176 | CPCC | CPCC560524 | PP | WA | WALLA WALLA | BOWMAN | TR_279003_636330310 | 2009 | Before | 2009-04-11 18:42 | 2009-04-11 19:58 | 1 | 75.25 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | PROSPER: replaced sec connector | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 709604 | CPCC | CPCC559035 | PP | WA | WALLA WALLA | BOWMAN | TR_348801_636330460 | 2009 | Before | 2009-03-31 14:34 | 2009-03-31 16:25 | 1 | 111.25 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Crew made repairs to the b/o open wire secondary that was damaged by the wind, customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 710442 | CPCC | CPCC551357 | PP | WA | WALLA WALLA | BOWMAN | OH_273304_1540821892 | 2009 | Before | 2009-02-05 10:16 | 2009-02-05 11:13 | 1 | 57.633 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | ANIMALS | ANIMALS | SECONDARY CABLE UG |  |  |  | PROSPER: Serviceman took outage on the dip fuse at pole# 273304 to make repairs to a B/O leg that was chewed by a critter, also lowered the tap settings on the padmount transformer. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.422 | 46.054
5W150 | 750407 | CPCC | CPCC601917 | PP | WA | WALLA WALLA | BOWMAN | TR_264061_649900232 | 2009 | Before | 2009-11-30 08:32 | 2009-11-30 10:11 | 1 | 98.367 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: will dispactch this at 9 when the serviceman starts. Serviceman found a blown xfmr fuse and replaced it. No cause found. Customer back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 749264 | CPCC | CPCC596722 | PP | WA | WALLA WALLA | BOWMAN | OH_239260_593050183 | 2009 | Before | 2009-11-07 00:54 | 2009-11-07 03:56 | 82 | 14967.733 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | PROSPER: car hit guy wire | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.3905 | 46.0678
5W150 | 750079 | CPCC | CPCC596778 | PP | WA | WALLA WALLA | BOWMAN | TR_250109_209420376 | 2009 | Before | 2009-11-07 14:57 | 2009-11-07 15:57 | 36 | 2166.6 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: squirrel serviceman refused xfmr | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 751309 | CPCC | CPCC593176 | PP | WA | WALLA WALLA | BOWMAN | TR_266208_302080400 | 2009 | Before | 2009-10-14 17:52 | 2009-10-14 18:43 | 5 | 251.833 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 747776 | CPCC | CPCC582529 | PP | WA | WALLA WALLA | BOWMAN | TR_329800_636330255 | 2009 | Before | 2009-08-15 14:45 | 2009-08-15 15:41 | 1 | 56.133 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 750590 | CPCC | CPCC591611 | PP | WA | WALLA WALLA | BOWMAN | BOW_CB5W150 | 2009 | Before | 2009-10-07 02:04 | 2009-10-07 02:04 | 0 | 0 | 47 | 3.917 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | POLE OH |  |  |  | PROSPER: Trash truck damage twp poles | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.3614 | 46.0679
5W150 | 750660 | CPCC | CPCC601922 | PP | WA | WALLA WALLA | BOWMAN | TR_243200_593050252 | 2009 | Before | 2009-11-30 09:28 | 2009-11-30 10:33 | 4 | 261.2 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman is on another job, he will get here next. Blown xfmr fuse. Serviceman investigating. Squirrel blew xfmr fuse. Serviceman replaced and all customers are back in service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 750349 | CPCC | CPCC596891 | PP | WA | WALLA WALLA | BOWMAN | TR_276600_636330278 | 2009 | Before | 2009-11-08 09:45 | 2009-11-08 11:12 | 1 | 86.95 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: squirrel. refused, back in power | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 746962 | CPCC | CPCC581934 | PP | WA | WALLA WALLA | BOWMAN | TR_289101_636330258 | 2009 | Before | 2009-08-11 15:57 | 2009-08-11 16:46 | 1 | 48.333 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: X-fmr fuse blown due to bird (starling). Serviceman replaced fuse and fuse held. Customer back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 745400 | CPCC | CPCC582064 | PP | WA | WALLA WALLA | BOWMAN | OH_334400_636330443 | 2009 | Before | 2009-08-12 11:39 | 2009-08-12 12:24 | 15 | 676.25 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: refused line fuse, power on | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.4409 | 46.0418
5W150 | 746610 | CPCC | CPCC591599 | PP | WA | WALLA WALLA | BOWMAN | BOW_CB5W150 | 2009 | Before | 2009-10-06 23:53 | 2009-10-07 02:04 | 4 | 520.733 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: De-energized to make up jumpers after repairs were made due to a car/pole | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.3614 | 46.0679
5W150 | 745133 | CPCC | CPCC582047 | PP | WA | WALLA WALLA | BOWMAN | OH_334400_636330443 | 2009 | Before | 2009-08-12 10:11 | 2009-08-12 11:36 | 15 | 1270.5 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused transformer# 334400 and it held, the cause was a B/O fuse, customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.4409 | 46.0418
5W150 | 746347 | CPCC | CPCC591506 | PP | WA | WALLA WALLA | BOWMAN | BOW_CB5W150 | 2009 | Before | 2009-10-06 13:48 | 2009-10-07 02:04 | 1792 | 211479.866 | 0 | 0 | 4 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | POLE OH |  |  |  | PROSPER: Crew needed to replace 2 poles and wire that was taken down by a truck. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.3614 | 46.0679
5W150 | 757883 | CPCC | CPCC627661 | PP | WA | WALLA WALLA | BOWMAN | TR_287100_1540752795 | 2010 | Before | 2010-04-10 14:29 | 2010-04-10 15:52 | 1 | 82.95 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Open secondary neutral. Made repairs and customer is back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 758133 | CPCC | CPCC610292 | PP | WA | WALLA WALLA | BOWMAN | TR_236100_593050200 | 2010 | Before | 2010-01-01 08:27 | 2010-01-01 09:06 | 6 | 230 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused transformer# 236100 and it held, the cause was a rotted fuse, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 758148 | CPCC | CPCC627066 | PP | WA | WALLA WALLA | BOWMAN | OH_271202_636330294 | 2010 | Before | 2010-04-08 12:40 | 2010-04-08 13:52 | 2 | 144.167 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: B/O jumper on dip cut-out. Serviceman to make repairs. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.4259 | 46.0534
5W150 | 740015 | CPCC | CPCC587524 | PP | WA | WALLA WALLA | BOWMAN | BOW_CB5W150 | 2009 | Before | 2009-09-17 13:06 | 2009-09-17 13:20 | 1791 | 23880 | 0 | 0 | 1 | Y | N | N | N | N |  | OPERATIONAL | PACIFICORP EMPLOYEE - FIELD |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Crew had hold on line. Jumper got away and hit neutral conductor. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.3614 | 46.0679
5W150 | 735690 | CPCC | CPCC570250 | PP | WA | WALLA WALLA | BOWMAN | OH_358800_1540858501 | 2009 | Before | 2009-06-07 08:17 | 2009-06-07 09:47 | 2 | 179.367 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: blown fuse | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.5153 | 46.0469
5W150 | 734944 | CPCC | CPCC564559 | PP | WA | WALLA WALLA | BOWMAN | TR_277502_1050461559 | 2009 | Before | 2009-05-09 08:24 | 2009-05-09 10:38 | 1 | 133.7 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: service needs to be replaced | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 736146 | CPCC | CPCC573837 | PP | WA | WALLA WALLA | BOWMAN | OH_277400_636330314 | 2009 | Before | 2009-07-03 10:44 | 2009-07-03 11:51 | 3 | 199.85 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Left message at 1048. Blown line fuse. No cause found. Refused and customer is back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.4145 | 46.0562
5W150 | 736967 | CPCC | CPCC580509 | PP | WA | WALLA WALLA | BOWMAN | TR_266405_302080388 | 2009 | Before | 2009-08-04 09:14 | 2009-08-04 09:47 | 4 | 132.2 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Broken fuse from wind vibration, refused transformer. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 737842 | CPCC | CPCC583718 | PP | WA | WALLA WALLA | BOWMAN | TR_262501_302080281 | 2009 | Before | 2009-08-24 23:00 | 2009-08-25 00:41 | 3 | 300.55 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: fuse melted out | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 737060 | CPCC | CPCC584939 | PP | WA | WALLA WALLA | BOWMAN | TR_364601_1540370053 | 2009 | Before | 2009-08-29 16:21 | 2009-08-29 18:17 | 2 | 231.7 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 740747 | CPCC | CPCC585642 | PP | WA | WALLA WALLA | BOWMAN | TR_263402_302080346 | 2009 | Before | 2009-09-03 12:59 | 2009-09-03 14:10 | 1 | 71.05 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | OVERLOAD |  |  | CONNECTOR OH |  |  |  | PROSPER: melted connectors on svc, also burned conductor. suspect undersized conductor. 2nd outage in a week. forwarded to engineering for svc upgrade. possible damage claim, open svc neutral | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 739954 | CPCC | CPCC584606 | PP | WA | WALLA WALLA | BOWMAN | TR_251105_209420364 | 2009 | Before | 2009-08-28 09:22 | 2009-08-28 10:07 | 10 | 449 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 251105 and it held, the cause was a squirrel, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 741192 | CPCC | CPCC583598 | PP | WA | WALLA WALLA | BOWMAN | TR_243200_593050252 | 2009 | Before | 2009-08-23 16:09 | 2009-08-23 17:42 | 1 | 93.183 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: squirell blown fuse | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 778530 | CPCC | CPCC631796 | PP | WA | WALLA WALLA | BOWMAN | OH_239260_593050183 | 2010 | Before | 2010-05-03 12:14 | 2010-05-03 14:46 | 37 | 2299.5 | 0 | 0 | 2 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Crew needed to make repairs to the overhead primary that was taken down by a tree. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.3905 | 46.0678
5W150 | 774297 | CPCC | CPCC638896 | PP | WA | WALLA WALLA | BOWMAN | TR_251105_209420364 | 2010 | Before | 2010-06-12 07:50 | 2010-06-12 09:55 | 1 | 124.7 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | PROSPER: replaced connectors at transformer | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 774684 | CPCC | CPCC630930 | PP | WA | WALLA WALLA | BOWMAN | OH_320300_636330398 | 2010 | Before | 2010-04-28 00:53 | 2010-04-28 01:55 | 2 | 123.433 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | TREES | TREE - NON-PREVENTABLE | CUT-OUT B/O OH |  |  |  | PROSPER: assoc. # 630920 | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.471 | 46.0404
5W150 | 771788 | CPCC | CPCC640508 | PP | WA | WALLA WALLA | BOWMAN | TR_243200_593050252 | 2010 | Before | 2010-06-26 15:26 | 2010-06-26 16:33 | 1 | 66.267 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: squirell blown transfomer fuse | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 768709 | CPCC | CPCC605965 | PP | WA | WALLA WALLA | BOWMAN | TR_262400_302080341 | 2009 | Before | 2009-12-10 20:45 | 2009-12-10 21:44 | 4 | 238.8 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: replace secondary conn at pole | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 772334 | CPCC | CPCC640608 | PP | WA | WALLA WALLA | BOWMAN | TR_262161_649900233 | 2010 | Before | 2010-06-27 15:22 | 2010-06-27 16:35 | 1 | 73.167 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: starling blown transformer fuse | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 771587 | CPCC | CPCC635952 | PP | WA | WALLA WALLA | BOWMAN | OH_364901_649900155 | 2010 | Before | 2010-05-20 06:00 | 2010-05-20 10:25 | 21 | 5577.95 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Crew isolated the overhead primary that is down due to a tree, the wire that is iolated feeds irrigation banks that are not in use at this time. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.5046 | 46.0478
5W150 | 767686 | CPCC | CPCC623380 | PP | WA | WALLA WALLA | BOWMAN | TR_246300_593050276 | 2010 | Before | 2010-03-26 16:01 | 2010-03-26 16:37 | 1 | 35.633 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused transformer# 246300 and it held, the cause is unknown, customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 771716 | CPCC | CPCC640119 | PP | WA | WALLA WALLA | BOWMAN | OH_277101_636330275 | 2010 | Before | 2010-06-24 04:56 | 2010-06-24 06:14 | 18 | 1408.5 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Blown line fuse. Patrolled line and could not find a cause. Refused and customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.4141 | 46.0519
5W150 | 782548 | CPCC | CPCC632700 | PP | WA | WALLA WALLA | BOWMAN | OH_252100_209420349 | 2010 | Before | 2010-05-07 20:40 | 2010-05-08 11:04 | 28 | 14545.417 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: Bad order dip fuse and UG. Crew needed to make repairs. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.3844 | 46.0508
5W150 | 780194 | CPCC | CPCC635717 | PP | WA | WALLA WALLA | BOWMAN | RC_263404_1540836522 | 2010 | Before | 2010-05-19 18:33 | 2010-05-20 00:26 | 451 | 82802.666 | 0 | 0 | 3 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Tree through primary. Isolate line and closed Field Recloser back in. Repairs made. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.4026 | 46.0564
5W150 | 782554 | CPCC | CPCC632718 | PP | WA | WALLA WALLA | BOWMAN | TR_252081_209420362 | 2010 | Before | 2010-05-08 04:05 | 2010-05-08 06:22 | 14 | 1922.667 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: Cable was mismarked and this transformer was still off. Switched transformer back on. Associated to outage 632700. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 782622 | CPCC | CPCC639576 | PP | WA | WALLA WALLA | BOWMAN | TR_267510_302080236 | 2010 | Before | 2010-06-18 08:09 | 2010-06-18 09:53 | 2 | 207.033 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: serviceman located open transformer fuse due to squirrel, investigated for damage, none observed, refused, outage restored | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 785037 | CPCC | CPCC630920 | PP | WA | WALLA WALLA | BOWMAN | OH_320300_636330398 | 2010 | Before | 2010-04-27 20:20 | 2010-04-28 01:55 | 30 | 10036.5 | 0 | 0 | 2 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | CUT-OUT B/O OH |  |  |  | PROSPER: removed tree limb off line, closed fuses, found bad cutout, need crew to replace all three cutouts. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.471 | 46.0404
5W150 | 782281 | CPCC | CPCC632661 | PP | WA | WALLA WALLA | BOWMAN | TR_233261_593050140 | 2010 | Before | 2010-05-07 14:47 | 2010-05-07 15:47 | 1 | 59.967 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: Serviceman replaced a B/O secondary connection at the weatherhead, customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 782288 | CPCC | CPCC632670 | PP | WA | WALLA WALLA | BOWMAN | TR_233261_593050140 | 2010 | Before | 2010-05-07 15:55 | 2010-05-07 18:45 | 1 | 170.317 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Standby repsonder is on another job he will get here next. service man talked with customer and ok with then to replace service tomarrow | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 781150 | CPCC | CPCC632535 | PP | WA | WALLA WALLA | BOWMAN | OH_250201_302080361 | 2010 | Before | 2010-05-06 12:20 | 2010-05-06 14:58 | 151 | 19487.75 | 0 | 0 | 2 | Y | N | N | N | N |  | INTERFERENCE | OTHER UTILITY/CONTRACTOR | TREES | TREE - NON-PREVENTABLE | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Crew needed to make repairs to the overhead primary that was taken down by a tee limb dropped by a tree trimmer. Also had to change out the transformer on pole# 250210, customers are all back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.3885 | 46.0529
5W150 | 782819 | CPCC | CPCC632748 | PP | WA | WALLA WALLA | BOWMAN | OH_252100_209420349 | 2010 | Before | 2010-05-08 10:38 | 2010-05-08 11:04 | 21 | 542.5 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | INTENTIONAL TO CLEAR TROUBLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: de-energized to install leads to live frount trans. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.3844 | 46.0508
5W150 | 781688 | CPCC | CPCC638040 | PP | WA | WALLA WALLA | BOWMAN | Line Cut-43408 | 2010 | Before | 2010-06-07 08:24 | 2010-06-07 09:48 | 7 | 582.983 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Blown line fuse. Serviceman patrolled line, no cause found. He refused and it held. All customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.4615 | 46.051
5W150 | 799367 | CPCC | CPCC656179 | PP | WA | WALLA WALLA | BOWMAN | TR_264302_302080310 | 2010 | Before | 2010-09-25 12:01 | 2010-09-25 14:24 | 6 | 853.5 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | PROSPER: REPLACED CONNECTORS | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 799373 | CPCC | CPCC656206 | PP | WA | WALLA WALLA | BOWMAN | TR_234102_593050148 | 2010 | Before | 2010-09-25 15:28 | 2010-09-25 16:13 | 4 | 177.867 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | PROSPER: replaced connectors | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 803430 | CPCC | CPCC659772 | PP | WA | WALLA WALLA | BOWMAN | TR_279004_649900238 | 2010 | Before | 2010-10-19 08:00 | 2010-10-19 09:18 | 1 | 78.1 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman arrived and found open fuse, refused and said cause was a starling | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 792606 | CPCC | CPCC656814 | PP | WA | WALLA WALLA | BOWMAN | OH_357901_302080000 | 2010 | Before | 2010-10-02 04:13 | 2010-10-02 06:57 | 10 | 1639.333 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | LIGHTNING ARRESTER OH |  |  |  | PROSPER: Bad order Lightning arrestor. Replaced and switched UG to get customers back on. See orignial outage 656810 for arrival times. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.3928 | 46.0493
5W150 | 792610 | CPCC | CPCC656820 | PP | WA | WALLA WALLA | BOWMAN | TR_276600_636330278 | 2010 | Before | 2010-10-02 09:02 | 2010-10-02 10:24 | 2 | 165.333 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Blown transformer fuse. Cause was squirrel, installed squirrel guard and refused. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 795014 | CPCC | CPCC657145 | PP | WA | WALLA WALLA | BOWMAN | TR_360806_456710472 | 2010 | Before | 2010-10-05 16:14 | 2010-10-05 18:11 | 1 | 116.867 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Serviceman replaced the B/O overhead secondary service, customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 797032 | CPCC | CPCC649399 | PP | WA | WALLA WALLA | BOWMAN | TR_264401_302080354 | 2010 | Before | 2010-08-12 20:28 | 2010-08-12 23:40 | 5 | 959.167 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | PROSPER: blown transformer fuse , transformer tested bad | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 793121 | CPCC | CPCC655604 | PP | WA | WALLA WALLA | BOWMAN | TR_360902_456710397 | 2010 | Before | 2010-09-21 16:08 | 2010-09-21 16:22 | 1 | 13.383 | 0 | 0 | 1 | Y | N | N | N | N |  | OPERATIONAL | INTERNAL CONTRACTOR |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman turned the customers main breaker back on after the AMR meter installers left the breaker turned off. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 795898 | CPCC | CPCC668649 | PP | WA | WALLA WALLA | BOWMAN | TR_361801_456710499 | 2010 | Before | 2010-12-06 14:54 | 2010-12-06 16:19 | 1 | 84.933 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: Serviceman replaced the B/O secondary connection at the transformer, customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 807263 | CPCC | CPCC685520 | PP | WA | WALLA WALLA | BOWMAN | OH_294161_636330486 | 2011 | Before | 2011-02-28 07:02 | 2011-02-28 09:40 | 11 | 1734.517 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused the tapline fuses at pole# 294161 and they held, the cause was high wind in the area, customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.4615 | 46.051
5W150 | 808847 | CPCC | CPCC700060 | PP | WA | WALLA WALLA | BOWMAN | TR_260103_302080201 | 2011 | Before | 2011-04-03 18:29 | 2011-04-03 19:45 | 1 | 76.167 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Fuse had melted out, fuse replaced, customer power restored | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 807779 | CPCC | CPCC685675 | PP | WA | WALLA WALLA | BOWMAN | OH_265961_1540117656 | 2011 | Before | 2011-02-28 10:23 | 2011-02-28 11:45 | 25 | 2048.333 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | OTHER INTERFERING OBJECT | WEATHER | WIND | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Servicemen removed a carport from the overhead primary and refused the tapline fuse at pole# 265961, customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.3979 | 46.0628
5W150 | 786119 | CPCC | CPCC638801 | PP | WA | WALLA WALLA | BOWMAN | TR_250306_209420393 | 2010 | Before | 2010-06-10 19:42 | 2010-06-10 22:38 | 5 | 878.25 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: changed broken cutout | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 789627 | CPCC | CPCC651754 | PP | WA | WALLA WALLA | BOWMAN | OH_239260_593050183 | 2010 | Before | 2010-08-26 16:09 | 2010-08-26 19:49 | 37 | 4495.117 | 0 | 0 | 2 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Crwe needed to make repairs to the overhead primary that was taken down by a tree. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.3905 | 46.0678
5W150 | 825019 | CPCC | CPCC706690 | PP | WA | WALLA WALLA | BOWMAN | TR_242202_593050256 | 2011 | Before | 2011-05-26 16:40 | 2011-05-26 17:18 | 3 | 112.2 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman onsite refusing transformer# 242202 that is open due to a squirrel. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 825427 | CPCC | CPCC709611 | PP | WA | WALLA WALLA | BOWMAN | TR_238203_593050185 | 2011 | Before | 2011-06-20 16:43 | 2011-06-20 19:18 | 1 | 155.233 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman replaced xfmr fuse no cause found. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 826639 | CPCC | CPCC703262 | PP | WA | WALLA WALLA | BOWMAN | TR_057701_20410448 | 2011 | Before | 2011-04-26 14:39 | 2011-04-26 15:24 | 1 | 45.067 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman reconnected the primary jumpers on pole# 057700, customer is back in full service. The jumpers were probably lifted during a storm outage and not replaced due to the house being empty. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 828664 | CPCC | CPCC705458 | PP | WA | WALLA WALLA | BOWMAN | OH_319900_636330342 | 2011 | Before | 2011-05-15 00:50 | 2011-05-15 02:33 | 43 | 4434.733 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (PROTECTED SPECIES) (BMTS) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman patrolled line after finding 2 fuses open at fp-319900 and found a deceased Pelecan between 2 sets of line fuses. Believe this to be the cause will close fuses on test and report.Closed in and held. Outage restored. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.472 | 46.0478
5W150 | 828798 | CPCC | CPCC704658 | PP | WA | WALLA WALLA | BOWMAN | OH_320300_636330398 | 2011 | Before | 2011-05-09 00:04 | 2011-05-09 01:13 | 31 | 2143.133 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Found A and C phase fuses blown at pole 320300, patrolled line, no cause found, fuses replaced and customer power restored. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.471 | 46.0404
5W150 | 829599 | CPCC | CPCC704802 | PP | WA | WALLA WALLA | BOWMAN | OH_320300_636330398 | 2011 | Before | 2011-05-09 23:52 | 2011-05-10 02:29 | 31 | 4870.617 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: A and C phase fuses open at pole 320300, serviceman patrolling the line. Patrolled Line, no cause found. Fuses replaced, customer power restored | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.471 | 46.0404
5W150 | 828141 | CPCC | CPCC705378 | PP | WA | WALLA WALLA | BOWMAN | BOW_CB5W150 | 2011 | Before | 2011-05-14 18:06 | 2011-05-14 18:06 | 0 | 0 | 1804 | 330.733 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: T&R | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.3614 | 46.0679
5W150 | 817977 | CPCC | CPCC677591 | PP | WA | WALLA WALLA | BOWMAN | TR_236260_593050188 | 2011 | Before | 2011-01-28 09:36 | 2011-01-28 10:42 | 4 | 265 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 236260 and it held, the cause was a squirrel, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 830633 | CPCC | CPCC704656 | PP | WA | WALLA WALLA | BOWMAN | OH_294161_636330486 | 2011 | Before | 2011-05-08 22:07 | 2011-05-09 02:20 | 8 | 2018.267 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Fuse had melted out at pole 294161, replaced fuse, restored customer power. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.4615 | 46.051
5W150 | 832220 | CPCC | CPCC704890 | PP | WA | WALLA WALLA | BOWMAN | OH_280360_636330418 | 2011 | Before | 2011-05-11 01:01 | 2011-05-11 04:18 | 54 | 10624.5 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD SUSPECTED, NO MORTALITY |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Blown line fuses. Serviceman is patrolling. Patrolled and did not find a cause. Serviceman suspects birds flying up the river. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.4506 | 46.0541
5W150 | 833899 | CPCC | CPCC702096 | PP | WA | WALLA WALLA | BOWMAN | TR_332600_636330444 | 2011 | Before | 2011-04-21 16:00 | 2011-04-21 16:41 | 1 | 41.217 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused transformer# 332600 and it held, the cause is unknown, customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 817440 | CPCC | CPCC675719 | PP | WA | WALLA WALLA | BOWMAN | OH_320300_636330398 | 2011 | Before | 2011-01-14 16:38 | 2011-01-14 17:39 | 18 | 1101.6 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | INTERFERENCE | VEHICLE ACCIDENT | POLE OH |  |  |  | PROSPER: Crew took outage on the tapline fuses at pole# 320300 to replace a carhit pole. Fuses installed, customer power restored. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.471 | 46.0404
5W150 | 811511 | CPCC | CPCC699720 | PP | WA | WALLA WALLA | BOWMAN | OH_294161_636330486 | 2011 | Before | 2011-04-01 06:36 | 2011-04-01 08:14 | 8 | 780.533 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD SUSPECTED, NO MORTALITY |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused the tapline fuses at pole# 294161 and they held, the cause was believed to be a bird but one was not found. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.4615 | 46.051
5W150 | 811961 | CPCC | CPCC700249 | PP | WA | WALLA WALLA | BOWMAN | TR_251202_209420371 | 2011 | Before | 2011-04-05 11:57 | 2011-04-05 12:57 | 8 | 472.4 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman replaced blown x-fmr fuse, cause was a squirrel. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 816906 | CPCC | CPCC675659 | PP | WA | WALLA WALLA | BOWMAN | OH_320300_636330398 | 2011 | Before | 2011-01-14 09:52 | 2011-01-14 17:39 | 13 | 6074.25 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | POLE OH |  |  |  | PROSPER: Crew needed to replace a pole that was hit by a car. Fuses in, customer power restored. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.471 | 46.0404
5W150 | 845577 | CPCC | CPCC723703 | PP | WA | WALLA WALLA | BOWMAN | TR_268502_302080233 | 2011 | Before | 2011-09-29 06:50 | 2011-09-29 08:03 | 3 | 218.75 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Deteriorated x-fmr fuse. Serviceman replaced fuse and it held. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2011-09-29 10:15 | COMPLETED |  | 2011-09-29 07:48 | 2011-09-29 08:08 | 2011-09-29 10:48 | -118.3923 | 46.0565
5W150 | 850308 | CPCC | CPCC725786 | PP | WA | WALLA WALLA | BOWMAN | OH_042900_20410349 | 2011 | Before | 2011-10-17 06:30 | 2011-10-17 10:51 | 1 | 260.833 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Crew needed to make repairs to the B/O underground primary between the open dip at pole# 042900 and transformer# 042880 | DISTRIBUTION | DEVICE | MANUAL | 2011-10-17 12:00 | COMPLETED |  | 2011-10-17 06:30 | 2011-10-17 10:51 | 2011-10-17 12:14 | -118.4464 | 46.0337
5W150 | 861413 | CPCC | CPCC732731 | PP | WA | WALLA WALLA | BOWMAN | OH_280201_636330256 | 2011 | Before | 2011-11-23 08:35 | 2011-11-23 13:25 | 3 | 870.65 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Crew needed to make repairs to the overhead primary that was taken down by a tree. Customers are back in full service. | DISTRIBUTION | DEVICE | MANUAL | 2011-11-23 13:00 | COMPLETED |  | 2011-11-23 08:35 | 2011-11-23 13:25 | 2011-11-23 17:46 | -118.4508 | 46.0523
5W150 | 858056 | CPCC | CPCC729536 | PP | WA | WALLA WALLA | BOWMAN | TR_268100_1540196545 | 2011 | Before | 2011-11-11 23:09 | 2011-11-12 02:23 | 1 | 193.733 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | POLE OH |  |  |  | SOURCE: 1 pole to the east of this location, crew to make repairs at at later date | DISTRIBUTION | CUSTOMER | AUTO | 2011-11-12 02:15 | COMPLETED |  | 2011-11-11 23:09 | 2011-11-12 02:23 | 2011-11-12 02:43 | -118.3926 | 46.0516
5W150 | 844458 | CPCC | CPCC717939 | PP | WA | WALLA WALLA | BOWMAN | TR_269509_302080231 | 2011 | Before | 2011-08-19 11:29 | 2011-08-19 13:13 | 1 | 103.8 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Serviceman made repairs to the overhead secondary neutral that was damaged by a squirrel, customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 843680 | CPCC | CPCC718689 | PP | WA | WALLA WALLA | BOWMAN | TR_334302_636330447 | 2011 | Before | 2011-08-25 11:40 | 2011-08-25 13:16 | 1 | 95.267 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: B/O secondary connectors at xfmr. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 858055 | CPCC | CPCC729542 | PP | WA | WALLA WALLA | BOWMAN | OH_268101_302080363 | 2011 | Before | 2011-11-11 23:54 | 2011-11-12 00:23 | 9 | 260.7 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | INTENTIONAL TO CLEAR TROUBLE | EQUIPMENT FAILURE | POLE FIRE | OTHER UG (EXPLAIN IN COMMENTS FIELD) |  |  |  | SOURCE: opened cut out to allow fire dept to put out pole fire | DISTRIBUTION | DEVICE | AUTO | 2011-11-12 03:00 | COMPLETED |  | 2011-11-11 23:54 | 2011-11-28 15:00 | 2011-11-12 02:18 | -118.392 | 46.0516
5W150 | 842422 | CPCC | CPCC719901 | PP | WA | WALLA WALLA | BOWMAN | OH_259002_1541013637 | 2011 | Before | 2011-08-31 16:42 | 2011-08-31 19:12 | 2 | 299.833 | 0 | 0 | 1 | Y | N | N | N | N |  | ENVIRONMENT | FIRE/SMOKE (NOT DUE TO FAULTS) |  |  | POLE OH |  |  |  | PROSPER: Gras fire in the area. Serviceman opened line fuses to de-energize line while needs crew to replace 3 damaged poles due to wild fire, attemtping fill crew(17:44)Repairs complete, power restored. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.4927 | 46.0498
5W150 | 837725 | CPCC | CPCC713325 | PP | WA | WALLA WALLA | BOWMAN | TR_268001_302080416 | 2011 | Before | 2011-07-21 12:02 | 2011-07-21 12:45 | 1 | 43.583 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 268001 and it held, the cause was a starling, customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 838202 | CPCC | CPCC723234 | PP | WA | WALLA WALLA | BOWMAN | TR_267303_1541013701 | 2011 | Before | 2011-09-25 11:20 | 2011-09-25 12:20 | 6 | 357.1 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | TRANSFORMER OH |  |  |  | PROSPER: Associated to outage 723248. Bad connectivity in Cadops. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 838205 | CPCC | CPCC723242 | PP | WA | WALLA WALLA | BOWMAN | TR_262001_302080356 | 2011 | Before | 2011-09-25 11:42 | 2011-09-25 12:20 | 1 | 38.4 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | TRANSFORMER OH |  |  |  | PROSPER: Associated to outage 723248. Bad connectivity in Cadops. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 838223 | CPCC | CPCC723247 | PP | WA | WALLA WALLA | BOWMAN | TR_268481_1540030645 | 2011 | Before | 2011-09-25 11:54 | 2011-09-25 12:20 | 6 | 158.8 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | TRANSFORMER OH |  |  |  | PROSPER: Associated to outage 723248. Bad connectivity in Cadops. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 838224 | CPCC | CPCC723248 | PP | WA | WALLA WALLA | BOWMAN | OH_266465_302080368 | 2011 | Before | 2011-09-25 11:20 | 2011-09-25 14:02 | 38 | 2492 | 0 | 0 | 2 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | TRANSFORMER OH |  |  |  | PROSPER: Blown line fuse and transformer fuse. Transformer needs to be replaced, cause was dquirrel. Repairs made and customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.3953 | 46.0552
5W150 | 837946 | CPCC | CPCC709793 | PP | WA | WALLA WALLA | BOWMAN | OH_329701_636330429 | 2011 | Before | 2011-06-22 04:25 | 2011-06-22 06:02 | 13 | 1268.367 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Two outside fuses blown at pole 329701, no cause found, serviceman will replace fuses. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.4508 | 46.046
5W150 | 837211 | CPCC | CPCC702972 | PP | WA | WALLA WALLA | BOWMAN | TR_230100_593050161 | 2011 | Before | 2011-04-25 12:56 | 2011-04-25 16:34 | 1 | 217.9 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Serviceman cleared the secondary service for now and will make repairs after the larger outages are restored. repairs made, outage restored | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W150 | 837218 | CPCC | CPCC702992 | PP | WA | WALLA WALLA | BOWMAN | OH_239305_593050178 | 2011 | Before | 2011-04-25 13:10 | 2011-04-25 15:54 | 15 | 2450.25 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: Crew needed to replace the B/O cutouts on pole# 239305 that were damaged by wind slapping the phases together. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.3887 | 46.0683
5W150 | 876669 | CPCC | CPCC743228 | PP | WA | WALLA WALLA | BOWMAN | TR_269800_302080242 | 2012 | Before | 2012-01-20 15:37 | 2012-01-20 16:24 | 1 | 47.183 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: Serviceman replaced b/o secondary connector. | DISTRIBUTION | CUSTOMER | AUTO | 2012-01-20 18:45 | COMPLETED |  | 2012-01-20 15:37 | 2012-01-20 16:24 | 2012-01-20 17:52 | -118.3907 | 46.0612
5W150 | 881847 | CPCC | CPCC747092 | PP | WA | WALLA WALLA | BOWMAN | TR_069801_20410251 | 2012 | Before | 2012-02-13 07:53 | 2012-02-13 08:50 | 1 | 56.9 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: Serviceman replaced the B/O secondary connector at the pole, customer is back in full service. | DISTRIBUTION | CUSTOMER | AUTO | 2012-02-13 11:00 | COMPLETED |  | 2012-02-13 07:53 | 2012-02-13 08:50 | 2012-02-13 09:31 | -118.4725 | 46.0325
5W150 | 876415 | CPCC | CPCC742989 | PP | WA | WALLA WALLA | BOWMAN | TR_269800_302080242 | 2012 | Before | 2012-01-20 06:51 | 2012-01-20 08:58 | 1 | 127.083 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: Serviceman replaced the B/O secondary connectors at the transformer, customer is back in full service. | DISTRIBUTION | CUSTOMER | AUTO | 2012-01-20 10:00 | COMPLETED |  | 2012-01-20 06:51 | 2012-01-20 08:58 | 2012-01-20 09:02 | -118.3907 | 46.0612
5W150 | 871166 | CPCC | CPCC737912 | PP | WA | WALLA WALLA | BOWMAN | OH_359902_369970321 | 2011 | Before | 2011-12-30 07:29 | 2011-12-30 08:18 | 82 | 3957.867 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CAP BANK B/O OH |  |  |  | SOURCE: Associate to outage# 737905. B/O mapping in cadops, mapping change made. B/O cap bank was the cause. | DISTRIBUTION | DEVICE | AUTO | 2011-12-30 10:45 | COMPLETED |  | 2011-12-30 07:43 | 2011-12-30 08:52 | 2011-12-30 10:56 | -118.3892 | 46.0491
5W150 | 863174 | CPCC | CPCC733866 | PP | WA | WALLA WALLA | BOWMAN | TR_274700_636330293 | 2011 | Before | 2011-12-01 13:30 | 2011-12-01 15:07 | 1 | 97.117 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman made repairs to the overhead secondary service that broke at the weatherhead, customer is back in full service. | DISTRIBUTION | CUSTOMER | AUTO | 2011-12-01 16:30 | COMPLETED |  | 2011-12-01 13:30 | 2011-12-01 15:07 | 2011-12-01 15:17 | -118.4212 | 46.0602
5W150 | 870799 | CPCC | CPCC737487 | PP | WA | WALLA WALLA | BOWMAN | OH_312100_636330271 | 2011 | Before | 2011-12-28 18:17 | 2011-12-28 21:26 | 8 | 1513.2 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: left message at 1819 replaced broken cut out | DISTRIBUTION | DEVICE | AUTO | 2011-12-28 21:30 | COMPLETED |  | 2011-12-28 18:17 | 2011-12-28 21:26 | 2011-12-28 23:16 | -118.4875 | 46.0368
5W150 | 895925 | CPCC | CPCC762423 | PP | WA | WALLA WALLA | BOWMAN | OH_266465_302080368 | 2012 | Before | 2012-03-30 18:58 | 2012-03-30 23:39 | 85 | 11763.433 | 0 | 0 | 3 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | POLE FIRE | POLE OH |  |  |  | SOURCE: See outage 762418 and 762419 for original outage. Serviceman took emergency outage due to pole fire. Open jumpers and refused picking up some of the customers. | DISTRIBUTION | DEVICE | MANUAL | 2012-03-31 | COMPLETED |  | 2012-03-30 18:58 | 2012-03-30 23:39 | 2012-03-31 01:05 | -118.3953 | 46.0552
5W150 | 902038 | CPCC | CPCC767041 | PP | WA | WALLA WALLA | BOWMAN | RC_263404_1540836522 | 2012 | Before | 2012-04-26 11:11 | 2012-04-26 12:34 | 458 | 33138.1 | 0 | 0 | 2 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman found locked open FR# 5W697, he patrolled the line and did not find a cause, closed on test and it held. | DISTRIBUTION | DEVICE | AUTO | 2012-04-26 14:30 | COMPLETED |  | 2012-04-26 11:22 | 2012-04-26 12:36 | 2012-04-26 14:30 | -118.4026 | 46.0564
5W150 | 902058 | CPCC | CPCC767059 | PP | WA | WALLA WALLA | BOWMAN | OH_366961_649900159 | 2012 | Before | 2012-04-26 12:48 | 2012-04-26 15:03 | 48 | 6462.4 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | POLE OH |  |  |  | SOURCE: Serviceman isolating a pole that caught fire, the pole feeds and irrigation bank that is not in use at this time. | DISTRIBUTION | DEVICE | AUTO | 2012-04-26 16:00 | COMPLETED |  | 2012-04-26 12:48 | 2012-04-26 15:03 | 2012-04-26 15:25 | -118.4997 | 46.048
5W150 | 902059 | CPCC | CPCC767067 | PP | WA | WALLA WALLA | BOWMAN | OH_366961_649900159 | 2012 | Before | 2012-04-26 14:02 | 2012-04-26 15:03 | 2 | 122.867 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | POLE FIRE | POLE OH |  |  |  | SOURCE: Serviceman took outage on the tapline fuse to isolate a pole that caught fire. pole feeds and irrigation bank that is not in use at this time | DISTRIBUTION | DEVICE | MANUAL | 2012-04-26 15:02 | COMPLETED |  | 2012-04-26 14:02 | 2012-04-26 15:03 | 2012-04-26 15:25 | -118.4997 | 46.048
5W150 | 895912 | CPCC | CPCC762447 | PP | WA | WALLA WALLA | BOWMAN | OH_266465_302080368 | 2012 | Before | 2012-03-30 22:04 | 2012-03-30 22:20 | 32 | 512 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | POLE FIRE | POLE OH |  |  |  | SOURCE: Tooke emergency outage to re-install jumpers and pick up all transformers but 1. See outage 762423. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-03-30 22:04 | 2012-03-30 22:20 | 2012-03-30 22:25 | -118.3953 | 46.0552
5W150 | 899999 | CPCC | CPCC765769 | PP | WA | WALLA WALLA | BOWMAN | OH_252100_209420349 | 2012 | Before | 2012-04-17 13:49 | 2012-04-17 15:56 | 36 | 4205.85 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Another journeyman needed to switch out the B/O underground primary between transformer# 252080 and transformer# 252081. Customers are back in full service. | DISTRIBUTION | DEVICE | AUTO | 2012-04-17 17:00 | COMPLETED |  | 2012-04-17 13:49 | 2012-04-17 15:56 | 2012-04-17 16:05 | -118.3844 | 46.0508
5W150 | 896246 | CPCC | CPCC763200 | PP | WA | WALLA WALLA | BOWMAN | TR_268600_302080225 | 2012 | Before | 2012-03-31 21:57 | 2012-03-31 22:49 | 1 | 51.833 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: Bad order connectors, replaced and customer is back on. | DISTRIBUTION | CUSTOMER | AUTO | 2012-04-01 01:00 | COMPLETED |  | 2012-03-31 21:57 | 2012-03-31 22:49 | 2012-04-01 00:05 | -118.3917 | 46.0582
5W150 | 902822 | CPCC | CPCC767474 | PP | WA | WALLA WALLA | BOWMAN | OH_277502_636330291 | 2012 | Before | 2012-04-29 22:32 | 2012-04-30 00:39 | 16 | 2034.933 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: refused | DISTRIBUTION | DEVICE | AUTO | 2012-04-30 01:45 | COMPLETED |  | 2012-04-29 22:32 | 2012-04-30 00:39 | 2012-04-30 03:45 | -118.4146 | 46.0566
5W150 | 904928 | CPCC | CPCC768828 | PP | WA | WALLA WALLA | BOWMAN | TR_269101_302080406 | 2012 | Before | 2012-05-09 10:30 | 2012-05-09 12:16 | 1 | 106.467 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | CONNECTOR OH |  |  |  | SOURCE: serviceman stated that a squirrel chewed through the neutral causing the connector to fall out, all customers are back in service | DISTRIBUTION | CUSTOMER | AUTO | 2012-05-09 13:30 | COMPLETED |  | 2012-05-09 10:30 | 2012-05-09 12:16 | 2012-05-09 14:06 | -118.3897 | 46.0516
5W150 | 900311 | CPCC | CPCC765889 | PP | WA | WALLA WALLA | BOWMAN | OH_364901_649900155 | 2012 | Before | 2012-04-19 04:49 | 2012-04-19 07:11 | 21 | 2989 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: could have been a limb no conformation. | DISTRIBUTION | DEVICE | AUTO | 2012-04-19 08:00 | COMPLETED |  | 2012-04-19 04:49 | 2012-04-19 07:11 | 2012-04-19 07:15 | -118.5046 | 46.0478
5W150 | 900528 | CPCC | CPCC765945 | PP | WA | WALLA WALLA | BOWMAN | OH_358800_1540858501 | 2012 | Before | 2012-04-20 07:12 | 2012-04-20 08:33 | 7 | 571.667 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (PROTECTED SPECIES) (BMTS) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman refused the tapline fuse at pole# 358800 and it held, the cause was a tree limb. PROSPER: protected bird - BMTS 9029 - per Environmental | DISTRIBUTION | DEVICE | AUTO | 2012-04-20 10:15 | COMPLETED |  | 2012-04-20 07:12 | 2012-05-21 09:03 | 2012-04-20 13:25 | -118.5153 | 46.0469
5W150 | 909392 | CPCC | CPCC771303 | PP | WA | WALLA WALLA | BOWMAN | OH_320300_636330398 | 2012 | Before | 2012-05-26 21:31 | 2012-05-26 23:57 | 28 | 4088.933 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman patrolled line and closed on test. Fuse held. outage restored. | DISTRIBUTION | DEVICE | AUTO | 2012-05-27 00:30 | COMPLETED |  | 2012-05-26 21:31 | 2012-05-26 23:57 | 2012-05-27 05:35 | -118.471 | 46.0404
5W150 | 900691 | CPCC | CPCC766032 | PP | WA | WALLA WALLA | BOWMAN | OH_280201_636330256 | 2012 | Before | 2012-04-21 05:55 | 2012-04-21 07:52 | 4 | 469.133 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (PROTECTED SPECIES) (BMTS) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman reports 2 outer phases blown at pole #280201, Cause pelican, re-fused and held, power restored | DISTRIBUTION | DEVICE | AUTO | 2012-04-21 09:00 | COMPLETED |  | 2012-04-21 05:55 | 2012-04-21 07:52 | 2012-04-21 15:00 | -118.4508 | 46.0523
5W150 | 904774 | CPCC | CPCC768794 | PP | WA | WALLA WALLA | BOWMAN | OH_364901_649900155 | 2012 | Before | 2012-05-09 01:53 | 2012-05-09 02:59 | 14 | 919.333 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: refused | DISTRIBUTION | DEVICE | AUTO | 2012-05-09 05:00 | COMPLETED |  | 2012-05-09 01:53 | 2012-05-09 02:59 | 2012-05-09 03:25 | -118.5046 | 46.0478
5W150 | 890820 | CPCC | CPCC756551 | PP | WA | WALLA WALLA | BOWMAN | OH_252100_209420349 | 2012 | Before | 2012-03-15 23:50 | 2012-03-16 04:15 | 36 | 9535.517 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Serviceman arrived and found b/o UG needs 4 man crew. Crew located and isolated fault, will make repairs and return to normal. customers are in power. | DISTRIBUTION | DEVICE | AUTO | 2012-03-16 03:00 | COMPLETED |  | 2012-03-15 23:50 | 2012-03-16 04:15 | 2012-03-16 06:30 | -118.3844 | 46.0508
5W150 | 897808 | CPCC | CPCC764472 | PP | WA | WALLA WALLA | BOWMAN | TR_261280_302080205 | 2012 | Before | 2012-04-06 16:13 | 2012-04-06 17:38 | 1 | 84.75 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: changed conns at weather head | DISTRIBUTION | CUSTOMER | AUTO | 2012-04-06 19:15 | COMPLETED |  | 2012-04-06 16:13 | 2012-04-06 17:38 | 2012-04-06 17:50 | -118.4065 | 46.0527
5W150 | 907602 | CPCC | CPCC770468 | PP | WA | WALLA WALLA | BOWMAN | TR_266404_302080389 | 2012 | Before | 2012-05-20 12:54 | 2012-05-20 13:50 | 4 | 226.133 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: serviceman arrived and found blown fuse from squierrel replaced it outage restored. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-05-20 16:00 | COMPLETED |  | 2012-05-20 12:54 | 2012-05-20 13:50 | 2012-05-20 18:18 | -118.3958 | 46.0564
5W150 | 909246 | CPCC | CPCC771273 | PP | WA | WALLA WALLA | BOWMAN | OH_320300_636330398 | 2012 | Before | 2012-05-26 11:16 | 2012-05-26 13:09 | 28 | 3174.733 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman reports fuse blown , patroling line, no cause found , replaced fuse , it held power restored | DISTRIBUTION | DEVICE | AUTO | 2012-05-26 14:15 | COMPLETED |  | 2012-05-26 11:16 | 2012-05-26 13:09 | 2012-05-26 18:40 | -118.471 | 46.0404
5W150 | 917188 | CPCC | CPCC775546 | PP | WA | WALLA WALLA | BOWMAN | OH_280360_636330418 | 2012 | Before | 2012-06-26 13:44 | 2012-06-26 13:50 | 76 | 475 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | INTENTIONAL TO CLEAR TROUBLE | ANIMALS | ANIMALS | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Crew took a quick outage to remove an osprey nest from the top of a pole. | DISTRIBUTION | DEVICE | MANUAL | 2012-06-26 14:01 | COMPLETED |  | 2012-06-26 13:44 | 2012-07-03 14:08 | 2012-06-26 14:02 | -118.4506 | 46.0541
5W150 | 920585 | CPCC | CPCC777231 | PP | WA | WALLA WALLA | BOWMAN | OH_235161_593050199 | 2012 | Before | 2012-07-08 21:43 | 2012-07-09 02:05 | 23 | 2924.367 | 0 | 0 | 2 | Y | N | N | N | Y | 2012-07-08 to 2012-07-09 WA All | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman found open l;ine fuse, lifted tap to isolate line down due to tree closed fuse power restored to most customers remainder needs crew. | DISTRIBUTION | DEVICE | MANUAL | 2012-07-09 05:45 | COMPLETED |  | 2012-07-08 21:43 | 2012-07-09 02:05 | 2012-07-09 02:52 | -118.3978 | 46.0653
5W150 | 923138 | CPCC | CPCC778840 | PP | WA | WALLA WALLA | BOWMAN | OH_318300_636330237 | 2012 | Before | 2012-07-13 22:16 | 2012-07-14 05:43 | 1 | 447.483 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | TRANSFORMER PADMOUNT/SUBMERSIBLE UG |  |  |  | SOURCE: serviceman found dip fuse open, cause unknown at this time, crew working on outage 778827 replaced UG transformer | DISTRIBUTION | DEVICE | MANUAL | 2012-07-14 07:35 | COMPLETED |  | 2012-07-13 22:16 | 2012-07-14 05:43 | 2012-07-14 05:46 | -118.4751 | 46.0398
5W150 | 923668 | CPCC | CPCC779110 | PP | WA | WALLA WALLA | BOWMAN | TR_274400_649900241 | 2012 | Before | 2012-07-15 11:23 | 2012-07-15 12:44 | 1 | 80.433 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: refuse transformer | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-07-15 14:30 | COMPLETED |  | 2012-07-15 11:23 | 2012-07-15 12:44 | 2012-07-15 13:31 | -118.5463 | 46.0554
5W150 | 929607 | CPCC | CPCC782110 | PP | WA | WALLA WALLA | BOWMAN | BOW_CB5W150 | 2012 | Before | 2012-08-03 00:38 | 2012-08-03 00:38 | 0 | 0 | 1729 | 345.8 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | SOURCE: T&R due to B/O xfrmr | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-08-03 00:38 | 2012-08-03 00:38 | 2012-08-03 06:30 | -118.3614 | 46.0679
5W150 | 930823 | CPCC | CPCC783264 | PP | WA | WALLA WALLA | BOWMAN | TR_277703_636330289 | 2012 | Before | 2012-08-07 08:19 | 2012-08-07 08:54 | 3 | 104.3 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: serviceman refused the cutout, customers are back in service (starling) | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-08-07 11:30 | COMPLETED |  | 2012-08-07 08:19 | 2012-08-07 08:54 | 2012-08-07 09:00 | -118.4152 | 46.0594
5W150 | 926040 | CPCC | CPCC780591 | PP | WA | WALLA WALLA | BOWMAN | OH_312100_636330271 | 2012 | Before | 2012-07-22 08:08 | 2012-07-22 14:15 | 7 | 2565.617 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: waiting for crew to make repairs Crew tested cable & refused, no cause found | DISTRIBUTION | DEVICE | MANUAL | 2012-07-22 16:15 | COMPLETED |  | 2012-07-22 08:08 | 2012-07-27 11:04 | 2012-07-22 14:16 | -118.4875 | 46.0368
5W150 | 913067 | CPCC | CPCC773312 | PP | WA | WALLA WALLA | BOWMAN | TR_268504_302080232 | 2012 | Before | 2012-06-10 08:17 | 2012-06-10 09:03 | 4 | 185.333 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman arrived and found open fuse will investigate and report. power restored. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-06-10 11:30 | COMPLETED |  | 2012-06-10 08:17 | 2012-06-10 09:03 | 2012-06-10 18:05 | -118.3915 | 46.0565
5W150 | 929265 | CPCC | CPCC781880 | PP | WA | WALLA WALLA | BOWMAN | TR_253900_209420291 | 2012 | Before | 2012-08-01 19:32 | 2012-08-01 22:38 | 2 | 372.433 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD SUSPECTED, NO MORTALITY |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman arrived and found open xfrmr fuse, replaced and restored power. bird caused. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-08-01 22:45 | COMPLETED |  | 2012-08-01 19:32 | 2012-08-08 10:58 | 2012-08-02 06:15 | -118.3821 | 46.0632
5W150 | 920588 | CPCC | CPCC777129 | PP | WA | WALLA WALLA | BOWMAN | TR_251800_209420293 | 2012 | Before | 2012-07-08 21:06 | 2012-07-09 01:28 | 4 | 1048.6 | 0 | 0 | 1 | Y | N | N | N | Y | 2012-07-08 to 2012-07-09 WA All | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Serviceman arrived and found broken cutout, replaced it and restored power | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2012-07-09 04:15 | COMPLETED |  | 2012-07-08 21:06 | 2012-07-09 01:28 | 2012-07-09 02:52 | -118.3857 | 46.0612
5W150 | 911133 | CPCC | CPCC772071 | PP | WA | WALLA WALLA | BOWMAN | Line Cut-63088 | 2012 | Before | 2012-06-04 07:27 | 2012-06-04 09:13 | 1810 | 191317 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF SUBSTATION | ANIMALS | ANIMALS | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Circuit switcher locked out at sub due to a fault on circuit 5W154. Breaker did not opperate correctly and circuit switcher locked out. PROSPER: magpie | DISTRIBUTION | DEVICE | AUTO | 2012-06-04 10:30 | COMPLETED |  | 2012-06-04 07:30 | 2012-06-12 08:43 | 2012-06-04 10:45 | -118.3606 | 46.0683
5W150 | 917861 | CPCC | CPCC775781 | PP | WA | WALLA WALLA | BOWMAN | TR_250109_209420376 | 2012 | Before | 2012-06-28 19:44 | 2012-06-28 20:24 | 35 | 1426.25 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman arrived and found squirrel caused blown xfrmr fuse. refused outage restored. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-06-28 22:45 | COMPLETED |  | 2012-06-28 19:44 | 2012-06-28 20:24 | 2012-06-29 05:58 | -118.3877 | 46.0517
5W150 | 912321 | CPCC | CPCC772900 | PP | WA | WALLA WALLA | BOWMAN | TR_328100_636330273 | 2012 | Before | 2012-06-06 18:47 | 2012-06-06 20:12 | 1 | 84.95 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: Serviceman found burned connector will make repairs and restore power.repairs made outage restored | DISTRIBUTION | CUSTOMER | AUTO | 2012-06-06 22:00 | COMPLETED |  | 2012-06-06 18:47 | 2012-06-06 20:12 | 2012-06-07 06:50 | -118.4534 | 46.037
5W150 | 911428 | CPCC | CPCC772454 | PP | WA | WALLA WALLA | BOWMAN | OH_280360_636330418 | 2012 | Before | 2012-06-04 16:20 | 2012-06-04 19:59 | 29 | 6352.183 | 0 | 0 | 2 | Y | N | N | N | N |  | ANIMALS | BIRD NEST (BMTS) |  |  | CROSS ARM OH |  |  |  | SOURCE: Osprey nest started a fire and burnt up cross arms on pole which caused line fuse to blow. Repairs made outage restored. | DISTRIBUTION | DEVICE | MANUAL | 2012-06-04 23:30 | COMPLETED |  | 2012-06-04 16:20 | 2012-06-08 10:48 | 2012-06-04 21:12 | -118.4506 | 46.0541
5W150 | 923086 | CPCC | CPCC778827 | PP | WA | WALLA WALLA | BOWMAN | OH_366961_649900159 | 2012 | Before | 2012-07-13 19:55 | 2012-07-14 01:54 | 41 | 8900.183 | 0 | 0 | 3 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | TRANSFORMER OH |  |  |  | SOURCE: Crew to make repairs | DISTRIBUTION | DEVICE | MANUAL | 2012-07-14 06:30 | COMPLETED |  | 2012-07-13 20:01 | 2012-07-14 01:54 | 2012-07-14 01:57 | -118.4997 | 46.048
5W150 | 929608 | CPCC | CPCC782111 | PP | WA | WALLA WALLA | BOWMAN | TR_242300_593050254 | 2012 | Before | 2012-08-03 00:52 | 2012-08-03 06:26 | 2 | 667.767 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | SOURCE: Serviceman arrived and needs 3 man crew. B/O xfrmr. Crew made repairs outage resolved | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2012-08-03 06:30 | COMPLETED |  | 2012-08-03 00:52 | 2012-08-03 06:26 | 2012-08-03 06:30 | -118.3833 | 46.0686
5W150 | 911429 | CPCC | CPCC772471 | PP | WA | WALLA WALLA | BOWMAN | OH_280360_636330418 | 2012 | Before | 2012-06-04 18:53 | 2012-06-04 19:59 | 49 | 3247.883 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | ANIMALS | ANIMALS | CROSS ARM OH |  |  |  | SOURCE: Associated with outage 772454, took emergancy outage to make repairs to pole PROSPER: bird nest | DISTRIBUTION | DEVICE | AUTO | 2012-06-04 22:00 | COMPLETED |  | 2012-06-04 18:53 | 2012-06-11 13:40 | 2012-06-04 21:13 | -118.4506 | 46.0541
5W150 | 912978 | CPCC | CPCC773307 | PP | WA | WALLA WALLA | BOWMAN | TR_194302_825860498 | 2012 | Before | 2012-06-10 06:57 | 2012-06-10 07:59 | 5 | 307.417 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman arrived and found blown xfrmr fuse due to starling. Closed fuse in outage restored | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-06-10 10:00 | COMPLETED |  | 2012-06-10 06:57 | 2012-06-10 07:59 | 2012-06-10 08:35 | -118.3575 | 46.0687
5W150 | 913577 | CPCC | CPCC773534 | PP | WA | WALLA WALLA | BOWMAN | TR_264401_302080354 | 2012 | Before | 2012-06-12 23:41 | 2012-06-13 01:03 | 1 | 82.35 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: Bad order connector at transformer. Replaced and customer is back in full power. | DISTRIBUTION | CUSTOMER | AUTO | 2012-06-13 02:45 | COMPLETED |  | 2012-06-12 23:41 | 2012-06-13 01:03 | 2012-06-13 01:40 | -118.3991 | 46.0556
5W150 | 1303681 | CPCC | CPCC785561 | PP | WA | WALLA WALLA | BOWMAN | OH_252100_209420349 | 2012 | Before | 2012-08-23 07:57 | 2012-08-23 13:06 | 36 | 11142.867 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Crew switched the B/O underground primary between transformer# 253080 and transformer# 252181, customers are back in full service. | DISTRIBUTION | DEVICE | MANUAL | 2012-08-23 14:00 | COMPLETED |  | 2012-08-23 07:57 | 2012-08-23 13:06 | 2012-08-23 13:15 | -118.3844 | 46.0508
5W150 | 1307481 | CPCC | CPCC787054 | PP | WA | WALLA WALLA | BOWMAN | OH_250201_302080361 | 2012 | Before | 2012-09-07 09:36 | 2012-09-07 14:26 | 197 | 43125.278 | 0 | 0 | 4 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Crew needed to make repairs to the B/O underground primary and the overhead primary that durnt down due to the fault current. PROSPER: added customers from CPCC787072 | DISTRIBUTION | DEVICE | MANUAL | 2012-09-07 16:45 | COMPLETED |  | 2012-09-07 09:42 | 2012-09-13 13:25 | 2012-09-07 15:25 | -118.3885 | 46.0529
5W150 | 1313393 | CPCC | CPCC790637 | PP | WA | WALLA WALLA | BOWMAN | TR_250109_209420376 | 2012 | Before | 2012-10-06 08:54 | 2012-10-06 10:32 | 35 | 3422.417 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman found blown xfmr fuse, is investigating cause. Serviceman found squrril as the cause. Is working on access for refuse. Refused & restored power | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-10-06 12:00 | COMPLETED |  | 2012-10-06 08:54 | 2012-10-06 10:41 | 2012-10-06 10:45 | -118.3877 | 46.0517
5W150 | 1327551 | CPCC | CPCC801404 | PP | WA | WALLA WALLA | BOWMAN | TR_357380_1540723534 | 2012 | Before | 2012-11-28 07:52 | 2012-11-28 10:27 | 1 | 154.967 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | SOURCE: Serviceman replaced the B/O meter, customer is back in full service. | DISTRIBUTION | CUSTOMER | AUTO | 2012-11-28 11:00 | COMPLETED |  | 2012-11-28 07:52 | 2012-11-28 10:37 | 2012-11-28 11:12 | -118.5191 | 46.0402
5W150 | 1313680 | CPCC | CPCC790879 | PP | WA | WALLA WALLA | BOWMAN | TR_250109_209420376 | 2012 | Before | 2012-10-08 08:51 | 2012-10-08 09:33 | 35 | 1499.167 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: outage due to squirrel, serviceman refused the cutout, customers are back in service | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-10-08 12:00 | COMPLETED |  | 2012-10-08 08:51 | 2012-10-08 09:33 | 2012-10-08 10:26 | -118.3877 | 46.0517
5W150 | 1318637 | CPCC | CPCC794495 | PP | WA | WALLA WALLA | BOWMAN | TR_262102_302080332 | 2012 | Before | 2012-10-26 14:09 | 2012-10-26 16:25 | 1 | 135.867 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman cut the overhead secondary service in the clear until the customer makes repairs to their equipment and call back for a reconnect. | DISTRIBUTION | CUSTOMER | AUTO | 2012-10-26 17:15 | COMPLETED |  | 2012-10-26 14:09 | 2012-10-26 16:25 | 2012-10-26 16:50 | -118.4033 | 46.052
5W150 | 1317737 | CPCC | CPCC794002 | PP | WA | WALLA WALLA | BOWMAN | OH_263405_302080343 | 2012 | Before | 2012-10-23 05:30 | 2012-10-23 12:00 | 5 | 1949.917 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER PADMOUNT/SUBMERSIBLE UG |  |  |  | SOURCE: crew complete, customers are back in service | DISTRIBUTION | DEVICE | MANUAL | 2012-10-23 13:30 | COMPLETED |  | 2012-10-23 05:30 | 2012-10-23 12:46 | 2012-10-23 17:36 | -118.4018 | 46.0564
5W150 | 1315810 | CPCC | CPCC792792 | PP | WA | WALLA WALLA | BOWMAN | OH_359600_1540723560 | 2012 | Before | 2012-10-16 08:24 | 2012-10-16 13:55 | 5 | 1655.083 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TERMINATION UG |  |  |  | SOURCE: Crew needed to make repairs to the B/O underground termination on dip pole# 359600. | DISTRIBUTION | DEVICE | MANUAL | 2012-10-16 14:00 | COMPLETED |  | 2012-10-16 08:24 | 2012-10-16 13:55 | 2012-10-16 14:45 | -118.5153 | 46.0435
5W150 | 1316615 | CPCC | CPCC793374 | PP | WA | WALLA WALLA | BOWMAN | TR_251105_209420364 | 2012 | Before | 2012-10-19 09:59 | 2012-10-19 10:30 | 10 | 305.667 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman refused transformer# 251105 and it held, the cause was a squirrel, customers are back in full service. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-10-19 13:00 | COMPLETED |  | 2012-10-19 09:59 | 2012-10-19 10:30 | 2012-10-19 10:45 | -118.385 | 46.0513
5W150 | 1315315 | CPCC | CPCC792303 | PP | WA | WALLA WALLA | BOWMAN | TR_192317_825860478 | 2012 | Before | 2012-10-15 08:22 | 2012-10-15 10:44 | 6 | 852.4 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | TRANSFORMER OH |  |  |  | SOURCE: Crew needed to replace the transformer and cutout on pole# 192317 that was damaged by a squirrel. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-10-15 11:30 | COMPLETED |  | 2012-10-15 08:30 | 2012-10-15 10:44 | 2012-10-15 10:51 | -118.3628 | 46.0684
5W150 | 1314941 | CPCC | CPCC791866 | PP | WA | WALLA WALLA | BOWMAN | TR_320001_636330396 | 2012 | Before | 2012-10-13 07:16 | 2012-10-13 11:01 | 1 | 225.733 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Bad order cutout, replaced and customer is back on. | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2012-10-13 12:15 | COMPLETED |  | 2012-10-13 07:16 | 2012-10-13 11:01 | 2012-10-13 11:06 | -118.4718 | 46.0353
5W150 | 1315274 | CPCC | CPCC792299 | PP | WA | WALLA WALLA | BOWMAN | BOW_CB5W150 | 2012 | Before | 2012-10-15 08:06 | 2012-10-15 08:07 | 0 | 0 | 1733 | 462.133 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | TRANSFORMER OH |  |  |  | SOURCE: T & R, the cause was a squirrel that got on top of a transformer and damaged it. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-10-15 08:06 | 2012-10-15 08:07 | 2012-10-15 08:51 | -118.3614 | 46.0679
5W150 | 1320766 | CPCC | CPCC795946 | PP | WA | WALLA WALLA | BOWMAN | TR_242202_593050256 | 2012 | Before | 2012-11-07 12:11 | 2012-11-07 15:26 | 3 | 584.3 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman found an open transformer fuse, due to a squirrel | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-11-07 15:15 | COMPLETED |  | 2012-11-07 12:11 | 2012-11-07 15:26 | 2012-11-07 15:30 | -118.383 | 46.0675
5W150 | 1315386 | CPCC | CPCC792336 | PP | WA | WALLA WALLA | BOWMAN | OH_239260_593050183 | 2012 | Before | 2012-10-15 10:59 | 2012-10-15 13:23 | 56 | 8037.867 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Crew needed to make repairs the overhead primary that was taken down by a tree limb. Customers are back in full service. | DISTRIBUTION | DEVICE | AUTO | 2012-10-15 14:15 | COMPLETED |  | 2012-10-15 11:15 | 2012-10-15 13:23 | 2012-10-15 13:36 | -118.3905 | 46.0678
5W150 | 1350541 | CPCC | CPCC823329 | PP | WA | WALLA WALLA | BOWMAN | TR_310203_636330368 | 2013 | Before | 2013-03-12 03:32 | 2013-03-12 04:22 | 1 | 49.717 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman found blown xfmr fuse, no cause. Refused & restored | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-03-12 06:45 | COMPLETED |  | 2013-03-12 03:32 | 2013-03-12 04:22 | 2013-03-12 04:25 | -118.4905 | 46.0381
5W150 | 1350199 | CPCC | CPCC823017 | PP | WA | WALLA WALLA | BOWMAN | OH_230240_593050166 | 2013 | Before | 2013-03-09 19:30 | 2013-03-10 04:15 | 2 | 930 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: This outage is replacement for mistakenly completed outage #823014. 3 man crew to be called. Crew mobilized. Crew completed repairs, restored power. | DISTRIBUTION | DEVICE | MANUAL | 2013-03-10 03:05 | COMPLETED |  | 2013-03-09 19:30 | 2013-03-10 04:45 | 2013-03-10 04:50 | -118.408 | 46.0676
5W150 | 1351405 | CPCC | CPCC823739 | PP | WA | WALLA WALLA | BOWMAN | TR_320001_636330396 | 2013 | Before | 2013-03-17 00:16 | 2013-03-17 06:17 | 1 | 361.333 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | POLE OH |  |  |  | SOURCE: crew to make temp repairs - pole # 320001 | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2013-03-17 00:16 | 2013-03-17 06:17 | 2013-03-17 06:19 | -118.4718 | 46.0353
5W150 | 1349761 | CPCC | CPCC822813 | PP | WA | WALLA WALLA | BOWMAN | OH_230240_593050166 | 2013 | Before | 2013-03-07 19:37 | 2013-03-08 00:11 | 2 | 547.533 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown dip fuse, bad order UG. Crew tested UG and it tested good. Refused and customers are back on. | DISTRIBUTION | DEVICE | MANUAL | 2013-03-08 02:00 | COMPLETED |  | 2013-03-07 19:37 | 2013-03-08 00:11 | 2013-03-08 08:35 | -118.408 | 46.0676
5W150 | 1350603 | CPCC | CPCC823333 | PP | WA | WALLA WALLA | BOWMAN | TR_292100_636330480 | 2013 | Before | 2013-03-12 08:01 | 2013-03-12 08:42 | 1 | 41.017 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD SUSPECTED, NO MORTALITY |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman refused transformer# 292100 and it held, the cause was believed to be a bird but one was not found. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-03-12 11:15 | COMPLETED |  | 2013-03-12 08:01 | 2013-03-14 11:13 | 2013-03-12 11:05 | -118.4666 | 46.0516
5W150 | 1351421 | CPCC | CPCC823760 | PP | WA | WALLA WALLA | BOWMAN | OH_239260_593050183 | 2013 | Before | 2013-03-17 02:32 | 2013-03-17 07:15 | 70 | 6762 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | POLE OH |  |  |  | SOURCE: crew to replace pole # 230001. Crew completed pole replacement. | DISTRIBUTION | DEVICE | AUTO | 2013-03-17 05:45 | COMPLETED |  | 2013-03-17 02:32 | 2013-03-17 07:17 | 2013-03-17 07:22 | -118.3905 | 46.0678
5W150 | 1353220 | CPCC | CPCC824799 | PP | WA | WALLA WALLA | BOWMAN | OH_364901_649900155 | 2013 | Before | 2013-03-25 10:29 | 2013-03-25 11:50 | 8 | 648.664 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (PROTECTED SPECIES) (BMTS) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman reports open b phase fuse on pole 364901, caused by goose in line, refused and it held, power restored PROSPER: Added customer from CPCC824755. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2013-03-25 10:29 | 2013-03-26 08:55 | 2013-03-25 12:05 | -118.5046 | 46.0478
5W150 | 1372237 | CPCC | CPCC836865 | PP | WA | WALLA WALLA | BOWMAN | TR_237001_593050204 | 2013 | Before | 2013-06-13 06:13 | 2013-06-13 07:19 | 3 | 199.3 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman refused transformer# 237001 and it held, the cause is unknown, pump is back in full service. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-06-13 09:15 | COMPLETED |  | 2013-06-13 06:13 | 2013-06-13 07:19 | 2013-06-13 08:36 | -118.3945 | 46.0639
5W150 | 1368275 | CPCC | CPCC834544 | PP | WA | WALLA WALLA | BOWMAN | OH_242201_1541062454 | 2013 | Before | 2013-05-28 08:18 | 2013-05-28 09:05 | 6 | 283.3 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman refused the tapline fuse at pole# 242201 and it held, the cause is unknown, customers are back in full service. | DISTRIBUTION | DEVICE | AUTO | 2013-05-28 11:30 | COMPLETED |  | 2013-05-28 08:18 | 2013-05-28 09:43 | 2013-05-28 09:46 | -118.383 | 46.0677
5W150 | 1387347 | CPCC | CPCC844259 | PP | WA | WALLA WALLA | BOWMAN | Line Cut-77002 | 2013 | Before | 2013-07-31 13:33 | 2013-07-31 18:24 | 10 | 2904.667 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | POLE OH |  |  |  | SOURCE: Crew needed to replace a pole that rotted and fell over. Repairs made and customers are back on. | DISTRIBUTION | DEVICE | MANUAL | 2013-07-31 19:30 | COMPLETED |  | 2013-07-31 13:33 | 2013-07-31 18:24 | 2013-07-31 18:51 | -118.3869 | 46.0541
5W150 | 1380797 | CPCC | CPCC841171 | PP | WA | WALLA WALLA | BOWMAN | Line Cut-76352 | 2013 | Before | 2013-07-10 18:09 | 2013-07-10 23:30 | 7 | 1105.283 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER PADMOUNT/SUBMERSIBLE UG |  |  |  | SOURCE: Serviceman found blown fuse o0n fp-360900. will patrol and try to determine cause. found blown dip, isolated dip and will call and report when line fuse is in. Crew replaced bushing on xfrmr and elbow and restored power. | DISTRIBUTION | DEVICE | MANUAL | 2013-07-10 21:15 | COMPLETED |  | 2013-07-10 18:09 | 2013-07-10 23:30 | 2013-07-11 00:06 | -118.3882 | 46.0491
5W150 | 1388068 | CPCC | CPCC844544 | PP | WA | WALLA WALLA | BOWMAN | OH_364901_649900155 | 2013 | Before | 2013-08-03 03:12 | 2013-08-03 07:23 | 21 | 5268.55 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Blown line fuse, 2nd man needed to patrol. Wire down, crew needed. Repairs made, no cause found as to why line came down. | DISTRIBUTION | DEVICE | MANUAL | 2013-08-03 10:30 | COMPLETED |  | 2013-08-03 03:12 | 2013-08-03 07:31 | 2013-08-03 07:36 | -118.5046 | 46.0478
5W150 | 1400597 | CPCC | CPCC852202 | PP | WA | WALLA WALLA | BOWMAN | BOW_CB5W150 | 2013 | Before | 2013-09-05 17:24 | 2013-09-05 17:25 | 0 | 0 | 1830 | 396.5 | 1 | Y | N | N | N | Y | 2013-09-05 to 2013-09-06 WA All | WEATHER | LIGHTNING |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: T&R due to lightning | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2013-09-05 17:24 | 2013-09-05 17:25 | 2013-09-06 05:27 | -118.3614 | 46.0679
5W150 | 1400598 | CPCC | CPCC852201 | PP | WA | WALLA WALLA | BOWMAN | BOW_CB5W150 | 2013 | Before | 2013-09-05 17:24 | 2013-09-05 17:24 | 0 | 0 | 1830 | 366 | 1 | Y | N | N | N | Y | 2013-09-05 to 2013-09-06 WA All | WEATHER | LIGHTNING |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: T&R due to lightning | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2013-09-05 17:24 | 2013-09-05 17:24 | 2013-09-06 05:27 | -118.3614 | 46.0679
5W150 | 1398800 | CPCC | CPCC850890 | PP | WA | WALLA WALLA | BOWMAN | TR_277260_649900240 | 2013 | Before | 2013-08-30 11:18 | 2013-08-30 13:05 | 1 | 107.05 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman refused transformer# 277260 and it held, the cause is unknown. Customers are back in full service. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-08-30 14:30 | COMPLETED |  | 2013-08-30 11:18 | 2013-08-30 13:05 | 2013-08-30 17:01 | -118.5392 | 46.0534
5W150 | 1388067 | CPCC | CPCC844545 | PP | WA | WALLA WALLA | BOWMAN | OH_364901_649900155 | 2013 | Before | 2013-08-03 04:22 | 2013-08-03 07:23 | 0 | 0 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | B/O EQUIPMENT | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Took emergency outage to make repairs to wire down. See outage 844544 for original call. | DISTRIBUTION | DEVICE | MANUAL | 2013-08-03 10:30 | COMPLETED |  | 2013-08-03 04:22 | 2013-08-03 07:31 | 2013-08-03 07:36 | -118.5046 | 46.0478
5W150 | 1397268 | CPCC | CPCC849963 | PP | WA | WALLA WALLA | BOWMAN | TR_064901_1540513131 | 2013 | Before | 2013-08-25 19:14 | 2013-08-25 23:07 | 1 | 233.183 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: serviceman refused the cutout and customers are back in service | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-08-25 22:15 | COMPLETED |  | 2013-08-25 19:14 | 2013-08-25 23:07 | 2013-08-26 00:41 | -118.4837 | 46.0336
5W150 | 1376803 | CPCC | CPCC839351 | PP | WA | WALLA WALLA | BOWMAN | OH_252100_209420349 | 2013 | Before | 2013-06-30 03:44 | 2013-06-30 07:35 | 28 | 6238.867 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: bad pri UG, crew to make repairs. Crew isolated bad sect, closed alternate loop and restored power | DISTRIBUTION | DEVICE | MANUAL | 2013-06-30 09:00 | COMPLETED |  | 2013-06-30 03:47 | 2013-06-30 07:41 | 2013-06-30 07:56 | -118.3844 | 46.0508
5W150 | 1403881 | CPCC | CPCC855162 | PP | WA | WALLA WALLA | BOWMAN | TR_340500_636330468 | 2013 | Before | 2013-09-15 21:29 | 2013-09-16 04:04 | 1 | 394.817 | 0 | 0 | 1 | Y | N | N | N | Y | 2013-09-15 to 2013-09-15 WA All | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Customers meter pole is down and needs repairs. Serviceman disconnected xfrmrs. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-09-16 00:30 | COMPLETED |  | 2013-09-15 21:29 | 2013-09-16 04:04 | 2013-09-16 04:16 | -118.4299 | 46.044
5W150 | 1404299 | CPCC | CPCC855337 | PP | WA | WALLA WALLA | BOWMAN | TR_366102_649900169 | 2013 | Before | 2013-09-16 09:40 | 2013-09-16 20:24 | 1 | 643.55 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Down nuetral, no outage,crew made repairs | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-09-16 12:45 | COMPLETED |  | 2013-09-16 09:40 | 2013-09-16 20:24 | 2013-09-16 21:52 | -118.5009 | 46.0373
5W150 | 1401103 | CPCC | CPCC853164 | PP | WA | WALLA WALLA | BOWMAN | TR_250002_302080379 | 2013 | Before | 2013-09-06 07:03 | 2013-09-07 02:37 | 1 | 1173.567 | 0 | 0 | 1 | Y | N | N | N | Y | 2013-09-05 to 2013-09-06 WA All | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Broken secondary neutral, making repairs. Repairs made and customer is back in full power. | DISTRIBUTION | CUSTOMER | AUTO |  | COMPLETED |  | 2013-09-06 07:03 | 2013-09-07 02:37 | 2013-09-07 03:41 | -118.3886 | 46.0495
5W150 | 1401674 | CPCC | CPCC853224 | PP | WA | WALLA WALLA | BOWMAN | TR_251802_209420292 | 2013 | Before | 2013-09-06 08:31 | 2013-09-06 19:17 | 6 | 3877.8 | 0 | 0 | 1 | Y | N | N | N | Y | 2013-09-05 to 2013-09-06 WA All | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Customer is cut in the clear until they make repairs | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2013-09-06 08:31 | 2013-09-06 19:17 | 2013-09-08 18:06 | -118.3846 | 46.0612
5W150 | 1401657 | CPCC | CPCC853374 | PP | WA | WALLA WALLA | BOWMAN | OH_260260_1541146324 | 2013 | Before | 2013-09-06 13:02 | 2013-09-07 10:49 | 8 | 10452.4 | 0 | 0 | 1 | Y | N | N | N | Y | 2013-09-05 to 2013-09-06 WA All | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Crew found tap fuse open they patrolled and found no issue. Close in and it held. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2013-09-06 13:02 | 2013-09-07 10:49 | 2013-09-08 17:56 | -118.534 | 46.0526
5W150 | 1401685 | CPCC | CPCC853270 | PP | WA | WALLA WALLA | BOWMAN | OH_270304_1541017824 | 2013 | Before | 2013-09-06 06:24 | 2013-09-07 07:33 | 320 | 125836.8 | 0 | 0 | 3 | Y | N | N | N | Y | 2013-09-05 to 2013-09-06 WA All | TREES | TREE - NON-PREVENTABLE |  |  | POLE OH |  |  |  | SOURCE: Broken pole due to tree. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2013-09-06 09:28 | 2013-09-07 07:33 | 2013-09-08 18:21 | -118.4289 | 46.0538
5W150 | 1422404 | CPCC | CPCC866872 | PP | WA | WALLA WALLA | BOWMAN | TR_264160_302080305 | 2013 | Before | 2013-11-19 09:37 | 2013-11-19 10:08 | 2 | 61.933 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman refused transformer# 264160 and it held, the cause was a squirrel, customers are back in full service. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-11-19 12:45 | COMPLETED |  | 2013-11-19 09:37 | 2013-11-19 10:08 | 2013-11-19 16:33 | -118.3991 | 46.0521
5W150 | 1422782 | CPCC | CPCC867174 | PP | WA | WALLA WALLA | BOWMAN | TR_277104_636330309 | 2013 | Before | 2013-11-21 05:54 | 2013-11-21 08:52 | 2 | 355.967 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Melted x-fmr fuse. Serviceman replaced fuse and it held. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-11-21 09:00 | COMPLETED |  | 2013-11-21 05:54 | 2013-11-21 08:52 | 2013-11-21 09:23 | -118.4144 | 46.0511
5W150 | 1414374 | CPCC | CPCC861845 | PP | WA | WALLA WALLA | BOWMAN | Line Cut-80147 | 2013 | Before | 2013-10-14 09:44 | 2013-10-14 11:00 | 1 | 75.533 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Crew has removed tree and repaired primary. | DISTRIBUTION | DEVICE | AUTO | 2013-10-14 12:45 | COMPLETED |  | 2013-10-14 09:44 | 2013-10-14 11:00 | 2013-10-14 12:28 | -118.4927 | 46.0648
5W150 | 1400946 | CPCC | CPCC853436 | PP | WA | WALLA WALLA | BOWMAN | TR_252300_209420385 | 2013 | Before | 2013-09-06 19:59 | 2013-09-06 21:35 | 1 | 96.05 | 0 | 0 | 1 | Y | N | N | N | Y | 2013-09-05 to 2013-09-06 WA All | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: secondary service. Repairs made. | DISTRIBUTION | CUSTOMER | AUTO |  | COMPLETED |  | 2013-09-06 19:59 | 2013-09-06 21:35 | 2013-09-06 22:01 | -118.3838 | 46.0547
5W150 | 1409756 | CPCC | CPCC860175 | PP | WA | WALLA WALLA | BOWMAN | TR_269806_302080238 | 2013 | Before | 2013-09-30 17:43 | 2013-09-30 18:14 | 1 | 31.35 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: serviceman removed tree limb | DISTRIBUTION | CUSTOMER | AUTO | 2013-09-30 20:45 | COMPLETED |  | 2013-09-30 17:43 | 2013-09-30 18:14 | 2013-09-30 18:17 | -118.3891 | 46.0612
5W150 | 1403882 | CPCC | CPCC855134 | PP | WA | WALLA WALLA | BOWMAN | TR_329800_636330255 | 2013 | Before | 2013-09-15 20:49 | 2013-09-16 03:59 | 7 | 3011.983 | 0 | 0 | 1 | Y | N | N | N | Y | 2013-09-15 to 2013-09-15 WA All | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Multiple customers out will need customer work done. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-09-16 | COMPLETED |  | 2013-09-15 20:49 | 2013-09-16 03:59 | 2013-09-16 04:16 | -118.4508 | 46.0475
5W150 | 1401684 | CPCC | CPCC853173 | PP | WA | WALLA WALLA | BOWMAN | OH_277502_636330291 | 2013 | Before | 2013-09-06 06:54 | 2013-09-07 18:28 | 17 | 31760.25 | 0 | 0 | 2 | Y | N | N | N | Y | 2013-09-05 to 2013-09-06 WA All | WEATHER | LIGHTNING |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Crew needed to make repairs to the overhead primary down in a creek. Repairs complete | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2013-09-06 07:14 | 2013-09-07 18:30 | 2013-09-08 18:21 | -118.4146 | 46.0566
5W150 | 1401698 | CPCC | CPCC853604 | PP | WA | WALLA WALLA | BOWMAN | TR_251802_209420292 | 2013 | Before | 2013-09-08 09:04 | 2013-09-08 18:38 | 1 | 573.85 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman found service taken down by trees from thursday's lighting storm. Calling tree crew to take care of major limbage, then put back up service. | DISTRIBUTION | CUSTOMER | AUTO | 2013-09-08 12:15 | COMPLETED |  | 2013-09-08 09:04 | 2013-09-08 18:40 | 2013-09-08 18:41 | -118.3846 | 46.0612
5W150 | 1402579 | CPCC | CPCC854001 | PP | WA | WALLA WALLA | BOWMAN | TR_283100_636330411 | 2013 | Before | 2013-09-11 11:23 | 2013-09-11 14:12 | 1 | 168.75 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman made repairs to the overhead secondary service that was damged by a tree limb, customer is back in full service. | DISTRIBUTION | CUSTOMER | AUTO | 2013-09-11 14:30 | COMPLETED |  | 2013-09-11 11:23 | 2013-09-11 14:12 | 2013-09-11 14:30 | -118.443 | 46.0521
5W150 | 1404750 | CPCC | CPCC855551 | PP | WA | WALLA WALLA | BOWMAN | TR_316760_636330335 | 2013 | Before | 2013-09-17 12:07 | 2013-09-17 16:42 | 1 | 275.667 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | OTHER INTERFERING OBJECT | WEATHER | WIND | POLE OH |  |  |  | SOURCE: Crew needed to replace a secondary pole that was damged after a barn roof blew off and hit the overhead secondary service. | DISTRIBUTION | CUSTOMER | AUTO | 2013-09-17 15:15 | COMPLETED |  | 2013-09-17 12:07 | 2013-09-17 16:42 | 2013-09-17 16:52 | -118.4794 | 46.0464
5W150 | 1409577 | CPCC | CPCC859836 | PP | WA | WALLA WALLA | BOWMAN | TR_232209_593050142 | 2013 | Before | 2013-09-30 09:12 | 2013-09-30 12:29 | 1 | 196.683 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman made repairs to the overhead secondary service that was damaged by a tree limb. | DISTRIBUTION | CUSTOMER | AUTO | 2013-09-30 12:15 | COMPLETED |  | 2013-09-30 09:12 | 2013-09-30 12:29 | 2013-09-30 13:38 | -118.4032 | 46.0671
5W150 | 1403869 | CPCC | CPCC855031 | PP | WA | WALLA WALLA | BOWMAN | Line Cut-78800 | 2013 | Before | 2013-09-15 18:52 | 2013-09-16 03:32 | 34 | 17673.767 | 0 | 0 | 1 | Y | N | N | N | Y | 2013-09-15 to 2013-09-15 WA All | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman found wire down, Need crew bucket to clear energized conductor safely, will call when repaired. Line cut at FP# 239203 on Gose N/O Heritage. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2013-09-15 19:27 | 2013-09-16 03:32 | 2013-09-16 03:56 | -118.3887 | 46.0679
5W150 | 1422405 | CPCC | CPCC866871 | PP | WA | WALLA WALLA | BOWMAN | TR_265605_302080260 | 2013 | Before | 2013-11-19 09:36 | 2013-11-19 10:54 | 5 | 390.083 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | SOURCE: Serviceman replaced the B/O secondary connector at the transformer, customers are back in full service. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-11-19 12:45 | COMPLETED |  | 2013-11-19 09:36 | 2013-11-19 10:54 | 2013-11-19 16:33 | -118.3979 | 46.0592
5W150 | 1401875 | CPCC | CPCC852203 | PP | WA | WALLA WALLA | BOWMAN | BOW_CB5W150 | 2013 | Before | 2013-09-05 17:25 | 2013-09-06 18:38 | 1830 | 1208184.45 | 0 | 0 | 5 | Y | N | N | N | Y | 2013-09-05 to 2013-09-06 WA All | WEATHER | LIGHTNING |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Lines down. Crew has made repairs and customers back in service. | DISTRIBUTION | DEVICE | AUTO | 2013-09-05 20:30 | COMPLETED |  | 2013-09-05 17:25 | 2013-09-06 18:38 | 2013-09-09 09:32 | -118.3614 | 46.0679
5W150 | 1403920 | CPCC | CPCC855127 | PP | WA | WALLA WALLA | BOWMAN | OH_265961_1540117656 | 2013 | Before | 2013-09-15 19:33 | 2013-09-16 04:56 | 28 | 15750.467 | 0 | 0 | 1 | Y | N | N | N | Y | 2013-09-15 to 2013-09-15 WA All | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: wire down, crew made repairs. | DISTRIBUTION | DEVICE | AUTO | 2013-09-15 23:30 | COMPLETED |  | 2013-09-15 20:29 | 2013-09-16 04:56 | 2013-09-16 05:26 | -118.3979 | 46.0628
5W150 | 1404249 | CPCC | CPCC855313 | PP | WA | WALLA WALLA | BOWMAN | OH_260260_1541146324 | 2013 | Before | 2013-09-16 08:42 | 2013-09-16 18:03 | 5 | 2806.25 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | INSULATOR OH |  |  |  | SOURCE: floater on pole 260200. will need a crew to make repairs and install a new pin. repairs made , power restored | DISTRIBUTION | DEVICE | AUTO | 2013-09-16 11:45 | COMPLETED |  | 2013-09-16 08:42 | 2013-09-16 18:03 | 2013-09-16 18:27 | -118.534 | 46.0526
5W150 | 1421016 | CPCC | CPCC866195 | PP | WA | WALLA WALLA | BOWMAN | TR_279004_649900238 | 2013 | Before | 2013-11-12 13:04 | 2013-11-12 15:11 | 1 | 127.467 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Tree limb damaged service. Serviceman made repairs. | DISTRIBUTION | CUSTOMER | AUTO | 2013-11-12 16:15 | COMPLETED |  | 2013-11-12 13:04 | 2013-11-12 15:11 | 2013-11-12 16:10 | -118.5341 | 46.0495
5W150 | 1424722 | CPCC | CPCC867903 | PP | WA | WALLA WALLA | BOWMAN | TR_239006_593050214 | 2013 | Before | 2013-11-26 21:09 | 2013-11-26 23:29 | 2 | 279.633 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Deteriorated fuse serviceman replaced fuse and restored power | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-11-27 00:15 | COMPLETED |  | 2013-11-26 21:09 | 2013-11-26 23:29 | 2013-11-27 03:09 | -118.3904 | 46.0653
5W150 | 1436241 | CPCC | CPCC876184 | PP | WA | WALLA WALLA | BOWMAN | TR_235060_593050198 | 2014 | Before | 2014-01-14 10:02 | 2014-01-14 10:26 | 3 | 71.5 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | TREES | TREE - NON-PREVENTABLE | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman de-energized x-fmr to make repairs to parlay | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2014-01-14 12:00 | COMPLETED |  | 2014-01-14 10:02 | 2014-01-14 10:26 | 2014-01-14 17:09 | -118.3979 | 46.0645
5W150 | 1428308 | CPCC | CPCC870864 | PP | WA | WALLA WALLA | BOWMAN | TR_311700_636330357 | 2013 | Before | 2013-12-11 06:41 | 2013-12-11 07:53 | 2 | 143.033 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: serviceman stated that the fuse appears to have melted out, will refuse the cutout | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-12-11 09:45 | COMPLETED |  | 2013-12-11 06:41 | 2013-12-11 07:53 | 2013-12-11 12:14 | -118.4891 | 46.046
5W150 | 1436256 | CPCC | CPCC876249 | PP | WA | WALLA WALLA | BOWMAN | TR_274400_649900241 | 2014 | Before | 2014-01-14 16:51 | 2014-01-14 17:59 | 1 | 68.117 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman refused transformer# 274400 and it held, the cause was a tree limb, customer is back in full service. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-01-14 20:00 | COMPLETED |  | 2014-01-14 16:51 | 2014-01-14 17:59 | 2014-01-14 18:04 | -118.5463 | 46.0554
5W150 | 1430427 | CPCC | CPCC871709 | PP | WA | WALLA WALLA | BOWMAN | OH_269100_302080365 | 2013 | Before | 2013-12-19 08:06 | 2013-12-19 11:21 | 56 | 5034.466 | 0 | 0 | 2 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | TRANSFORMER OH |  |  |  | SOURCE: Serviceman reports blown fuse on Pole 269100, patrolled Line, found B/O xfmr on pole 264161 caused by squirrel. crew replaced xfmr. | DISTRIBUTION | DEVICE | AUTO | 2013-12-19 11:45 | COMPLETED |  | 2013-12-19 08:37 | 2013-12-19 11:21 | 2013-12-19 16:44 | -118.3889 | 46.0516
5W150 | 1435114 | CPCC | CPCC874855 | PP | WA | WALLA WALLA | BOWMAN | OH_252100_209420349 | 2014 | Before | 2014-01-11 13:10 | 2014-01-11 15:29 | 36 | 5020.934 | 0 | 0 | 2 | Y | N | N | N | Y | 2014/01/10 to 2014/01/12 WA All | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Servicemen isolated the B/O underground primary between transformer# 252080 and transformer# 252081. Customers are back in fulll service. | DISTRIBUTION | DEVICE | AUTO | 2014-01-11 16:15 | COMPLETED |  | 2014-01-11 13:11 | 2014-01-11 15:29 | 2014-01-11 15:38 | -118.3844 | 46.0508
5W150 | 1446851 | CPCC | CPCC886883 | PP | WA | WALLA WALLA | BOWMAN | TR_264302_302080310 | 2014 | Before | 2014-02-26 16:19 | 2014-02-26 17:32 | 6 | 434.7 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Servicemen onsite replacing the broken cutout and cutout arm. | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2014-02-26 20:00 | COMPLETED |  | 2014-02-26 16:19 | 2014-02-26 17:32 | 2014-02-26 18:38 | -118.3999 | 46.0545
5W150 | 1447739 | CPCC | CPCC887342 | PP | WA | WALLA WALLA | BOWMAN | TR_193303_825860456 | 2014 | Before | 2014-03-02 15:14 | 2014-03-02 17:27 | 1 | 133.483 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - TRIMMABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Bad order secondary conductor arching in trees. Serviceman and helper to replace service wire and do a little trimming. | DISTRIBUTION | CUSTOMER | AUTO | 2014-03-02 18:15 | COMPLETED |  | 2014-03-02 15:14 | 2014-03-02 17:28 | 2014-03-02 17:33 | -118.3596 | 46.0687
5W150 | 1459847 | CPCC | CPCC894345 | PP | WA | WALLA WALLA | BOWMAN | OH_280201_636330256 | 2014 | Before | 2014-04-22 16:24 | 2014-04-22 22:02 | 4 | 1351.333 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | POLE OH |  |  |  | SOURCE: crew on site making repairs to the pole and transformer | DISTRIBUTION | DEVICE | MANUAL | 2014-04-22 22:00 | COMPLETED |  | 2014-04-22 16:24 | 2014-04-22 22:02 | 2014-04-23 03:33 | -118.4508 | 46.0523
5W150 | 1468818 | CPCC | CPCC898751 | PP | WA | WALLA WALLA | BOWMAN | OH_320300_636330398 | 2014 | Before | 2014-05-24 22:16 | 2014-05-25 00:43 | 27 | 3946.509 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman arrived and found open fuse, asked for 2nd man to help patrol. patrolled found no cause, closed in and it held. PROSPER: added cust from 898752 | DISTRIBUTION | DEVICE | AUTO | 2014-05-25 01:30 | COMPLETED |  | 2014-05-24 22:24 | 2014-05-28 14:20 | 2014-05-25 05:33 | -118.471 | 46.0404
5W150 | 1458077 | CPCC | CPCC893431 | PP | WA | WALLA WALLA | BOWMAN | OH_358800_1540858501 | 2014 | Before | 2014-04-16 00:09 | 2014-04-16 06:41 | 9 | 3521.333 | 0 | 0 | 2 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (PROTECTED SPECIES) (BMTS) |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: crew to replace wire & refuse PROSPER: Dead pelican was found. | DISTRIBUTION | DEVICE | MANUAL | 2014-04-16 07:15 | COMPLETED |  | 2014-04-16 00:09 | 2014-04-25 08:30 | 2014-04-16 06:43 | -118.5153 | 46.0469
5W150 | 1468960 | CPCC | CPCC898970 | PP | WA | WALLA WALLA | BOWMAN | TR_251105_209420364 | 2014 | Before | 2014-05-25 18:13 | 2014-05-25 22:35 | 10 | 2625.167 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | SOURCE: Serviceman found b/o xfrmr, called crew and they replaced it. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-05-25 21:15 | COMPLETED |  | 2014-05-25 18:13 | 2014-05-25 22:35 | 2014-05-26 03:18 | -118.385 | 46.0513
5W150 | 1466038 | CPCC | CPCC897264 | PP | WA | WALLA WALLA | BOWMAN | TR_251105_209420364 | 2014 | Before | 2014-05-13 07:31 | 2014-05-13 08:52 | 10 | 810.833 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman reports fuse blown on transformer, caused by squirrel, refused and it held, power restored | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-05-13 10:45 | COMPLETED |  | 2014-05-13 07:31 | 2014-05-13 08:52 | 2014-05-13 11:28 | -118.385 | 46.0513
5W150 | 1460500 | CPCC | CPCC894446 | PP | WA | WALLA WALLA | BOWMAN | OH_294161_636330486 | 2014 | Before | 2014-04-23 14:36 | 2014-04-23 16:19 | 11 | 1123.1 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Serviceman will need additional help to replace the B/O cutout on pole# 294161 | DISTRIBUTION | DEVICE | AUTO | 2014-04-23 19:00 | COMPLETED |  | 2014-04-23 15:54 | 2014-04-23 16:19 | 2014-04-23 16:58 | -118.4615 | 46.051
5W150 | 1479829 | CPCC | CPCC904965 | PP | WA | WALLA WALLA | BOWMAN | TR_268800_302080243 | 2014 | Before | 2014-07-04 06:08 | 2014-07-04 07:01 | 5 | 263 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: serviceman reports that a bird caused the outage, will refuse the cutout | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-07-04 09:15 | COMPLETED |  | 2014-07-04 06:08 | 2014-07-04 07:01 | 2014-07-04 07:13 | -118.3924 | 46.0611
5W150 | 1486977 | CPCC | CPCC909045 | PP | WA | WALLA WALLA | BOWMAN | TR_264303_302080349 | 2014 | Before | 2014-07-25 08:46 | 2014-07-25 09:28 | 2 | 83.433 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman working OPQ#16266463 took outage on transformer, | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-07-25 12:00 | COMPLETED |  | 2014-07-25 08:46 | 2014-07-25 09:28 | 2014-07-25 12:19 | -118.3993 | 46.0545
5W150 | 1491833 | CPCC | CPCC911907 | PP | WA | WALLA WALLA | BOWMAN | TR_253900_209420291 | 2014 | Before | 2014-08-08 16:32 | 2014-08-08 22:55 | 2 | 767.2 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman found open fuse, no cause found. Replaced it and restored power. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-08-08 19:45 | COMPLETED |  | 2014-08-08 16:32 | 2014-08-08 22:55 | 2014-08-09 06:28 | -118.3821 | 46.0632
5W150 | 1483870 | CPCC | CPCC907092 | PP | WA | WALLA WALLA | BOWMAN | TR_352904_369970386 | 2014 | Before | 2014-07-16 06:06 | 2014-07-16 08:01 | 2 | 230.1 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown xfmr fuse. Serviceman investigating. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-07-16 09:15 | COMPLETED |  | 2014-07-16 06:06 | 2014-07-16 09:50 | 2014-07-16 10:09 | -118.4039 | 46.0481
5W150 | 1482535 | CPCC | CPCC906296 | PP | WA | WALLA WALLA | BOWMAN | OH_250201_302080361 | 2014 | Before | 2014-07-13 06:26 | 2014-07-13 07:27 | 151 | 9283.983 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown fuse no cause found. Re-fused and it held. | DISTRIBUTION | DEVICE | AUTO | 2014-07-13 09:45 | COMPLETED |  | 2014-07-13 06:34 | 2014-07-13 07:27 | 2014-07-13 12:08 | -118.3885 | 46.0529
5W150 | 1482718 | CPCC | CPCC906784 | PP | WA | WALLA WALLA | BOWMAN | OH_320300_636330398 | 2014 | Before | 2014-07-13 18:58 | 2014-07-13 23:53 | 30 | 2926.434 | 0 | 0 | 2 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: crew removed tree & put wire back up | DISTRIBUTION | DEVICE | MANUAL | 2014-07-14 | COMPLETED |  | 2014-07-13 19:01 | 2014-07-13 23:53 | 2014-07-13 23:58 | -118.471 | 46.0404
5W150 | 1491236 | CPCC | CPCC911534 | PP | WA | WALLA WALLA | BOWMAN | TR_367960_649900128 | 2014 | Before | 2014-08-06 15:54 | 2014-08-06 17:44 | 3 | 332.55 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: removed tree branch, made repairs to service wire, replaced fuse | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-08-06 19:00 | COMPLETED |  | 2014-08-06 15:54 | 2014-08-06 17:44 | 2014-08-07 04:19 | -118.4986 | 46.0479
5W150 | 1490285 | CPCC | CPCC911063 | PP | WA | WALLA WALLA | BOWMAN | TR_279003_636330310 | 2014 | Before | 2014-08-04 05:47 | 2014-08-04 12:08 | 1 | 381.5 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | SOURCE: Crew made repairs to b/o ug secondary | DISTRIBUTION | CUSTOMER | AUTO | 2014-08-04 09:00 | COMPLETED |  | 2014-08-04 05:47 | 2014-08-04 13:38 | 2014-08-04 16:45 | -118.4095 | 46.0502
5W150 | 1479611 | CPCC | CPCC904902 | PP | WA | WALLA WALLA | BOWMAN | TR_231201_593050173 | 2014 | Before | 2014-07-03 11:33 | 2014-07-03 13:25 | 1 | 112.3 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Serviceman found bad order cutout and burned off xfmr cutout jumper | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-07-03 14:45 | COMPLETED |  | 2014-07-03 11:33 | 2014-07-03 13:25 | 2014-07-03 14:38 | -118.4074 | 46.0676
5W150 | 1482538 | CPCC | CPCC906304 | PP | WA | WALLA WALLA | BOWMAN | TR_252201_209420378 | 2014 | Before | 2014-07-13 08:31 | 2014-07-13 10:37 | 1 | 126.367 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS | EQUIPMENT FAILURE | B/O EQUIPMENT | CUT-OUT B/O OH |  |  |  | SOURCE: Se4rviceman found squirrel caused b/o cutout. Made repairs with crew that was out already and restored power. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-07-13 11:30 | COMPLETED |  | 2014-07-13 08:31 | 2014-07-13 10:37 | 2014-07-13 12:13 | -118.3829 | 46.0529
5W150 | 1475036 | CPCC | CPCC902306 | PP | WA | WALLA WALLA | BOWMAN | TR_242204_593050250 | 2014 | Before | 2014-06-17 09:17 | 2014-06-17 10:10 | 1 | 53.033 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | SOURCE: Bad neutral , crew to make repairs | DISTRIBUTION | CUSTOMER | AUTO | 2014-06-17 12:30 | COMPLETED |  | 2014-06-17 09:17 | 2014-06-17 10:10 | 2014-06-17 16:03 | -118.3827 | 46.0668
5W150 | 1482017 | CPCC | CPCC905994 | PP | WA | WALLA WALLA | BOWMAN | TR_247300_593050277 | 2014 | Before | 2014-07-11 08:55 | 2014-07-11 10:06 | 5 | 356.417 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman refused transformer# 247300 and it held, the cause is unknown. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-07-11 12:00 | COMPLETED |  | 2014-07-11 08:55 | 2014-07-11 10:06 | 2014-07-11 10:24 | -118.3732 | 46.0694
5W150 | 1474177 | CPCC | CPCC901947 | PP | WA | WALLA WALLA | BOWMAN | OH_294161_636330486 | 2014 | Before | 2014-06-14 06:09 | 2014-06-14 08:13 | 8 | 992.667 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman found open center phase fuse at 294161. Patrolling line. Called for 1 man to help patrol. Refused & restored, no cause found. | DISTRIBUTION | DEVICE | AUTO | 2014-06-14 09:15 | COMPLETED |  | 2014-06-14 06:09 | 2014-06-14 08:13 | 2014-06-14 08:29 | -118.4615 | 46.051
5W150 | 1487851 | CPCC | CPCC909475 | PP | WA | WALLA WALLA | BOWMAN | TR_234300_1050461164 | 2014 | Before | 2014-07-28 11:51 | 2014-07-28 12:44 | 1 | 52.75 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman reports fuse blown on transformer, caused by starling, refused and it held, power restored | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-07-28 15:00 | COMPLETED |  | 2014-07-28 11:51 | 2014-07-28 12:44 | 2014-07-28 17:05 | -118.3998 | 46.0684
5W150 | 1490973 | CPCC | CPCC911479 | PP | WA | WALLA WALLA | BOWMAN | TR_253900_209420291 | 2014 | Before | 2014-08-06 08:23 | 2014-08-06 09:16 | 2 | 106.4 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman refused transformer# 253900 and it held, the cause is unknown, customers are back in full service. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-08-06 11:30 | COMPLETED |  | 2014-08-06 08:23 | 2014-08-06 09:16 | 2014-08-06 09:59 | -118.3821 | 46.0632
5W150 | 1494868 | CPCC | CPCC914917 | PP | WA | WALLA WALLA | BOWMAN | TR_234300_1050461164 | 2014 | Before | 2014-08-18 08:13 | 2014-08-18 08:53 | 1 | 40.733 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman found transformer fuse open on pole # 234600 due to starling. Re-fused and it held. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-08-18 11:15 | COMPLETED |  | 2014-08-18 08:13 | 2014-08-18 08:53 | 2014-08-18 16:14 | -118.3998 | 46.0684
5W150 | 1507821 | CPCC | CPCC921966 | PP | WA | WALLA WALLA | BOWMAN | TR_269000_1541117971 | 2014 | Before | 2014-10-06 13:24 | 2014-10-06 14:02 | 1 | 37.467 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: Serviceman replaced the B/O overhead secondary connector at the transformer, customer is back in full service. Customer did have an electrician at the site per the serviceman Holso. | DISTRIBUTION | CUSTOMER | AUTO | 2014-10-06 16:30 | COMPLETED |  | 2014-10-06 13:24 | 2014-10-06 14:02 | 2014-10-06 14:08 | -118.3897 | 46.0493
5W150 | 1517035 | CPCC | CPCC930657 | PP | WA | WALLA WALLA | BOWMAN | OH_342703_1540128211 | 2014 | Before | 2014-11-11 16:59 | 2014-11-11 20:30 | 11 | 2318.25 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman refused the dip fuses at pole# 342703 and they held, the cause is unknown. | DISTRIBUTION | DEVICE | AUTO | 2014-11-11 20:00 | COMPLETED |  | 2014-11-11 16:59 | 2014-11-11 20:30 | 2014-11-12 16:04 | -118.4259 | 46.0454
5W150 | 1502239 | CPCC | CPCC918669 | PP | WA | WALLA WALLA | BOWMAN | TR_268102_302080410 | 2014 | Before | 2014-09-14 08:15 | 2014-09-14 08:46 | 2 | 62.667 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: outage due to a squirrel, serviceman refused the cutout and customers are back in service | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-09-14 11:15 | COMPLETED |  | 2014-09-14 08:15 | 2014-09-14 08:46 | 2014-09-14 12:28 | -118.3912 | 46.0516
5W150 | 1508285 | CPCC | CPCC922247 | PP | WA | WALLA WALLA | BOWMAN | TR_262501_302080281 | 2014 | Before | 2014-10-08 11:59 | 2014-10-08 13:21 | 1 | 81.833 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: Serviceman replaced the B/O secondary connector at the transformer, customer is back in full service. | DISTRIBUTION | CUSTOMER | AUTO | 2014-10-08 15:00 | COMPLETED |  | 2014-10-08 11:59 | 2014-10-08 13:21 | 2014-10-08 16:18 | -118.4034 | 46.0567
5W150 | 1498404 | CPCC | CPCC916522 | PP | WA | WALLA WALLA | BOWMAN | OH_320300_636330398 | 2014 | Before | 2014-08-30 16:09 | 2014-08-30 19:59 | 32 | 7345.067 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: removed tree branch, reinstalled downed wire | DISTRIBUTION | DEVICE | AUTO | 2014-08-30 19:15 | COMPLETED |  | 2014-08-30 16:15 | 2014-08-30 19:59 | 2014-08-30 20:28 | -118.471 | 46.0404
5W150 | 1497033 | CPCC | CPCC915951 | PP | WA | WALLA WALLA | BOWMAN | TR_344600_636330463 | 2014 | Before | 2014-08-25 15:54 | 2014-08-25 16:56 | 2 | 123.1 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman reports blown fuse on transformer, tested good, re-fused and it held power restored, no cause found | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2014-08-25 15:54 | 2014-08-25 16:56 | 2014-08-25 18:03 | -118.4215 | 46.0437
5W150 | 1511579 | CPCC | CPCC924923 | PP | WA | WALLA WALLA | BOWMAN | TR_367000_649900176 | 2014 | Before | 2014-10-24 07:31 | 2014-10-24 08:27 | 2 | 113.1 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (PROTECTED SPECIES) (BMTS) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman refused transformer# 367000 and it held, the cause was an Owl. Seviceman added bird guarding to the transformer. Owl was burried at the base of the pole. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-10-24 10:30 | COMPLETED |  | 2014-10-24 07:31 | 2014-10-24 08:27 | 2014-10-24 12:33 | -118.4976 | 46.0346
5W150 | 1498510 | CPCC | CPCC916590 | PP | WA | WALLA WALLA | BOWMAN | TR_267508_302080235 | 2014 | Before | 2014-08-31 14:05 | 2014-08-31 15:58 | 1 | 112.633 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | SOURCE: replaced connectors | DISTRIBUTION | CUSTOMER | AUTO | 2014-08-31 17:15 | COMPLETED |  | 2014-08-31 14:05 | 2014-08-31 15:58 | 2014-08-31 16:03 | -118.3938 | 46.0565
5W150 | 1508286 | CPCC | CPCC922246 | PP | WA | WALLA WALLA | BOWMAN | TR_262601_302080282 | 2014 | Before | 2014-10-08 11:57 | 2014-10-08 13:22 | 3 | 255.1 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD SUSPECTED, NO MORTALITY |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman refused and it held, the cause was an Owl. Serviceman will turn in an order to have a crew birg bird guard on this transformer bank. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-10-08 15:00 | COMPLETED |  | 2014-10-08 11:57 | 2014-11-03 11:31 | 2014-10-08 16:18 | -118.4034 | 46.0581
5W150 | 1496711 | CPCC | CPCC915799 | PP | WA | WALLA WALLA | BOWMAN | TR_234300_1050461164 | 2014 | Before | 2014-08-24 10:51 | 2014-08-24 11:31 | 1 | 40.517 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman arrived and found small bird cause blown fuse. Refused and restored power. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-08-24 14:00 | COMPLETED |  | 2014-08-24 10:51 | 2014-08-24 11:31 | 2014-08-24 13:43 | -118.3998 | 46.0684
5W150 | 1524541 | CPCC | CPCC937796 | PP | WA | WALLA WALLA | BOWMAN | TR_251802_209420292 | 2014 | Before | 2014-12-11 13:30 | 2014-12-12 06:09 | 6 | 5991.6 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  |  | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-12-11 16:30 | COMPLETED |  | 2014-12-11 13:31 | 2014-12-12 06:18 | 2014-12-12 16:38 | -118.3846 | 46.0612
5W150 | 1524446 | CPCC | CPCC938286 | PP | WA | WALLA WALLA | BOWMAN | OH_320300_636330398 | 2014 | Before | 2014-12-11 13:33 | 2014-12-12 00:35 | 32 | 21182.4 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Line repaired, Fuses in and Holding | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2014-12-11 14:58 | 2014-12-12 05:29 | 2014-12-12 16:32 | -118.471 | 46.0404
5W150 | 1535571 | CPCC | CPCC945932 | PP | WA | WALLA WALLA | BOWMAN | TR_236403_593050179 | 2015 | Before | 2015-02-04 12:25 | 2015-02-04 13:00 | 3 | 107.2 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman refused transformer# 236403 and it held, the cause was a squirrel. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2015-02-04 12:25 | 2015-02-04 13:40 | 2015-02-04 13:44 | -118.3953 | 46.07
5W150 | 1531279 | CPCC | CPCC943465 | PP | WA | WALLA WALLA | BOWMAN | TR_329900_636330450 | 2015 | Before | 2015-01-10 18:31 | 2015-01-10 19:12 | 1 | 40.233 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | POLE OH |  |  |  | SOURCE: car hit pole, no damage | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-01-10 21:45 | COMPLETED |  | 2015-01-10 18:32 | 2015-01-11 02:26 | 2015-01-11 02:28 | -118.4508 | 46.0482
5W150 | 1524879 | CPCC | CPCC939513 | PP | WA | WALLA WALLA | BOWMAN | TR_277104_636330309 | 2014 | Before | 2014-12-12 17:46 | 2014-12-12 19:52 | 1 | 125.733 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | OTHER, KNOWN CAUSE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Yard light burnt out | DISTRIBUTION | CUSTOMER | AUTO | 2014-12-12 21:00 | COMPLETED |  | 2014-12-12 17:46 | 2014-12-12 21:47 | 2014-12-12 21:53 | -118.4144 | 46.0511
5W150 | 1524905 | CPCC | CPCC939246 | PP | WA | WALLA WALLA | BOWMAN | TR_251802_209420292 | 2014 | Before | 2014-12-12 08:13 | 2014-12-12 20:29 | 1 | 736.317 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | SECONDARY CONDUCTOR OH |  |  |  |  | DISTRIBUTION | CUSTOMER | AUTO | 2014-12-12 11:15 | COMPLETED |  | 2014-12-12 08:13 | 2014-12-12 22:38 | 2014-12-12 22:43 | -118.3846 | 46.0612
5W150 | 1524990 | CPCC | CPCC938695 | PP | WA | WALLA WALLA | BOWMAN | TR_262400_302080341 | 2014 | Before | 2014-12-11 16:40 | 2014-12-12 10:02 | 5 | 5208.25 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | SECONDARY CONDUCTOR OH |  |  |  |  | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-12-11 19:45 | COMPLETED |  | 2014-12-11 16:40 | 2014-12-13 00:06 | 2014-12-13 00:08 | -118.4033 | 46.056
5W150 | 1524989 | CPCC | CPCC938677 | PP | WA | WALLA WALLA | BOWMAN | TR_266102_302080403 | 2014 | Before | 2014-12-11 16:36 | 2014-12-12 07:37 | 1 | 901.683 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | SECONDARY CONDUCTOR OH |  |  |  |  | DISTRIBUTION | CUSTOMER | AUTO | 2014-12-11 19:45 | COMPLETED |  | 2014-12-11 16:36 | 2014-12-18 11:39 | 2014-12-13 00:08 | -118.3953 | 46.051
5W150 | 1527760 | CPCC | CPCC941716 | PP | WA | WALLA WALLA | BOWMAN | TR_251303_209420387 | 2014 | Before | 2014-12-25 05:42 | 2014-12-25 07:07 | 6 | 510.1 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman found fuse blown, No Cause found, Re-Fused and holding | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-12-25 08:45 | COMPLETED |  | 2014-12-25 05:43 | 2014-12-25 07:08 | 2014-12-25 07:13 | -118.3851 | 46.0543
5W150 | 1522336 | CPCC | CPCC935436 | PP | WA | WALLA WALLA | BOWMAN | TR_275700_1541017805 | 2014 | Before | 2014-12-04 14:57 | 2014-12-04 15:44 | 1 | 47.15 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman reports blown fuse on pole # 275760. Re-fused and it held. Cause unknow. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-12-04 18:00 | COMPLETED |  | 2014-12-04 14:57 | 2014-12-04 15:44 | 2014-12-04 15:54 | -118.4181 | 46.0598
5W150 | 1564520 | CPCC | CPCC967137 | PP | WA | WALLA WALLA | BOWMAN | OH_359803_1541062402 | 2015 | Before | 2015-06-01 06:38 | 2015-06-01 07:24 | 89 | 4147.4 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown line fuse due to a squirrel, re-Fused and Holding | DISTRIBUTION | DEVICE | AUTO | 2015-06-01 09:45 | COMPLETED |  | 2015-06-01 06:42 | 2015-06-01 08:13 | 2015-06-01 08:13 | -118.3886 | 46.0464
5W150 | 1561662 | CPCC | CPCC965027 | PP | WA | WALLA WALLA | BOWMAN | TR_239301_593050221 | 2015 | Before | 2015-05-20 13:21 | 2015-05-20 14:44 | 1 | 83.017 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman made repairs to the overhead secondary service that was damaged by a tree | DISTRIBUTION | CUSTOMER | AUTO | 2015-05-20 16:30 | COMPLETED |  | 2015-05-20 13:22 | 2015-05-20 14:45 | 2015-05-20 14:48 | -118.3895 | 46.0689
5W150 | 1559617 | CPCC | CPCC964130 | PP | WA | WALLA WALLA | BOWMAN | TR_268504_302080232 | 2015 | Before | 2015-05-12 17:24 | 2015-05-12 17:53 | 1 | 29.067 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | OTHER, KNOWN CAUSE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: service man will have crew out in the AM to straighten pole, OK for tonight | DISTRIBUTION | CUSTOMER | AUTO | 2015-05-12 20:30 | COMPLETED |  | 2015-05-12 17:24 | 2015-05-12 17:54 | 2015-05-12 17:58 | -118.3915 | 46.0565
5W150 | 1564122 | CPCC | CPCC966482 | PP | WA | WALLA WALLA | BOWMAN | OH_280360_636330418 | 2015 | Before | 2015-05-30 04:14 | 2015-05-30 06:49 | 48 | 7427.2 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: patroled, no cause found | DISTRIBUTION | DEVICE | AUTO | 2015-05-30 08:00 | COMPLETED |  | 2015-05-30 04:55 | 2015-05-30 06:49 | 2015-05-30 06:53 | -118.4506 | 46.0541
5W150 | 1564453 | CPCC | CPCC967073 | PP | WA | WALLA WALLA | BOWMAN | OH_359803_1541062402 | 2015 | Before | 2015-05-31 21:08 | 2015-05-31 23:39 | 88 | 13271.867 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: r5emoved tree branch | DISTRIBUTION | DEVICE | AUTO | 2015-06-01 00:30 | COMPLETED |  | 2015-05-31 21:19 | 2015-06-01 01:52 | 2015-06-01 01:53 | -118.3886 | 46.0464
5W150 | 1543376 | CPCC | CPCC953572 | PP | WA | WALLA WALLA | BOWMAN | Line Cut-94666 | 2015 | Before | 2015-03-05 14:32 | 2015-03-05 16:46 | 3 | 402.4 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Crew enroute to make repairs to the overhead primary that broke at a jumper | DISTRIBUTION | DEVICE | MANUAL | 2015-03-05 18:00 | COMPLETED |  | 2015-03-05 14:32 | 2015-03-05 16:49 | 2015-03-05 16:53 | -118.4685 | 46.0492
5W150 | 1551196 | CPCC | CPCC960170 | PP | WA | WALLA WALLA | BOWMAN | Line Cut-95278 | 2015 | Before | 2015-04-14 04:03 | 2015-04-14 07:45 | 27 | 5997.6 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: 0510 response found primary wire down, fuse is still in. calling in crew help and flaggers to repair. pulled apart at wedge clamp | DISTRIBUTION | DEVICE | AUTO | 2015-04-14 08:00 | COMPLETED |  | 2015-04-14 04:56 | 2015-04-14 12:10 | 2015-04-14 12:13 | -118.4891 | 46.046
5W150 | 1541227 | CPCC | CPCC952657 | PP | WA | WALLA WALLA | BOWMAN | TR_250201_302080374 | 2015 | Before | 2015-02-25 20:35 | 2015-02-26 00:12 | 10 | 2166.333 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: crew to repair downed service wire | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2015-02-25 20:37 | 2015-02-26 07:32 | 2015-02-26 07:33 | -118.3886 | 46.0529
5W150 | 1544922 | CPCC | CPCC954529 | PP | WA | WALLA WALLA | BOWMAN | OH_294161_636330486 | 2015 | Before | 2015-03-15 10:07 | 2015-03-15 11:45 | 10 | 984.167 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman found 40t fuse blown at FP 294161, patrolled and found no cause, re-fused and restored customers | DISTRIBUTION | DEVICE | AUTO | 2015-03-15 13:15 | COMPLETED |  | 2015-03-15 10:09 | 2015-03-15 11:52 | 2015-03-15 11:53 | -118.4615 | 46.051
5W150 | 1542567 | CPCC | CPCC953176 | PP | WA | WALLA WALLA | BOWMAN | TR_279003_636330310 | 2015 | Before | 2015-03-02 08:30 | 2015-03-02 15:02 | 1 | 392.283 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | SOURCE: Left msg w/ responce crew, Crew to trouble shoot B/O Ug. secondary | DISTRIBUTION | CUSTOMER | MANUAL | 2015-03-02 14:30 | COMPLETED |  | 2015-03-02 08:30 | 2015-03-02 16:35 | 2015-03-02 16:38 | -118.4095 | 46.0502
5W150 | 1548036 | CPCC | CPCC957021 | PP | WA | WALLA WALLA | BOWMAN | OH_245301_593050274 | 2015 | Before | 2015-03-29 10:43 | 2015-03-29 12:37 | 24 | 1669.15 | 0 | 0 | 2 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | LIGHTNING ARRESTER OH |  |  |  | SOURCE: squirrel, replaced blown lightning arrester added bird guard | DISTRIBUTION | DEVICE | AUTO | 2015-03-29 14:15 | COMPLETED |  | 2015-03-29 11:11 | 2015-03-29 12:39 | 2015-03-29 12:43 | -118.378 | 46.0686
5W150 | 1541901 | CPCC | CPCC953169 | PP | WA | WALLA WALLA | BOWMAN | TR_279003_636330310 | 2015 | Before | 2015-03-02 05:49 | 2015-03-02 08:07 | 4 | 550.933 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Found fuse blown on pole # 279003; unknown cause. Re-fused and it held. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-03-02 09:00 | COMPLETED |  | 2015-03-02 05:49 | 2015-03-02 09:36 | 2015-03-02 09:38 | -118.4095 | 46.0502
5W150 | 1565791 | CPCC | CPCC967610 | PP | WA | WALLA WALLA | BOWMAN | TR_261102_302080323 | 2015 | Before | 2015-06-04 08:15 | 2015-06-04 09:55 | 4 | 400.2 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman refused transformer# 261102 and it held, the cause was a squirrel. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-06-04 13:00 | COMPLETED |  | 2015-06-04 09:51 | 2015-06-04 10:39 | 2015-06-04 10:43 | -118.406 | 46.0519
5W150 | 1586925 | CPCC | CPCC982487 | PP | WA | WALLA WALLA | BOWMAN | Line Cut-97449 | 2015 | Before | 2015-08-06 08:27 | 2015-08-06 11:29 | 17 | 3097.683 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | CONSTRUCTION |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Crew took outage to transfer the primary to a new pole | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2015-08-06 08:27 | 2015-08-06 11:52 | 2015-08-06 11:53 | -118.3872 | 46.0465
5W150 | 1576238 | CPCC | CPCC973934 | PP | WA | WALLA WALLA | BOWMAN | TR_252081_209420362 | 2015 | Before | 2015-07-05 13:19 | 2015-07-05 19:04 | 1 | 344.717 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: bad Ug sec | DISTRIBUTION | CUSTOMER | AUTO | 2015-07-05 16:30 | COMPLETED |  | 2015-07-05 13:19 | 2015-07-05 19:05 | 2015-07-05 19:08 | -118.3827 | 46.05
5W150 | 1565718 | CPCC | CPCC967592 | PP | WA | WALLA WALLA | BOWMAN | OH_280360_636330418 | 2015 | Before | 2015-06-04 02:33 | 2015-06-04 05:00 | 59 | 8653.333 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Crew patrolled the line and did not find any fault. Replaced A and B Phase Fuses at Pole 280360 | DISTRIBUTION | DEVICE | AUTO | 2015-06-04 06:15 | COMPLETED |  | 2015-06-04 02:34 | 2015-06-04 07:06 | 2015-06-04 07:08 | -118.4506 | 46.0541
5W150 | 1577114 | CPCC | CPCC974466 | PP | WA | WALLA WALLA | BOWMAN | TR_235264_593050192 | 2015 | Before | 2015-07-07 09:15 | 2015-07-07 10:27 | 1 | 71.833 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: secondary service | DISTRIBUTION | CUSTOMER | AUTO | 2015-07-07 12:15 | COMPLETED |  | 2015-07-07 09:15 | 2015-07-07 17:55 | 2015-07-07 17:58 | -118.3979 | 46.0681
5W150 | 1584901 | CPCC | CPCC980517 | PP | WA | WALLA WALLA | BOWMAN | TR_356900_369971619 | 2015 | Before | 2015-07-31 06:17 | 2015-07-31 09:12 | 6 | 1048.5 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Bad cutout -- did callout foir a crew | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-07-31 09:30 | COMPLETED |  | 2015-07-31 06:17 | 2015-07-31 15:15 | 2015-07-31 15:19 | -118.3969 | 46.0491
5W150 | 1588219 | CPCC | CPCC983039 | PP | WA | WALLA WALLA | BOWMAN | OH_250201_302080361 | 2015 | Before | 2015-08-10 08:56 | 2015-08-10 10:47 | 151 | 16828.95 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | B/O EQUIPMENT | SPLICE B/O OH |  |  |  | SOURCE: Crew took outage to make repairs to the overhead primary that pulled apart at a sleeve. | DISTRIBUTION | DEVICE | MANUAL | 2015-08-10 11:00 | COMPLETED |  | 2015-08-10 08:56 | 2015-08-10 15:22 | 2015-08-10 15:24 | -118.3886 | 46.0529
5W150 | 1568992 | CPCC | CPCC969363 | PP | WA | WALLA WALLA | BOWMAN | Line Cut-96212 | 2015 | Before | 2015-06-15 05:53 | 2015-06-15 08:02 | 17 | 2180.817 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: Broken jumper | DISTRIBUTION | DEVICE | AUTO | 2015-06-15 09:00 | COMPLETED |  | 2015-06-15 05:54 | 2015-06-15 08:43 | 2015-06-15 08:48 | -118.4032 | 46.0677
5W150 | 1573511 | CPCC | CPCC971944 | PP | WA | WALLA WALLA | BOWMAN | OH_280360_636330418 | 2015 | Before | 2015-06-29 00:15 | 2015-06-29 01:59 | 77 | 7981.05 | 0 | 0 | 1 | Y | N | N | N | Y | 2015-06-29 Washington | PLANNED | EMERGENCY DAMAGE REPAIR | INTERFERENCE | VEHICLE ACCIDENT | POLE OH |  |  |  | SOURCE: crew had to deenergize the line to make repairs to a car hit pole, see outage 971890 Crew replaced the pole | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2015-06-29 00:15 | 2015-07-01 11:22 | 2015-06-29 05:58 | -118.4506 | 46.0541
5W150 | 1611000 | CPCC | CPCC997986 | PP | WA | WALLA WALLA | BOWMAN | TR_252280_209420334 | 2015 | Before | 2015-11-09 14:18 | 2015-11-09 14:32 | 14 | 190.167 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | DETERIORATION OR ROTTING | SECONDARY CABLE UG |  |  |  | SOURCE: Serviceman took outage on the transformer to make repairs to the B/O underground secondary service | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-11-09 17:30 | COMPLETED |  | 2015-11-09 14:18 | 2015-11-09 15:20 | 2015-11-09 15:24 | -118.3832 | 46.0525
5W150 | 1591280 | CPCC | CPCC984771 | PP | WA | WALLA WALLA | BOWMAN | TR_250001_302080378 | 2015 | Before | 2015-08-20 12:52 | 2015-08-20 15:17 | 1 | 144.533 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Crew made repairs to the overhead secondary service that was damaged by a tree limb. | DISTRIBUTION | CUSTOMER | AUTO | 2015-08-20 16:00 | COMPLETED |  | 2015-08-20 12:53 | 2015-08-20 15:28 | 2015-08-20 15:34 | -118.3886 | 46.05
5W150 | 1611002 | CPCC | CPCC997963 | PP | WA | WALLA WALLA | BOWMAN | TR_252280_209420334 | 2015 | Before | 2015-11-09 10:58 | 2015-11-09 14:32 | 1 | 213.467 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | SOURCE: Serviceman installed a service saver due to a B/o underground secondary service | DISTRIBUTION | CUSTOMER | AUTO |  | COMPLETED |  | 2015-11-09 11:48 | 2015-11-09 15:20 | 2015-11-09 15:24 | -118.3832 | 46.0525
5W150 | 1595350 | CPCC | CPCC987761 | PP | WA | WALLA WALLA | BOWMAN | TR_252080_209420363 | 2015 | Before | 2015-09-02 17:38 | 2015-09-02 23:20 | 1 | 342.783 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | DIG-IN (NON-PACIFICORP PERSONNEL) |  |  | SECONDARY CABLE UG |  |  |  | SOURCE: serviceman reports that there was dig in and a neutral problem, will get crew to make repairs,repairs completed, customer restored | DISTRIBUTION | CUSTOMER | MANUAL | 2015-09-02 23:45 | COMPLETED |  | 2015-09-02 17:38 | 2015-09-03 06:01 | 2015-09-03 06:03 | -118.3839 | 46.05
5W150 | 1605063 | CPCC | CPCC994258 | PP | WA | WALLA WALLA | BOWMAN | TR_235060_593050198 | 2015 | Before | 2015-10-13 20:19 | 2015-10-13 22:56 | 1 | 157.683 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: Serviceman replaced B/O Connectors, Restored Customer | DISTRIBUTION | CUSTOMER | AUTO | 2015-10-13 23:30 | COMPLETED |  | 2015-10-13 20:19 | 2015-10-14 10:14 | 2015-10-14 10:14 | -118.3979 | 46.0645
5W150 | 1605746 | CPCC | CPCC994978 | PP | WA | WALLA WALLA | BOWMAN | TR_356903_369970314 | 2015 | Before | 2015-10-17 08:28 | 2015-10-17 09:50 | 3 | 246.6 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman replaced a blown transformer fuse due to a squirrel | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-10-17 11:30 | COMPLETED |  | 2015-10-17 08:28 | 2015-10-17 16:19 | 2015-10-17 16:24 | -118.3949 | 46.0491
5W150 | 1588602 | CPCC | CPCC983208 | PP | WA | WALLA WALLA | BOWMAN | TR_276201_636330323 | 2015 | Before | 2015-08-11 14:53 | 2015-08-11 16:00 | 3 | 201.8 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: starling | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-08-11 18:00 | COMPLETED |  | 2015-08-11 14:53 | 2015-08-11 16:50 | 2015-08-11 16:54 | -118.4158 | 46.0532
5W150 | 1595262 | CPCC | CPCC987555 | PP | WA | WALLA WALLA | BOWMAN | TR_269107_302080407 | 2015 | Before | 2015-09-02 09:50 | 2015-09-02 11:17 | 1 | 86.183 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: Serviceman found a burnt connector on hot leg; will repair | DISTRIBUTION | CUSTOMER | AUTO | 2015-09-02 13:00 | COMPLETED |  | 2015-09-02 09:50 | 2015-09-02 16:13 | 2015-09-02 16:18 | -118.3901 | 46.0517
5W150 | 1608859 | CPCC | CPCC996789 | PP | WA | WALLA WALLA | BOWMAN | OH_277400_636330314 | 2015 | Before | 2015-10-31 17:26 | 2015-10-31 21:42 | 57 | 14595.8 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: Holso repoted burnt off jumper at 277506, repaired and restored customers on Outage | DISTRIBUTION | DEVICE | AUTO | 2015-10-31 20:45 | COMPLETED |  | 2015-10-31 17:36 | 2015-11-01 00:20 | 2015-11-01 00:24 | -118.4145 | 46.0562
5W150 | 1604512 | CPCC | CPCC993968 | PP | WA | WALLA WALLA | BOWMAN | OH_269100_302080365 | 2015 | Before | 2015-10-11 14:37 | 2015-10-11 17:58 | 59 | 7428.65 | 0 | 0 | 3 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Crew made repairs, replaced B/O Cutout, restored all customers | DISTRIBUTION | DEVICE | AUTO | 2015-10-11 17:45 | COMPLETED |  | 2015-10-11 14:37 | 2015-10-11 17:59 | 2015-10-11 18:03 | -118.3889 | 46.0516
5W150 | 1605969 | CPCC | CPCC995176 | PP | WA | WALLA WALLA | BOWMAN | Line Cut-98497 | 2015 | Before | 2015-10-18 10:42 | 2015-10-18 12:06 | 89 | 7480.45 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman reported that a squirrell blew the transformer fuse at Pole 364607 Cad ops is mismapped due to recent configuration change on the line Related to Outage 995169 | DISTRIBUTION | DEVICE | AUTO | 2015-10-18 14:00 | COMPLETED |  | 2015-10-18 10:47 | 2015-10-18 18:29 | 2015-10-18 18:29 | -118.3883 | 46.0464
5W150 | 1608862 | CPCC | CPCC996818 | PP | WA | WALLA WALLA | BOWMAN | BOW_CB5W150 | 2015 | Before | 2015-10-31 19:42 | 2015-10-31 19:42 | 0 | 0 | 1728 | 201.6 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Trip & Close | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2015-10-31 19:42 | 2015-11-02 11:01 | 2015-11-01 00:24 | -118.3614 | 46.0679
5W150 | 1608864 | CPCC | CPCC996819 | PP | WA | WALLA WALLA | BOWMAN | BOW_CB5W150 | 2015 | Before | 2015-10-31 19:42 | 2015-10-31 21:36 | 1728 | 78873.117 | 0 | 0 | 2 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: CB 5W150 locked open -- serviceman and crew reported a tree fell accross feeder -- they will clear tree & then call from sub to close breaker | DISTRIBUTION | DEVICE | AUTO | 2015-10-31 22:45 | COMPLETED |  | 2015-10-31 19:42 | 2015-11-02 09:07 | 2015-11-01 00:24 | -118.3614 | 46.0679
5W150 | 1613911 | CPCC | CPCC999760 | PP | WA | WALLA WALLA | BOWMAN | TR_242204_593050250 | 2015 | Before | 2015-11-17 17:18 | 2015-11-18 08:04 | 1 | 886 | 0 | 0 | 1 | Y | N | N | N | Y | Washington 11-17-2015 | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Crew needed w/130' of 1/o | DISTRIBUTION | CUSTOMER | MANUAL | 2015-11-17 23:22 | COMPLETED |  | 2015-11-17 17:19 | 2015-11-19 09:12 | 2015-11-19 09:14 | -118.3827 | 46.0668
5W150 | 1622881 | CPCC | CPCC1012592 | PP | WA | WALLA WALLA | BOWMAN | TR_264602_302080285 | 2015 | Before | 2015-12-15 10:44 | 2015-12-15 14:13 | 2 | 417.2 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | TRANSFORMER OH |  |  |  | SOURCE: Crew needed to replace a transformer that was damaged by a squirrel | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-12-15 14:15 | COMPLETED |  | 2015-12-15 11:15 | 2015-12-15 15:27 | 2015-12-15 15:32 | -118.4001 | 46.0593
5W150 | 1614685 | CPCC | CPCC1001382 | PP | WA | WALLA WALLA | BOWMAN | TR_194305_825860500 | 2015 | Before | 2015-11-22 12:59 | 2015-11-22 14:51 | 14 | 1572.9 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman replaced a broken fuse | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-11-22 16:00 | COMPLETED |  | 2015-11-22 12:59 | 2015-11-22 19:18 | 2015-11-22 19:19 | -118.3579 | 46.0685
5W150 | 1619485 | CPCC | CPCC1006570 | PP | WA | WALLA WALLA | BOWMAN | TR_241260_593050244 | 2015 | Before | 2015-12-10 07:27 | 2015-12-10 11:41 | 1 | 254.733 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: pole is fine, replaced broken sec nuet that ran through a tree | DISTRIBUTION | CUSTOMER | AUTO | 2015-12-10 10:30 | COMPLETED |  | 2015-12-10 07:27 | 2015-12-10 11:43 | 2015-12-10 11:44 | -118.3864 | 46.0678
5W150 | 1654394 | CPCC | CPCC1040687 | PP | WA | WALLA WALLA | BOWMAN | OH_277101_636330275 | 2016 | After | 2016-04-15 06:02 | 2016-04-15 09:12 | 44 | 8363.667 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman refused and restored all customers | DISTRIBUTION | DEVICE | AUTO | 2016-04-15 09:30 | COMPLETED |  | 2016-04-15 06:13 | 2016-04-15 18:22 | 2016-04-15 18:28 | -118.4141 | 46.0519
5W150 | 1658772 | CPCC | CPCC1042987 | PP | WA | WALLA WALLA | BOWMAN | TR_262900_302080298 | 2016 | After | 2016-05-01 16:45 | 2016-05-01 18:08 | 3 | 249.5 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: located failed C/O, wil replace,restore & report when completed(05:25) | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2016-05-01 19:45 | COMPLETED |  | 2016-05-01 16:45 | 2016-05-01 18:49 | 2016-05-01 18:52 | -118.4051 | 46.0629
5W150 | 1651189 | CPCC | CPCC1035632 | PP | WA | WALLA WALLA | BOWMAN | OH_252100_209420349 | 2016 | After | 2016-04-05 05:27 | 2016-04-05 08:47 | 28 | 5598.717 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Crew onsite isolating the B/O underground primary between transformer# 352081 and transformer# 253080. | DISTRIBUTION | DEVICE | AUTO | 2016-04-05 08:30 | COMPLETED |  | 2016-04-05 05:27 | 2016-04-05 08:48 | 2016-04-05 08:53 | -118.3844 | 46.0508
5W150 | 1641872 | CPCC | CPCC1027100 | PP | WA | WALLA WALLA | BOWMAN | TR_230303_593050171 | 2016 | After | 2016-02-27 10:00 | 2016-02-27 11:15 | 1 | 75.133 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman found melted out fuse on transformer bank , no cause found, refused and holding, all customers restored | DISTRIBUTION | CUSTOMER | AUTO | 2016-02-27 13:00 | COMPLETED |  | 2016-02-27 10:00 | 2016-02-27 13:10 | 2016-02-27 13:12 | -118.4085 | 46.0684
5W150 | 1642674 | CPCC | CPCC1028201 | PP | WA | WALLA WALLA | BOWMAN | OH_252100_209420349 | 2016 | After | 2016-03-02 00:17 | 2016-03-02 05:46 | 36 | 10400.667 | 0 | 0 | 3 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Crew found B/O Cable between FP 252081 and 253080, Isolated and Closed N/O at FP 252181 , all customers restored PROSPER: The failure was between fp#253080 & fp#252181 as per the responding foreman | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2016-03-02 00:17 | 2016-03-04 09:23 | 2016-03-02 05:52 | -118.3844 | 46.0508
5W150 | 1654299 | CPCC | CPCC1040691 | PP | WA | WALLA WALLA | BOWMAN | OH_277101_636330275 | 2016 | After | 2016-04-15 06:57 | 2016-04-15 09:11 | 4 | 539.067 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Opened fuse to make repairs to downed line on Outage 1040687 | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2016-04-15 06:57 | 2016-04-15 13:06 | 2016-04-15 13:08 | -118.4141 | 46.0519
5W150 | 1674736 | CPCC | CPCC1051287 | PP | WA | WALLA WALLA | BOWMAN | TR_352904_369970386 | 2016 | After | 2016-06-17 07:12 | 2016-06-17 08:22 | 1 | 70.383 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: serviceman reports blown fuse no cause found - refused and it held | DISTRIBUTION | CUSTOMER | AUTO | 2016-06-17 10:15 | COMPLETED |  | 2016-06-17 07:12 | 2016-06-17 12:18 | 2016-06-17 12:22 | -118.4039 | 46.0481
5W150 | 1670146 | CPCC | CPCC1048029 | PP | WA | WALLA WALLA | BOWMAN | OH_250201_302080361 | 2016 | After | 2016-06-03 11:02 | 2016-06-03 15:45 | 152 | 18365.7 | 0 | 0 | 4 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: found fuse open on pole 250201; found blown dip fuse at pole 250200; crew to repair cutout; crew found b/o ug cable btwn 251181 & 252281 (cadops/faar maps are not correct), 251181 goes to 252281, then to 252280. Closed n/o at 252280 to restore customers | DISTRIBUTION | DEVICE | MANUAL | 2016-06-03 16:30 | COMPLETED |  | 2016-06-03 11:12 | 2016-06-03 15:57 | 2016-06-03 15:58 | -118.3886 | 46.0529
5W150 | 1678545 | CPCC | CPCC1053509 | PP | WA | WALLA WALLA | BOWMAN | OH_251200_209420337 | 2016 | After | 2016-06-29 13:41 | 2016-06-29 22:46 | 88 | 37651.55 | 0 | 0 | 3 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Found dip fuse open on pole 251200; b/o ug primary cable; crew to switch it out to restore customers. B/O Cable between FP 251181 and 252281. Transformer at FP 251180 has to also be changed. | DISTRIBUTION | DEVICE | AUTO | 2016-06-29 16:45 | COMPLETED |  | 2016-06-29 13:42 | 2016-06-30 04:16 | 2016-06-30 04:18 | -118.3859 | 46.0529
5W150 | 1672849 | CPCC | CPCC1050531 | PP | WA | WALLA WALLA | BOWMAN | OH_252100_209420349 | 2016 | After | 2016-06-11 09:48 | 2016-06-11 13:49 | 28 | 6749.167 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Crew isolated Bad cable between FP 252081 and 253080, Closed N/O at Fp 252181, All customers are restored | DISTRIBUTION | DEVICE | AUTO | 2016-06-11 13:00 | COMPLETED |  | 2016-06-11 09:54 | 2016-06-11 13:50 | 2016-06-11 13:53 | -118.3844 | 46.0508
5W150 | 1679514 | CPCC | CPCC1054381 | PP | WA | WALLA WALLA | BOWMAN | TR_318500_1050460940 | 2016 | After | 2016-07-02 21:58 | 2016-07-02 22:56 | 1 | 57.55 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: re-fused transformer -- starling | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2016-07-03 01:00 | COMPLETED |  | 2016-07-02 21:58 | 2016-07-02 23:29 | 2016-07-02 23:32 | -118.4731 | 46.043
5W150 | 1665022 | CPCC | CPCC1045538 | PP | WA | WALLA WALLA | BOWMAN | OH_294161_636330486 | 2016 | After | 2016-05-16 06:59 | 2016-05-16 08:27 | 10 | 884 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Junctiona blown -- patrolling line. No cause found, refused and customers are back on. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2016-05-16 06:59 | 2016-05-16 08:31 | 2016-05-16 08:33 | -118.4615 | 46.051
5W150 | 1674485 | CPCC | CPCC1051234 | PP | WA | WALLA WALLA | BOWMAN | TR_250300_302080371 | 2016 | After | 2016-06-16 12:01 | 2016-06-16 12:30 | 3 | 86.7 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Found xfmr fuse open on pole 250300 due to squirrel; re-fused and it held. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2016-06-16 12:01 | 2016-06-16 12:57 | 2016-06-16 13:02 | -118.3886 | 46.0549
5W150 | 1704950 | CPCC | CPCC1071126 | PP | WA | WALLA WALLA | BOWMAN | TR_269501_302080220 | 2016 | After | 2016-09-25 10:25 | 2016-09-25 11:39 | 1 | 73.917 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman refused transformer fuse blown due to Squirrel, restored all customers | DISTRIBUTION | CUSTOMER | AUTO |  | COMPLETED |  | 2016-09-25 10:25 | 2016-09-25 13:14 | 2016-09-25 13:18 | -118.389 | 46.0579
5W150 | 1705932 | CPCC | CPCC1072033 | PP | WA | WALLA WALLA | BOWMAN | OH_364901_649900155 | 2016 | After | 2016-09-28 15:38 | 2016-09-28 16:55 | 18 | 1391.7 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown line fuse, patrolling for cause -- starlng -- re-fused | DISTRIBUTION | DEVICE | AUTO | 2016-09-28 18:45 | COMPLETED |  | 2016-09-28 15:38 | 2016-09-28 16:56 | 2016-09-28 16:58 | -118.5047 | 46.0478
5W150 | 1696551 | CPCC | CPCC1066171 | PP | WA | WALLA WALLA | BOWMAN | TR_317700_636330336 | 2016 | After | 2016-08-26 19:46 | 2016-08-26 20:41 | 1 | 55.483 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Re-fused transformer -- no cause | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2016-08-26 22:45 | COMPLETED |  | 2016-08-26 19:46 | 2016-08-27 03:30 | 2016-08-27 03:33 | -118.4771 | 46.0457
5W150 | 1702713 | CPCC | CPCC1070552 | PP | WA | WALLA WALLA | BOWMAN | OH_239260_593050183 | 2016 | After | 2016-09-20 02:31 | 2016-09-20 06:25 | 25 | 5856.25 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | PLANNED OUTAGE |  |  |  | SOURCE: Crew Opened fuse to facilitate repairs on Outage 1070551 | DISTRIBUTION | DEVICE | MANUAL | 2016-09-20 07:15 | COMPLETED |  | 2016-09-20 02:31 | 2016-09-20 06:26 | 2016-09-20 06:28 | -118.3905 | 46.0678
5W150 | 1702714 | CPCC | CPCC1070551 | PP | WA | WALLA WALLA | BOWMAN | OH_239260_593050183 | 2016 | After | 2016-09-20 01:57 | 2016-09-20 06:25 | 56 | 15012.648 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Wire down due to a tree, crew is onsite making repairs, repairs complete, all customers restored ( 1 customer left off due to damaged mast, electricain will have to make repairs) PROSPER: change time to first out 09/20/2016 1:56:42, was 09/20/2016 1:40:02 | DISTRIBUTION | DEVICE | MANUAL | 2016-09-20 07:15 | COMPLETED |  | 2016-09-20 02:11 | 2016-09-20 14:43 | 2016-09-20 06:28 | -118.3905 | 46.0678
5W150 | 1684960 | CPCC | CPCC1059020 | PP | WA | WALLA WALLA | BOWMAN | TR_253900_209420291 | 2016 | After | 2016-07-20 08:35 | 2016-07-20 11:05 | 2 | 299.767 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Re-fused transformer -- no cause | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2016-07-20 11:45 | COMPLETED |  | 2016-07-20 08:35 | 2016-07-20 11:40 | 2016-07-20 11:43 | -118.3822 | 46.0632
5W150 | 1689894 | CPCC | CPCC1061294 | PP | WA | WALLA WALLA | BOWMAN | TR_064900_20410471 | 2016 | After | 2016-08-03 19:21 | 2016-08-03 20:41 | 1 | 79.417 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: replaced transformer fuse | DISTRIBUTION | CUSTOMER | AUTO | 2016-08-03 22:30 | COMPLETED |  | 2016-08-03 19:22 | 2016-08-04 06:14 | 2016-08-04 06:18 | -118.4822 | 46.0342
5W150 | 1699392 | CPCC | CPCC1067954 | PP | WA | WALLA WALLA | BOWMAN | OH_320300_636330398 | 2016 | After | 2016-09-06 19:50 | 2016-09-07 05:43 | 49 | 6942.368 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | POLE OH |  |  |  | SOURCE: Crew changed out pole due to Pole Fire at FP 053700, all customers restored | DISTRIBUTION | DEVICE | MANUAL | 2016-09-07 05:30 | COMPLETED |  | 2016-09-06 20:18 | 2016-09-07 14:21 | 2016-09-07 05:48 | -118.471 | 46.0404
5W150 | 1702326 | CPCC | CPCC1070233 | PP | WA | WALLA WALLA | BOWMAN | TR_329800_636330255 | 2016 | After | 2016-09-17 20:26 | 2016-09-18 10:10 | 6 | 4944.8 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Pole Fire at this FP , Serviceman isolated transformer, crew needed to change out cutouts & crossarm | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2016-09-18 07:30 | COMPLETED |  | 2016-09-17 20:26 | 2016-09-18 15:23 | 2016-09-18 15:28 | -118.4509 | 46.0475
5W150 | 1696012 | CPCC | CPCC1065888 | PP | WA | WALLA WALLA | BOWMAN | TR_252280_209420334 | 2016 | After | 2016-08-24 19:24 | 2016-08-25 00:06 | 1 | 281.85 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | SOURCE: B/O Secondary cable, crew to repair, Repairs completed and all customers restored | DISTRIBUTION | CUSTOMER | AUTO |  | COMPLETED |  | 2016-08-24 19:24 | 2016-08-25 05:15 | 2016-08-25 05:18 | -118.3832 | 46.0525
5W150 | 1693531 | CPCC | CPCC1064532 | PP | WA | WALLA WALLA | BOWMAN | TR_330201_636330455 | 2016 | After | 2016-08-16 08:26 | 2016-08-16 09:20 | 1 | 54.25 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Original call ID 1064525 for differant location , blown transformer fuse , caused by starling | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2016-08-16 11:30 | COMPLETED |  | 2016-08-16 08:26 | 2016-08-16 09:25 | 2016-08-16 09:28 | -118.4498 | 46.0385
5W150 | 1699009 | CPCC | CPCC1067712 | PP | WA | WALLA WALLA | BOWMAN | OH_312700_1540918583 | 2016 | After | 2016-09-05 06:19 | 2016-09-05 10:30 | 44 | 3297.4 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | SOURCE: Crew replaced a bad overhead transformer and Cut out | DISTRIBUTION | DEVICE | AUTO | 2016-09-05 09:30 | COMPLETED |  | 2016-09-05 06:30 | 2016-09-05 18:11 | 2016-09-05 18:13 | -118.4883 | 46.046
5W150 | 1705846 | CPCC | CPCC1072021 | PP | WA | WALLA WALLA | BOWMAN | TR_250201_302080374 | 2016 | After | 2016-09-28 13:22 | 2016-09-28 14:31 | 8 | 549.067 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | CONSTRUCTION |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Planned outage no paperwork | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2016-09-28 17:30 | COMPLETED |  | 2016-09-28 13:22 | 2016-09-28 14:31 | 2016-09-28 14:33 | -118.3886 | 46.0529
5W150 | 1694580 | CPCC | CPCC1065029 | PP | WA | WALLA WALLA | BOWMAN | TR_247300_593050277 | 2016 | After | 2016-08-19 11:54 | 2016-08-19 13:16 | 5 | 411 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown transformer fuse, no cause found | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2016-08-19 15:00 | COMPLETED |  | 2016-08-19 11:54 | 2016-08-19 13:47 | 2016-08-19 13:48 | -118.3732 | 46.0694
5W150 | 1692473 | CPCC | CPCC1062676 | PP | WA | WALLA WALLA | BOWMAN | OH_252100_209420349 | 2016 | After | 2016-08-12 09:27 | 2016-08-12 12:48 | 28 | 5611.2 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Dip fuse blown -- crew switched to restore customers | DISTRIBUTION | DEVICE | AUTO | 2016-08-12 12:30 | COMPLETED |  | 2016-08-12 09:27 | 2016-08-12 14:56 | 2016-08-12 14:58 | -118.3844 | 46.0508
5W150 | 1695961 | CPCC | CPCC1065859 | PP | WA | WALLA WALLA | BOWMAN | TR_330201_636330455 | 2016 | After | 2016-08-24 14:08 | 2016-08-24 14:49 | 2 | 82.5 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Re-fused transformer -- starling | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2016-08-24 14:40 | 2016-08-24 17:16 | 2016-08-24 17:18 | -118.4498 | 46.0385
5W150 | 1700793 | CPCC | CPCC1068783 | PP | WA | WALLA WALLA | BOWMAN | TR_269000_1541117971 | 2016 | After | 2016-09-12 22:16 | 2016-09-12 23:41 | 1 | 85 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VANDALISM OR THEFT |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman found meter cut & red sealed -- customer account is showing active -- meter number does not match account meter -- possible meter swap -- re-connected meter -- will turn into service center for follow up -- customer advised PROSPER: change from CUSTOMER REQUESTED to VANDALISM OR THEFT | DISTRIBUTION | CUSTOMER | AUTO | 2016-09-13 01:30 | COMPLETED |  | 2016-09-12 22:17 | 2016-09-21 15:46 | 2016-09-13 04:28 | -118.3898 | 46.0493
5W150 | 1701925 | CPCC | CPCC1069456 | PP | WA | WALLA WALLA | BOWMAN | TR_251202_209420371 | 2016 | After | 2016-09-16 13:43 | 2016-09-16 14:13 | 9 | 267.3 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Found xfmr fuse open on pole 251202 due to a starling; re-fused and it held. (associate to outage 1069457) | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2016-09-16 13:43 | 2016-09-20 16:30 | 2016-09-16 14:18 | -118.3863 | 46.0524
5W150 | 1712876 | CPCC | CPCC1079021 | PP | WA | WALLA WALLA | BOWMAN | TR_251200_209420382 | 2016 | After | 2016-10-20 08:07 | 2016-10-20 09:50 | 1 | 103.333 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: limb thru service repair made | DISTRIBUTION | CUSTOMER | AUTO | 2016-10-20 11:15 | COMPLETED |  | 2016-10-20 08:07 | 2016-10-20 18:04 | 2016-10-20 18:08 | -118.3859 | 46.0529
5W150 | 1712509 | CPCC | CPCC1078929 | PP | WA | WALLA WALLA | BOWMAN | TR_330201_636330455 | 2016 | After | 2016-10-19 09:42 | 2016-10-19 10:16 | 2 | 69.533 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: found fuse open on pole 330201; unknown cause; re-fused and it held. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2016-10-19 12:45 | COMPLETED |  | 2016-10-19 09:42 | 2016-10-19 12:35 | 2016-10-19 12:38 | -118.4498 | 46.0385
5W150 | 1708343 | CPCC | CPCC1073580 | PP | WA | WALLA WALLA | BOWMAN | OH_312700_1540918583 | 2016 | After | 2016-10-07 10:23 | 2016-10-07 15:00 | 9 | 2497.95 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | POLE FIRE | POLE OH |  |  |  | SOURCE: Serviceman opened other phases due to burnt pole top 310700 | DISTRIBUTION | DEVICE | MANUAL | 2016-10-07 15:30 | COMPLETED |  | 2016-10-07 10:23 | 2016-10-07 15:04 | 2016-10-07 15:08 | -118.4883 | 46.046
5W150 | 1708344 | CPCC | CPCC1073576 | PP | WA | WALLA WALLA | BOWMAN | OH_312700_1540918583 | 2016 | After | 2016-10-07 10:01 | 2016-10-07 15:00 | 44 | 13158.933 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | POLE OH |  |  |  | SOURCE: found burnt pole 310700; crew completed repairs to pole top. | DISTRIBUTION | DEVICE | MANUAL | 2016-10-07 15:30 | COMPLETED |  | 2016-10-07 10:01 | 2016-10-07 15:03 | 2016-10-07 15:08 | -118.4883 | 46.046
5W150 | 1713144 | CPCC | CPCC1079264 | PP | WA | WALLA WALLA | BOWMAN | OH_266465_302080368 | 2016 | After | 2016-10-21 14:36 | 2016-10-21 18:11 | 91 | 5877.333 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CROSS ARM OH |  |  |  | SOURCE: Tap fuse blown -- arm burnt up -- serviceman isolated & re-fused tap -- need crew | DISTRIBUTION | DEVICE | AUTO | 2016-10-21 18:15 | COMPLETED |  | 2016-10-21 14:37 | 2016-10-22 06:06 | 2016-10-22 06:08 | -118.3953 | 46.0552
5W150 | 1718689 | CPCC | CPCC1082487 | PP | WA | WALLA WALLA | BOWMAN | TR_235160_593050196 | 2016 | After | 2016-11-16 12:31 | 2016-11-16 13:06 | 1 | 34.4 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman replaced a blown transformer fuse due to a squirrel at F/P 235160 | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2016-11-16 15:45 | COMPLETED |  | 2016-11-16 12:32 | 2016-11-16 18:46 | 2016-11-16 18:48 | -118.3979 | 46.0662
5W150 | 1716170 | CPCC | CPCC1081063 | PP | WA | WALLA WALLA | BOWMAN | TR_231000_593050156 | 2016 | After | 2016-11-03 18:50 | 2016-11-03 21:39 | 1 | 168.317 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | CONNECTOR OH |  |  |  | SOURCE: Serviceman replaced B/O Connector, had to clear some tree branches and reattach service at home, all customers restored | DISTRIBUTION | CUSTOMER | AUTO |  | COMPLETED |  | 2016-11-03 18:51 | 2016-11-04 03:13 | 2016-11-04 03:18 | -118.406 | 46.0652
5W150 | 1735923 | CPCC | CPCC1103242 | PP | WA | WALLA WALLA | BOWMAN | OH_252100_209420349 | 2017 | After | 2017-01-10 13:27 | 2017-01-10 14:39 | 28 | 2018.8 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: open fuse, suspect failed ug primary, checking fault indicators to isolate(14:27 rr) | DISTRIBUTION | DEVICE | AUTO | 2017-01-10 16:30 | COMPLETED |  | 2017-01-10 13:27 | 2017-01-10 15:02 | 2017-01-10 15:03 | -118.3844 | 46.0508
5W150 | 1735928 | CPCC | CPCC1103344 | PP | WA | WALLA WALLA | BOWMAN | OP_252181__3733220 | 2017 | After | 2017-01-10 14:40 | 2017-01-10 15:13 | 28 | 945.467 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: BAD PRI UG, CREW TO SWITCH AROUND | DISTRIBUTION | DEVICE | AUTO | 2017-01-10 17:45 | COMPLETED |  | 2017-01-10 14:40 | 2017-01-10 15:18 | 2017-01-10 15:23 | -118.3823 | 46.0514
5W150 | 1738360 | CPCC | CPCC1105053 | PP | WA | WALLA WALLA | BOWMAN | BOW_CB5W150 | 2017 | After | 2017-01-16 12:24 | 2017-01-16 14:05 | 1682 | 169769.867 | 0 | 0 | 1 | Y | N | N | N | Y | WA Walla Walla 01-16-2017 | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE |  |  | LIGHTNING ARRESTER SUB |  |  |  | SOURCE: Transmission line tripped open de-energizing Bowman substation, cause was blown lightning arrestor inside Bowman Substation. Cut arrestor in the clear and re-energize Bowman Sub. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2017-01-16 12:28 | 2017-01-17 10:22 | 2017-01-16 15:18 | -118.3614 | 46.068
5W150 | 1741790 | CPCC | CPCC1109074 | PP | WA | WALLA WALLA | BOWMAN | OH_241261_593050245 | 2017 | After | 2017-01-25 01:27 | 2017-01-25 10:00 | 6 | 3080.298 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: same outage as 1109071 | DISTRIBUTION | DEVICE | MANUAL | 2017-01-25 13:00 | COMPLETED |  | 2017-01-25 03:59 | 2017-01-26 09:52 | 2017-01-25 11:33 | -118.3851 | 46.0679
5W150 | 1748632 | CPCC | CPCC1116355 | PP | WA | WALLA WALLA | BOWMAN | OH_252100_209420349 | 2017 | After | 2017-02-20 14:23 | 2017-02-20 15:52 | 28 | 2510.667 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: b/o ug | DISTRIBUTION | DEVICE | AUTO | 2017-02-20 17:30 | COMPLETED |  | 2017-02-20 14:23 | 2017-02-20 15:56 | 2017-02-20 15:58 | -118.3844 | 46.0508
5W150 | 1766540 | CPCC | CPCC1134573 | PP | WA | WALLA WALLA | BOWMAN | TR_268102_302080410 | 2017 | After | 2017-04-16 10:01 | 2017-04-16 11:04 | 4 | 253.4 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: re-fused transformer -- squirrel | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2017-04-16 12:15 | COMPLETED |  | 2017-04-16 10:01 | 2017-04-16 16:45 | 2017-04-16 16:48 | -118.3913 | 46.0516
5W150 | 1769268 | CPCC | CPCC1136156 | PP | WA | WALLA WALLA | BOWMAN | OH_294161_636330486 | 2017 | After | 2017-04-26 05:12 | 2017-04-26 07:51 | 10 | 1592.5 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Fuse Open on pole 294161, Patrolling for cause, nothing found, closed on test and it held. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2017-04-26 06:48 | 2017-04-26 10:07 | 2017-04-26 10:08 | -118.4615 | 46.051
5W150 | 1776374 | CPCC | CPCC1141124 | PP | WA | WALLA WALLA | BOWMAN | TR_266102_302080403 | 2017 | After | 2017-05-20 18:58 | 2017-05-20 20:05 | 1 | 67.117 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Squirrels chewed thru 8 ft of service neutral, serviceman replaced and rerouted service away from tree, restored all customers | DISTRIBUTION | CUSTOMER | AUTO | 2017-05-20 22:00 | COMPLETED |  | 2017-05-20 18:58 | 2017-05-21 05:38 | 2017-05-21 05:43 | -118.3953 | 46.051
5W150 | 1775240 | CPCC | CPCC1140414 | PP | WA | WALLA WALLA | BOWMAN | TR_323201_636330393 | 2017 | After | 2017-05-16 19:44 | 2017-05-17 03:25 | 3 | 1381.75 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: crew to replace transformer | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2017-05-17 04:30 | COMPLETED |  | 2017-05-16 23:23 | 2017-05-17 05:29 | 2017-05-17 05:33 | -118.4653 | 46.038
5W150 | 1777423 | CPCC | CPCC1142179 | PP | WA | WALLA WALLA | BOWMAN | OH_235161_593050199 | 2017 | After | 2017-05-24 06:44 | 2017-05-24 08:50 | 11 | 947.185 | 0 | 0 | 2 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Squirrel into transformer at FP 238102 caused line fuse to blow, Serviceman cleared hazard at transformer and will refuse PROSPER: Combined with CPCC1142177 | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2017-05-24 07:26 | 2017-05-25 16:37 | 2017-05-24 09:43 | -118.3979 | 46.0653
5W150 | 1769069 | CPCC | CPCC1135994 | PP | WA | WALLA WALLA | BOWMAN | OH_239260_593050183 | 2017 | After | 2017-04-24 17:12 | 2017-04-24 21:06 | 82 | 4807.767 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Tap fuses blown -- headed to 911 location -- found broken cutouts & burnt up cross arm @ fp# 230303 PROSPER: power out | DISTRIBUTION | DEVICE | AUTO | 2017-04-24 20:30 | COMPLETED |  | 2017-04-24 17:22 | 2017-04-26 09:29 | 2017-04-25 15:33 | -118.3905 | 46.0678
5W150 | 1761222 | CPCC | CPCC1125625 | PP | WA | WALLA WALLA | BOWMAN | OH_364901_649900155 | 2017 | After | 2017-04-06 06:05 | 2017-04-06 08:12 | 19 | 2418.7 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman reported that line fuse at F/P 364901 was blown due to a Turkey flying into the line at F/P 364600 | DISTRIBUTION | DEVICE | AUTO | 2017-04-06 10:15 | COMPLETED |  | 2017-04-06 07:09 | 2017-04-06 21:57 | 2017-04-06 21:58 | -118.5047 | 46.0478
5W150 | 1770311 | CPCC | CPCC1136771 | PP | WA | WALLA WALLA | BOWMAN | OH_280360_636330418 | 2017 | After | 2017-04-30 21:29 | 2017-05-01 01:37 | 45 | 11166 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: serviceman found open fuse 40 ampere at FP 280360 on west side of line heading south. second limeman called out to help patrol line to find cause - other single fuse found at FP 329701 - 25 ampere - line patrolled - no cause found | DISTRIBUTION | DEVICE | AUTO | 2017-05-01 00:45 | COMPLETED |  | 2017-04-30 21:38 | 2017-05-01 05:53 | 2017-05-01 05:58 | -118.4506 | 46.0541
5W150 | 1759052 | CPCC | CPCC1123759 | PP | WA | WALLA WALLA | BOWMAN | OH_269805_302080212 | 2017 | After | 2017-03-29 12:47 | 2017-03-29 14:42 | 30 | 3450 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Serviceman reports fuse open at FP 269805 due to B/O Cutout, Crew to make repairs, Crew onsite, repairs in progress, all repairs complete and all customers restored | DISTRIBUTION | DEVICE | AUTO | 2017-03-29 16:00 | COMPLETED |  | 2017-03-29 12:53 | 2017-03-29 14:44 | 2017-03-29 14:48 | -118.3888 | 46.0612
5W150 | 1767551 | CPCC | CPCC1135107 | PP | WA | WALLA WALLA | BOWMAN | TR_280302_636330419 | 2017 | After | 2017-04-19 18:49 | 2017-04-19 19:50 | 1 | 61.067 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | SOURCE: Replaced burnt up connector at the transformer -- customer advised | DISTRIBUTION | CUSTOMER | AUTO | 2017-04-19 22:00 | COMPLETED |  | 2017-04-19 18:49 | 2017-04-19 20:09 | 2017-04-19 20:13 | -118.4508 | 46.0538
5W150 | 1780086 | CPCC | CPCC1143750 | PP | WA | WALLA WALLA | BOWMAN | OH_358800_1540858501 | 2017 | After | 2017-06-01 20:18 | 2017-06-01 21:15 | 1 | 57.05 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman found Open line Fuse at FP 358800, Patrolled for cause, no cause found, refused and restored all customers | DISTRIBUTION | DEVICE | AUTO | 2017-06-01 23:30 | COMPLETED |  | 2017-06-01 20:18 | 2017-06-02 07:54 | 2017-06-02 07:58 | -118.5153 | 46.0469
5W150 | 1782846 | CPCC | CPCC1145696 | PP | WA | WALLA WALLA | BOWMAN | TR_277001_636330304 | 2017 | After | 2017-06-11 10:13 | 2017-06-11 10:50 | 1 | 36.85 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: serviceman reports he found broken jumper at FP 277001, repairs made and customer is back in service | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2017-06-11 13:15 | COMPLETED |  | 2017-06-11 10:14 | 2017-06-11 13:07 | 2017-06-11 13:08 | -118.4144 | 46.0499
5W150 | 1785430 | CPCC | CPCC1146693 | PP | WA | WALLA WALLA | BOWMAN | TR_268504_302080232 | 2017 | After | 2017-06-17 08:45 | 2017-06-17 09:22 | 4 | 146.2 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: squirrel, refused transformer | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2017-06-17 11:45 | COMPLETED |  | 2017-06-17 08:45 | 2017-06-18 00:14 | 2017-06-18 00:18 | -118.3915 | 46.0565
5W150 | 1787266 | CPCC | CPCC1147554 | PP | WA | WALLA WALLA | BOWMAN | TR_268800_302080243 | 2017 | After | 2017-06-23 07:21 | 2017-06-23 07:50 | 5 | 142.583 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Re-fused transformer -- no cause | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2017-06-23 10:30 | COMPLETED |  | 2017-06-23 07:21 | 2017-06-23 10:50 | 2017-06-23 10:53 | -118.3924 | 46.0611
5W150 | 1789609 | CPCC | CPCC1149498 | PP | WA | WALLA WALLA | BOWMAN | TR_252081_209420362 | 2017 | After | 2017-06-28 12:27 | 2017-06-29 00:03 | 1 | 696.067 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | SOURCE: bad UG sec. | DISTRIBUTION | CUSTOMER | MANUAL | 2017-06-29 02:00 | COMPLETED |  | 2017-06-28 12:27 | 2017-06-29 06:04 | 2017-06-29 06:09 | -118.3827 | 46.05
5W150 | 1794937 | CPCC | CPCC1152811 | PP | WA | WALLA WALLA | BOWMAN | TR_260507_1540242598 | 2017 | After | 2017-07-15 09:18 | 2017-07-15 10:46 | 1 | 88.433 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | SOURCE: serviceman reports small bird got into transformer area, caused fuse to open, refused and customers restored | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2017-07-15 12:30 | COMPLETED |  | 2017-07-15 09:18 | 2017-07-15 11:49 | 2017-07-15 11:53 | -118.4079 | 46.0578
5W150 | 1797316 | CPCC | CPCC1154014 | PP | WA | WALLA WALLA | BOWMAN | TR_261102_302080323 | 2017 | After | 2017-07-21 19:24 | 2017-07-21 20:00 | 4 | 143 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | SOURCE: serviceman reports a squirrel caused transformer fuse to open, tested and then refused, customers have been restored | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2017-07-21 22:30 | COMPLETED |  | 2017-07-21 19:24 | 2017-07-21 23:35 | 2017-07-21 23:38 | -118.406 | 46.0519
5W150 | 1802920 | CPCC | CPCC1157610 | PP | WA | WALLA WALLA | BOWMAN | OH_329701_636330429 | 2017 | After | 2017-08-08 09:01 | 2017-08-08 09:55 | 11 | 596.567 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: blown fuse due to starling melted cutout | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2017-08-08 09:01 | 2017-08-08 11:03 | 2017-08-08 11:08 | -118.4509 | 46.046
5W150 | 1802929 | CPCC | CPCC1157609 | PP | WA | WALLA WALLA | BOWMAN | Line Cut-108359 | 2017 | After | 2017-08-08 08:38 | 2017-08-08 10:52 | 2 | 268.467 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: blown fuse due to starling melted cutout crew to repair | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2017-08-08 09:01 | 2017-08-08 11:26 | 2017-08-08 11:29 | -118.451 | 46.046
5W150 | 1803460 | CPCC | CPCC1158059 | PP | WA | WALLA WALLA | BOWMAN | OH_277502_636330291 | 2017 | After | 2017-08-09 02:52 | 2017-08-09 08:30 | 17 | 5742.033 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - TRIMMABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Crew had to put wire up and resag 3 Spans, all 3 phases | DISTRIBUTION | DEVICE | MANUAL | 2017-08-09 13:45 | COMPLETED |  | 2017-08-09 03:38 | 2017-08-09 15:42 | 2017-08-09 15:43 | -118.4147 | 46.0566
5W150 | 1803459 | CPCC | CPCC1158070 | PP | WA | WALLA WALLA | BOWMAN | OH_277502_636330291 | 2017 | After | 2017-08-09 05:30 | 2017-08-09 08:30 | 1 | 180.483 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | PLANNED OUTAGE |  |  |  | SOURCE: Opened fuses to facilitate repairs on outage 1158059 | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2017-08-09 05:30 | 2017-08-09 15:42 | 2017-08-09 15:43 | -118.4147 | 46.0566
5W150 | 1814415 | CPCC | CPCC1164041 | PP | WA | WALLA WALLA | BOWMAN | TR_265403_302080387 | 2017 | After | 2017-09-16 20:02 | 2017-09-16 20:25 | 4 | 95.467 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | SOURCE: serviceman reports fatigued fuse, refused and customers have been restored | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2017-09-16 23:45 | COMPLETED |  | 2017-09-16 20:02 | 2017-09-16 22:21 | 2017-09-16 22:23 | -118.3971 | 46.0564
5W150 | 1822773 | CPCC | CPCC1168851 | PP | WA | WALLA WALLA | BOWMAN | OH_269903_1541062442 | 2017 | After | 2017-10-19 09:03 | 2017-10-19 12:20 | 44 | 1634.869 | 0 | 0 | 2 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | TRANSFORMER OH |  |  |  | SOURCE: Blown fuse, caused by squirrel PROSPER: add 1 from CPCC1168856 | DISTRIBUTION | DEVICE | MANUAL | 2017-10-19 14:38 | COMPLETED |  | 2017-10-19 09:25 | 2017-10-26 09:19 | 2017-10-19 14:24 | -118.3888 | 46.0637
5W150 | 1823920 | CPCC | CPCC1170113 | PP | WA | WALLA WALLA | BOWMAN | TR_250401_302080369 | 2017 | After | 2017-10-22 04:30 | 2017-10-22 12:20 | 4 | 1878.4 | 0 | 0 | 1 | Y | N | N | N | Y | WA Washington 10-21-2017 | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Tree blew transformer fuse, trimmed tree and refused. | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2017-10-22 17:30 | COMPLETED |  | 2017-10-22 04:31 | 2017-10-22 15:40 | 2017-10-22 15:43 | -118.3886 | 46.0557
5W150 | 1823923 | CPCC | CPCC1169722 | PP | WA | WALLA WALLA | BOWMAN | OH_334400_636330443 | 2017 | After | 2017-10-21 16:59 | 2017-10-22 11:15 | 17 | 14533.4 | 0 | 0 | 2 | Y | N | N | N | Y | WA Washington 10-21-2017 | EQUIPMENT FAILURE | POLE FIRE |  |  | POLE OH |  |  |  | SOURCE: Crew will need to change pole out. Inaccessible location. ETR extended. | DISTRIBUTION | DEVICE | MANUAL | 2017-10-22 12:30 | COMPLETED |  | 2017-10-21 17:10 | 2017-10-22 15:42 | 2017-10-22 15:43 | -118.4409 | 46.0418
5W150 | 1835125 | CPCC | CPCC1178010 | PP | WA | WALLA WALLA | BOWMAN | TR_264901_302080303 | 2017 | After | 2017-12-09 14:33 | 2017-12-09 15:43 | 1 | 69.15 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | SOURCE: replaced bad sec connector | DISTRIBUTION | CUSTOMER | AUTO |  | COMPLETED |  | 2017-12-09 14:33 | 2017-12-09 18:19 | 2017-12-09 18:23 | -118.3998 | 46.0629
5W150 | 1836567 | CPCC | CPCC1178746 | PP | WA | WALLA WALLA | BOWMAN | OH_269502_1541062433 | 2017 | After | 2017-12-17 10:19 | 2017-12-17 14:11 | 13 | 844.833 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | SOURCE: Tap fuse blown -- patrolled line & found transformer fuse open @ fp# 268602 -- re-fused tap -- bad transformer & cutout -- ran Arcos for a crew | DISTRIBUTION | DEVICE | MANUAL | 2017-12-17 16:00 | COMPLETED |  | 2017-12-17 10:19 | 2017-12-17 14:37 | 2017-12-17 14:38 | -118.3888 | 46.0579
5W150 | 1837134 | CPCC | CPCC1178914 | PP | WA | WALLA WALLA | BOWMAN | OH_294161_636330486 | 2017 | After | 2017-12-19 07:19 | 2017-12-19 08:48 | 8 | 706.133 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD SUSPECTED, NO MORTALITY |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown line fuse, no cause found, suspect birds | DISTRIBUTION | DEVICE | AUTO | 2017-12-19 11:45 | COMPLETED |  | 2017-12-19 08:05 | 2017-12-20 00:26 | 2017-12-20 00:28 | -118.4615 | 46.051
5W150 | 1839123 | CPCC | CPCC1180685 | PP | WA | WALLA WALLA | BOWMAN | BOW_CB5W150 | 2017 | After | 2017-12-29 13:43 | 2017-12-29 16:18 | 1658 | 257515.033 | 0 | 0 | 1 | Y | N | N | N | Y | WA Washington 12-29-2017 | TREES | TREE - NON-PREVENTABLE | WEATHER | ICE | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: circuit breaker locked open at sub, found tree thru line PROSPER: Update outage time to SCADA time 12/29/2017 13:42:41 | DISTRIBUTION | DEVICE | MANUAL | 2017-12-29 18:00 | COMPLETED |  | 2017-12-29 13:43 | 2018-01-02 14:31 | 2017-12-29 23:33 | -118.3614 | 46.0677
5W150 | 1839312 | CPCC | CPCC1181655 | PP | WA | WALLA WALLA | BOWMAN | OH_239260_593050183 | 2017 | After | 2017-12-30 01:58 | 2017-12-30 14:30 | 82 | 54907.633 | 0 | 0 | 2 | Y | N | N | N | Y | WA Washington 12-29-2017 | WEATHER | ICE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Crew repaired down primary conductors | DISTRIBUTION | DEVICE | MANUAL | 2017-12-30 18:00 | COMPLETED |  | 2017-12-30 03:56 | 2017-12-30 19:02 | 2017-12-30 19:03 | -118.3905 | 46.0678
5W150 | 1839321 | CPCC | CPCC1181668 | PP | WA | WALLA WALLA | BOWMAN | OH_235161_593050199 | 2017 | After | 2017-12-30 05:02 | 2017-12-30 15:38 | 33 | 20964.35 | 0 | 0 | 1 | Y | N | N | N | Y | WA Washington 12-29-2017 | WEATHER | ICE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Crew made repairs to wire down. | DISTRIBUTION | DEVICE | MANUAL | 2017-12-30 18:00 | COMPLETED |  | 2017-12-30 06:07 | 2017-12-30 19:03 | 2017-12-30 19:08 | -118.3979 | 46.0653
5W150 | 1839319 | CPCC | CPCC1180431 | PP | WA | WALLA WALLA | BOWMAN | OH_262403_1540843411 | 2017 | After | 2017-12-29 06:17 | 2017-12-30 13:56 | 10 | 10547.167 | 0 | 0 | 2 | Y | N | N | N | Y | WA Washington 12-29-2017 | WEATHER | ICE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Multiple wire down in many locations damage to facilities in need of repair; crews will respond as soon as they can | DISTRIBUTION | DEVICE | MANUAL | 2017-12-30 18:00 | COMPLETED |  | 2017-12-29 06:18 | 2017-12-30 19:03 | 2017-12-30 19:08 | -118.4033 | 46.0564
5W150 | 1839333 | CPCC | CPCC1181870 | PP | WA | WALLA WALLA | BOWMAN | OH_265961_1540117656 | 2017 | After | 2017-12-30 15:29 | 2017-12-30 18:46 | 28 | 5495.467 | 0 | 0 | 1 | Y | N | N | N | Y | WA Washington 12-29-2017 | WEATHER | ICE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Multiple wire down in many locations; damage to facilities in need of repair from ice storm | DISTRIBUTION | DEVICE | MANUAL | 2017-12-31 00:15 | COMPLETED |  | 2017-12-30 15:32 | 2017-12-30 19:15 | 2017-12-30 19:18 | -118.3979 | 46.0628
5W150 | 1839320 | CPCC | CPCC1180478 | PP | WA | WALLA WALLA | BOWMAN | OH_265961_1540117656 | 2017 | After | 2017-12-29 04:28 | 2017-12-30 13:56 | 28 | 56224.467 | 0 | 0 | 1 | Y | N | N | N | Y | WA Washington 12-29-2017 | WEATHER | ICE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Jumpers opened, needs crew to resag conductor | DISTRIBUTION | DEVICE | MANUAL | 2017-12-30 18:00 | COMPLETED |  | 2017-12-29 07:36 | 2017-12-30 19:03 | 2017-12-30 19:08 | -118.3979 | 46.0628
5W150 | 1839377 | CPCC | CPCC1181700 | PP | WA | WALLA WALLA | BOWMAN | TR_265700_302080264 | 2017 | After | 2017-12-30 07:54 | 2017-12-30 21:32 | 1 | 817.717 | 0 | 0 | 1 | Y | N | N | N | Y | WA Washington 12-29-2017 | WEATHER | ICE |  |  | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | SOURCE: service reinstalled PROSPER: power out | DISTRIBUTION | CUSTOMER | MANUAL | 2017-12-31 | COMPLETED |  | 2017-12-30 07:55 | 2018-01-04 10:38 | 2017-12-30 22:13 | -118.3976 | 46.0606
5W150 | 1839442 | CPCC | CPCC1181888 | PP | WA | WALLA WALLA | BOWMAN | TR_288201_636330427 | 2017 | After | 2017-12-30 16:26 | 2017-12-31 03:14 | 1 | 648.433 | 0 | 0 | 1 | Y | N | N | N | Y | WA Washington 12-29-2017 | WEATHER | ICE |  |  | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | SOURCE: primary wire down due to storm miss modeled, transformer located west of this location | DISTRIBUTION | CUSTOMER | MANUAL | 2017-12-31 12:00 | COMPLETED |  | 2017-12-30 16:26 | 2017-12-31 03:24 | 2017-12-31 03:28 | -118.4331 | 46.0524
5W150 | 1839447 | CPCC | CPCC1181337 | PP | WA | WALLA WALLA | BOWMAN | BOW_CB5W150 | 2017 | After | 2017-12-29 17:35 | 2017-12-31 01:31 | 1649 | 1023505.95 | 0 | 0 | 3 | Y | N | N | N | Y | WA Washington 12-29-2017 | WEATHER | ICE |  |  | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | SOURCE: ice storm, multiple outages reported and cleared PROSPER: Update outage to SCADA time power out | DISTRIBUTION | DEVICE | MANUAL | 2017-12-31 12:00 | COMPLETED |  | 2017-12-29 17:36 | 2018-01-03 14:57 | 2017-12-31 03:28 | -118.3614 | 46.0677
5W150 | 1839626 | CPCC | CPCC1181831 | PP | WA | WALLA WALLA | BOWMAN | TR_267101_302080404 | 2017 | After | 2017-12-30 13:15 | 2017-12-31 13:42 | 1 | 1467.783 | 0 | 0 | 1 | Y | N | N | N | Y | WA Washington 12-29-2017 | TREES | TREE - NON-PREVENTABLE | WEATHER | ICE | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: crew repaired service PROSPER: power out | DISTRIBUTION | CUSTOMER | MANUAL | 2018-01-01 00:15 | COMPLETED |  | 2017-12-30 13:15 | 2018-01-04 10:50 | 2017-12-31 19:23 | -118.3942 | 46.0516
5W150 | 1839624 | CPCC | CPCC1181893 | PP | WA | WALLA WALLA | BOWMAN | TR_269503_302080215 | 2017 | After | 2017-12-30 17:06 | 2017-12-31 12:42 | 1 | 1175.75 | 0 | 0 | 1 | Y | N | N | N | Y | WA Washington 12-29-2017 | TREES | TREE - NON-PREVENTABLE | WEATHER | ICE | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Crew repaired secondary service drop PROSPER: power out | DISTRIBUTION | CUSTOMER | MANUAL | 2018-01-01 00:15 | COMPLETED |  | 2017-12-30 17:06 | 2018-01-04 10:53 | 2017-12-31 19:23 | -118.3887 | 46.0573
5W150 | 1839672 | CPCC | CPCC1181964 | PP | WA | WALLA WALLA | BOWMAN | TR_267303_1541013701 | 2017 | After | 2017-12-30 21:36 | 2017-12-31 15:28 | 6 | 6429.9 | 0 | 0 | 1 | Y | N | N | N | Y | WA Washington 12-29-2017 | WEATHER | ICE |  |  | TRANSFORMER OH |  |  |  | SOURCE: Bad Transformer | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2018-01-01 00:15 | COMPLETED |  | 2017-12-30 21:36 | 2017-12-31 21:37 | 2017-12-31 21:38 | -118.3943 | 46.0545
5W150 | 1839623 | CPCC | CPCC1181778 | PP | WA | WALLA WALLA | BOWMAN | TR_236480_1540825214 | 2017 | After | 2017-12-30 11:05 | 2017-12-31 09:51 | 1 | 1366.217 | 0 | 0 | 1 | Y | N | N | N | Y | WA Washington 12-29-2017 | TREES | TREE - NON-PREVENTABLE | WEATHER | ICE | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Crew removed tree limbs, repaired secondary service drop PROSPER: power out | DISTRIBUTION | CUSTOMER | MANUAL | 2017-12-31 12:00 | COMPLETED |  | 2017-12-30 11:05 | 2018-01-04 10:47 | 2017-12-31 19:23 | -118.3956 | 46.0704
5W150 | 1839625 | CPCC | CPCC1181859 | PP | WA | WALLA WALLA | BOWMAN | TR_269509_302080231 | 2017 | After | 2017-12-30 15:00 | 2017-12-31 11:06 | 1 | 1205.65 | 0 | 0 | 1 | Y | N | N | N | Y | WA Washington 12-29-2017 | TREES | TREE - NON-PREVENTABLE | WEATHER | ICE | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Crew removed tree limbs, repaired secondary service drop PROSPER: hazard | DISTRIBUTION | CUSTOMER | MANUAL | 2017-12-31 12:00 | COMPLETED |  | 2017-12-30 15:00 | 2018-01-04 10:50 | 2017-12-31 19:23 | -118.3906 | 46.0565
5W150 | 1839683 | CPCC | CPCC1181868 | PP | WA | WALLA WALLA | BOWMAN | TR_361901_1541289715 | 2017 | After | 2017-12-30 15:25 | 2017-12-31 06:19 | 1 | 894.05 | 0 | 0 | 1 | Y | N | N | N | Y | WA Washington 12-29-2017 | WEATHER | ICE |  |  | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | SOURCE: secondary wire down, due to storm, tree hazard, repairs made | DISTRIBUTION | CUSTOMER | MANUAL | 2017-12-31 12:00 | COMPLETED |  | 2017-12-30 15:27 | 2017-12-31 21:39 | 2017-12-31 21:43 | -118.3858 | 46.0491
5W150 | 1840964 | CPCC | CPCC1182928 | PP | WA | WALLA WALLA | BOWMAN | OH_259002_1541013637 | 2018 | After | 2018-01-08 09:03 | 2018-01-08 10:07 | 2 | 127.867 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Line Fuse Blown, Serviceman to patrol for cause, serviceman patrolled and found no cause, refused and restored | DISTRIBUTION | DEVICE | AUTO | 2018-01-08 12:45 | COMPLETED |  | 2018-01-08 09:04 | 2018-01-08 14:42 | 2018-01-08 14:44 | -118.4928 | 46.0498
5W150 | 1842642 | CPCC | CPCC1184087 | PP | WA | WALLA WALLA | BOWMAN | TR_283101_636330412 | 2018 | After | 2018-01-17 09:30 | 2018-01-17 11:33 | 2 | 246.967 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: tree took secondary wire down at secondary pole 283102, repairs made and customemrs back in service PROSPER: power out | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2018-01-17 13:43 | COMPLETED |  | 2018-01-17 09:30 | 2018-01-18 09:54 | 2018-01-17 15:24 | -118.4436 | 46.0508
5W150 | 1843094 | CPCC | CPCC1184468 | PP | WA | WALLA WALLA | BOWMAN | OH_265961_1540117656 | 2018 | After | 2018-01-19 10:20 | 2018-01-19 10:36 | 28 | 460.133 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | B/O EQUIPMENT | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Took emergency outage due to stranded primary wire. Repairs made. | DISTRIBUTION | DEVICE | MANUAL | 2018-01-19 11:15 | COMPLETED |  | 2018-01-19 10:20 | 2018-01-19 14:06 | 2018-01-19 14:09 | -118.3979 | 46.0628
5W150 | 1849170 | CPCC | CPCC1188650 | PP | WA | WALLA WALLA | BOWMAN | OH_320300_636330398 | 2018 | After | 2018-02-17 17:00 | 2018-02-17 19:37 | 11 | 1726.267 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown fuse due to a tree in primary between 320301-320300 cleared tree & fuse in. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2018-02-17 17:34 | 2018-02-19 12:36 | 2018-02-19 12:39 | -118.471 | 46.0404
5W150 | 1862143 | CPCC | CPCC1197985 | PP | WA | WALLA WALLA | BOWMAN | TR_267801_302080274 | 2018 | After | 2018-04-11 20:03 | 2018-04-12 04:13 | 1 | 489.25 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Failed cutout, burnt cross arm and cutout is hanging in the air. Crew needed. Repairs made. | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2018-04-12 08:15 | COMPLETED |  | 2018-04-11 20:54 | 2018-04-12 08:11 | 2018-04-12 08:15 | -118.3938 | 46.0613
5W150 | 1865617 | CPCC | CPCC1199770 | PP | WA | WALLA WALLA | BOWMAN | TR_265605_302080260 | 2018 | After | 2018-04-26 23:54 | 2018-04-27 04:22 | 3 | 804.6 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | SOURCE: B/O Transformer, ARCOS Callout completed, crew changed and restored all customersd | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2018-04-27 06:00 | COMPLETED |  | 2018-04-26 23:54 | 2018-04-27 05:17 | 2018-04-27 05:20 | -118.3979 | 46.0592
5W150 | 1867969 | CPCC | CPCC1201751 | PP | WA | WALLA WALLA | BOWMAN | BOW_CB5W150 | 2018 | After | 2018-05-08 20:26 | 2018-05-08 20:27 | 0 | 0 | 1695 | 819.25 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Trip & close | DISTRIBUTION | DEVICE | AUTO | 2018-05-08 23:30 | COMPLETED |  | 2018-05-08 20:26 | 2018-05-09 03:20 | 2018-05-09 03:25 | -118.3614 | 46.0677
5W150 | 1868329 | CPCC | CPCC1201867 | PP | WA | WALLA WALLA | BOWMAN | TR_252181_209420347 | 2018 | After | 2018-05-09 08:02 | 2018-05-10 04:54 | 1 | 1251.967 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | SOURCE: bad sec UG, need crew to make repairs -- repairs made -- | DISTRIBUTION | CUSTOMER | AUTO |  | COMPLETED |  | 2018-05-09 08:04 | 2018-05-10 16:15 | 2018-05-10 16:20 | -118.3823 | 46.0514
5W150 | 1868370 | CPCC | CPCC1202009 | PP | WA | WALLA WALLA | BOWMAN | TR_261403_302080308 | 2018 | After | 2018-05-10 12:53 | 2018-05-10 15:12 | 4 | 556.2 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: serviceman reports a blown fuse due to lightning, refused the cutout and cusstmers are back in service | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2018-05-10 16:00 | COMPLETED |  | 2018-05-10 12:53 | 2018-05-10 16:19 | 2018-05-10 16:20 | -118.4072 | 46.0564
5W150 | 1868354 | CPCC | CPCC1201942 | PP | WA | WALLA WALLA | BOWMAN | TR_250403_302080370 | 2018 | After | 2018-05-09 18:24 | 2018-05-10 03:22 | 1 | 537.633 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Need crew to replace service | DISTRIBUTION | CUSTOMER | MANUAL | 2018-05-10 04:30 | COMPLETED |  | 2018-05-09 18:24 | 2018-05-10 16:17 | 2018-05-10 16:20 | -118.3886 | 46.0551
5W150 | 1870186 | CPCC | CPCC1202862 | PP | WA | WALLA WALLA | BOWMAN | OH_260260_1541146324 | 2018 | After | 2018-05-19 13:36 | 2018-05-19 15:44 | 7 | 898.333 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | LIGHTNING ARRESTER OH |  |  |  | SOURCE: lcoated open fuses due to failed lightening arrestor, will close for test to restore | DISTRIBUTION | DEVICE | AUTO | 2018-05-19 17:15 | COMPLETED |  | 2018-05-19 13:38 | 2018-05-19 16:11 | 2018-05-19 16:15 | -118.5341 | 46.0526
5W150 | 1871201 | CPCC | CPCC1203251 | PP | WA | WALLA WALLA | BOWMAN | OH_294161_636330486 | 2018 | After | 2018-05-24 04:38 | 2018-05-24 09:27 | 8 | 2311.433 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Tap Fuse Open, Serviceman patrolling for cause -- 1 phase of primary holding by a couple of strands | DISTRIBUTION | DEVICE | MANUAL | 2018-05-24 10:30 | COMPLETED |  | 2018-05-24 06:06 | 2018-05-24 14:38 | 2018-05-24 14:40 | -118.4614 | 46.0511
5W150 | 1871202 | CPCC | CPCC1203260 | PP | WA | WALLA WALLA | BOWMAN | OH_294161_636330486 | 2018 | After | 2018-05-24 07:38 | 2018-05-24 09:27 | 4 | 437.267 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Open third phase to make repairs -- Tap Fuse Open, Serviceman patrolling for cause -- 1 phase of primary holding by a couple of strands | DISTRIBUTION | DEVICE | MANUAL | 2018-05-24 10:30 | COMPLETED |  | 2018-05-24 07:38 | 2018-05-24 14:38 | 2018-05-24 14:40 | -118.4614 | 46.0511
5W150 | 1871203 | CPCC | CPCC1203287 | PP | WA | WALLA WALLA | BOWMAN | TR_266363_302080392 | 2018 | After | 2018-05-24 10:54 | 2018-05-24 12:10 | 3 | 229.15 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: serviceman reports blown fuse, will investigate, no cause found refused cutout and all customers are back in service | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2018-05-24 14:00 | COMPLETED |  | 2018-05-24 10:54 | 2018-05-24 14:38 | 2018-05-24 14:40 | -118.3968 | 46.0545
5W150 | 1873082 | CPCC | CPCC1204565 | PP | WA | WALLA WALLA | BOWMAN | TR_352904_369970386 | 2018 | After | 2018-06-01 17:09 | 2018-06-01 19:30 | 2 | 282.7 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: re-fused transformer -- bird | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2018-06-01 20:15 | COMPLETED |  | 2018-06-01 17:09 | 2018-06-01 21:50 | 2018-06-01 21:52 | -118.4039 | 46.0481
5W150 | 1873269 | CPCC | CPCC1204640 | PP | WA | WALLA WALLA | BOWMAN | OH_310500_636330347 | 2018 | After | 2018-06-02 21:07 | 2018-06-03 06:35 | 4 | 2271.733 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | TRANSFORMER PADMOUNT/SUBMERSIBLE UG |  |  |  | SOURCE: Bad pamount transformer -- ran arcos for a crew -- no takers in Walla Walla -- crew coming form Yakima PROSPER: power out | DISTRIBUTION | DEVICE | MANUAL | 2018-06-03 07:30 | COMPLETED |  | 2018-06-02 21:08 | 2018-06-04 16:07 | 2018-06-03 07:10 | -118.491 | 46.043
5W150 | 1875512 | CPCC | CPCC1206100 | PP | WA | WALLA WALLA | BOWMAN | TR_329801_1540031566 | 2018 | After | 2018-06-11 18:24 | 2018-06-11 19:50 | 1 | 86 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman replaced blown transformer fuse, unknown what caused it, restored all customers | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2018-06-11 22:00 | COMPLETED |  | 2018-06-11 18:24 | 2018-06-12 05:55 | 2018-06-12 05:55 | -118.4509 | 46.0466
5W150 | 1878098 | CPCC | CPCC1210618 | PP | WA | WALLA WALLA | BOWMAN | TR_277000_636330305 | 2018 | After | 2018-06-19 21:44 | 2018-06-20 02:20 | 2 | 551.133 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: 01:08 Serviceman reports cutout needs to be replaced. 02:19 Cutout replaced and sevice restored. | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2018-06-20 03:15 | COMPLETED |  | 2018-06-19 21:45 | 2018-06-21 05:53 | 2018-06-21 05:55 | -118.4144 | 46.0503
5W150 | 1878836 | CPCC | CPCC1211497 | PP | WA | WALLA WALLA | BOWMAN | OH_277400_636330314 | 2018 | After | 2018-06-24 00:13 | 2018-06-24 03:23 | 2 | 379.333 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Open line fuse, serviceman to patrol for cause. no cause found, refused and restored | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2018-06-24 00:13 | 2018-06-24 06:10 | 2018-06-24 06:15 | -118.4145 | 46.0562
5W150 | 1880176 | CPCC | CPCC1212730 | PP | WA | WALLA WALLA | BOWMAN | TR_329700_1540032864 | 2018 | After | 2018-06-29 07:51 | 2018-06-29 08:43 | 1 | 52.733 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown transformer fuse, caused by starling | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2018-06-29 11:00 | COMPLETED |  | 2018-06-29 07:51 | 2018-06-29 10:00 | 2018-06-29 10:05 | -118.4523 | 46.0459
5W150 | 1887780 | CPCC | CPCC1217935 | PP | WA | WALLA WALLA | BOWMAN | TR_289101_636330258 | 2018 | After | 2018-07-25 08:31 | 2018-07-25 10:05 | 1 | 93.783 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD SUSPECTED, NO MORTALITY |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown transformer fuse suspect bird | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2018-07-25 08:31 | 2018-07-25 13:52 | 2018-07-25 13:55 | -118.43 | 46.051
5W150 | 1888659 | CPCC | CPCC1218419 | PP | WA | WALLA WALLA | BOWMAN | TR_329700_1540032864 | 2018 | After | 2018-07-28 08:37 | 2018-07-28 09:37 | 1 | 59.65 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman tested and refused O/H transformer ok. Cause was Starling. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2018-07-28 11:45 | COMPLETED |  | 2018-07-28 08:37 | 2018-07-28 09:39 | 2018-07-28 09:40 | -118.4526 | 46.0458
5W150 | 1889789 | CPCC | CPCC1218924 | PP | WA | WALLA WALLA | BOWMAN | TR_329700_1540032864 | 2018 | After | 2018-08-01 09:09 | 2018-08-01 10:19 | 1 | 70.133 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown transformer fuse, cause was starling. Refused and power is on. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2018-08-01 12:15 | COMPLETED |  | 2018-08-01 09:09 | 2018-08-01 14:39 | 2018-08-01 14:40 | -118.4526 | 46.0458
5W150 | 1890776 | CPCC | CPCC1219397 | PP | WA | WALLA WALLA | BOWMAN | TR_289101_636330258 | 2018 | After | 2018-08-04 17:58 | 2018-08-04 23:09 | 1 | 311.033 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: replaced transformer fuse | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2018-08-04 23:30 | COMPLETED |  | 2018-08-04 17:58 | 2018-08-05 18:11 | 2018-08-05 18:15 | -118.43 | 46.051
5W150 | 1890866 | CPCC | CPCC1219503 | PP | WA | WALLA WALLA | BOWMAN | TR_259101_649900221 | 2018 | After | 2018-08-06 07:06 | 2018-08-06 08:24 | 1 | 78.15 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman reports detiorated fuse. Refused, service restored. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2018-08-06 10:15 | COMPLETED |  | 2018-08-06 07:06 | 2018-08-06 08:39 | 2018-08-06 08:40 | -118.4926 | 46.0507
5W150 | 1891659 | CPCC | CPCC1219836 | PP | WA | WALLA WALLA | BOWMAN | TR_253900_209420291 | 2018 | After | 2018-08-08 08:16 | 2018-08-08 09:43 | 2 | 173.833 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown XFMR Fuse, no cause found. Refused and sevice is restored. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2018-08-08 11:00 | COMPLETED |  | 2018-08-08 08:16 | 2018-08-08 18:44 | 2018-08-08 18:45 | -118.3822 | 46.0632
5W150 | 1891727 | CPCC | CPCC1219937 | PP | WA | WALLA WALLA | BOWMAN | TR_253900_209420291 | 2018 | After | 2018-08-08 18:38 | 2018-08-08 19:31 | 1 | 52.933 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman refused transformer fuse blown due to Starling | DISTRIBUTION | CUSTOMER | AUTO | 2018-08-08 21:30 | COMPLETED |  | 2018-08-08 18:38 | 2018-08-09 06:13 | 2018-08-09 06:15 | -118.3822 | 46.0632
5W150 | 1896332 | CPCC | CPCC1222549 | PP | WA | WALLA WALLA | BOWMAN | OH_253201_209420330 | 2018 | After | 2018-08-26 12:50 | 2018-08-27 02:00 | 34 | 17685.7 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Bad order primary UG, crew onsite switching. | DISTRIBUTION | DEVICE | MANUAL | 2018-08-27 02:30 | COMPLETED |  | 2018-08-26 13:00 | 2018-08-27 02:08 | 2018-08-27 02:10 | -118.3822 | 46.0529
5W150 | 1896531 | CPCC | CPCC1222729 | PP | WA | WALLA WALLA | BOWMAN | TR_366800_649900152 | 2018 | After | 2018-08-27 13:40 | 2018-08-27 15:12 | 1 | 92.117 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: | DISTRIBUTION | CUSTOMER | AUTO | 2018-08-27 16:30 | COMPLETED |  | 2018-08-27 13:40 | 2018-08-27 15:48 | 2018-08-27 15:50 | -118.4995 | 46.0462
5W150 | 1896624 | CPCC | CPCC1222732 | PP | WA | WALLA WALLA | BOWMAN | TR_253281_209420331 | 2018 | After | 2018-08-27 14:04 | 2018-08-27 16:30 | 1 | 146.083 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | OTHER, KNOWN CAUSE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Had to split secondary cable and restored power to customers. | DISTRIBUTION | CUSTOMER | MANUAL | 2018-08-27 20:00 | COMPLETED |  | 2018-08-27 14:04 | 2018-08-27 23:49 | 2018-08-27 23:50 | -118.3821 | 46.0523
5W150 | 1897362 | CPCC | CPCC1223140 | PP | WA | WALLA WALLA | BOWMAN | TR_318500_1050460940 | 2018 | After | 2018-08-30 22:56 | 2018-08-31 03:26 | 1 | 270.333 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | SOURCE: Bad transformer need crew to replace - | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2018-08-31 06:30 | COMPLETED |  | 2018-08-30 22:56 | 2018-08-31 05:13 | 2018-08-31 05:15 | -118.4741 | 46.043
5W150 | 1900107 | CPCC | CPCC1226823 | PP | WA | WALLA WALLA | BOWMAN | TR_366800_649900152 | 2018 | After | 2018-09-12 12:49 | 2018-09-12 14:05 | 3 | 227.9 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Blown transformer fuse, cause was starling. Also had a tree limb in the seconday. Repairs made. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2018-09-12 15:45 | COMPLETED |  | 2018-09-12 12:49 | 2018-09-12 18:24 | 2018-09-12 18:25 | -118.4995 | 46.0462
5W150 | 1901622 | CPCC | CPCC1229615 | PP | WA | WALLA WALLA | BOWMAN | TR_367960_649900128 | 2018 | After | 2018-09-18 15:00 | 2018-09-18 15:52 | 1 | 51.85 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman must open pot @ 367960 to make repairs. Will report back. | DISTRIBUTION | CUSTOMER | AUTO | 2018-09-18 17:45 | COMPLETED |  | 2018-09-18 15:01 | 2018-09-18 17:50 | 2018-09-18 17:55 | -118.4983 | 46.0479
5W150 | 1905752 | CPCC | CPCC1232361 | PP | WA | WALLA WALLA | BOWMAN | RC_263404_1540836522 | 2018 | After | 2018-10-06 15:04 | 2018-10-07 11:24 | 304 | 159428.4 | 0 | 0 | 4 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | POLE OH |  |  |  | SOURCE: open reclosure due to burned transmission pole, 69kV de-energized, crew dispatched(15:34 r4r), Calling out crew in acros jk 1656, no response, cntract crew dispatched, 3 hour eta, etr is 14:00 10/07/2018(17:49 r4r) | DISTRIBUTION | DEVICE | MANUAL | 2018-10-07 14:00 | COMPLETED |  | 2018-10-06 15:34 | 2018-10-08 13:34 | 2018-10-07 13:40 | -118.4026 | 46.0564
5W150 | 1906960 | CPCC | CPCC1233176 | PP | WA | WALLA WALLA | BOWMAN | OH_259002_1541013637 | 2018 | After | 2018-10-12 10:19 | 2018-10-12 11:26 | 2 | 133.567 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: no cause found - refused and it held ok | DISTRIBUTION | DEVICE | AUTO | 2018-10-12 14:00 | COMPLETED |  | 2018-10-12 10:49 | 2018-10-12 11:53 | 2018-10-12 11:55 | -118.4928 | 46.0498
5W150 | 1908587 | CPCC | CPCC1234214 | PP | WA | WALLA WALLA | BOWMAN | TR_289101_636330258 | 2018 | After | 2018-10-19 17:49 | 2018-10-19 20:06 | 1 | 137.4 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman re-fused transformer, no cause found | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2018-10-19 21:00 | COMPLETED |  | 2018-10-19 17:49 | 2018-10-20 06:06 | 2018-10-20 06:10 | -118.43 | 46.051
5W150 | 1908775 | CPCC | CPCC1234364 | PP | WA | WALLA WALLA | BOWMAN | TR_243200_593050252 | 2018 | After | 2018-10-21 15:06 | 2018-10-21 16:54 | 4 | 432.4 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Squirrel fatality, re-fused and closed in successfully | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2018-10-21 18:15 | COMPLETED |  | 2018-10-21 15:06 | 2018-10-21 16:59 | 2018-10-21 17:00 | -118.3815 | 46.0672
5W150 | 1911254 | CPCC | CPCC1236001 | PP | WA | WALLA WALLA | BOWMAN | OH_294161_636330486 | 2018 | After | 2018-11-02 07:56 | 2018-11-02 10:15 | 8 | 1108.8 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | POLE OH |  |  |  | SOURCE: Blown line fuse, serviceman is investigating. Pole fire, FP# 324800. Let Irragation bank isolated and restored power. | DISTRIBUTION | DEVICE | AUTO | 2018-11-02 11:00 | COMPLETED |  | 2018-11-02 08:49 | 2018-11-02 16:27 | 2018-11-02 16:30 | -118.4614 | 46.0511
5W150 | 1913366 | CPCC | CPCC1237560 | PP | WA | WALLA WALLA | BOWMAN | TR_347701_1540118162 | 2018 | After | 2018-11-13 11:10 | 2018-11-13 13:54 | 1 | 163.067 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Crew completed replacing B/O O/H cutout. | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2018-11-13 16:00 | COMPLETED |  | 2018-11-13 11:11 | 2018-11-13 16:31 | 2018-11-13 16:35 | -118.4138 | 46.0462
5W150 | 1918366 | CPCC | CPCC1244559 | PP | WA | WALLA WALLA | BOWMAN | OH_294161_636330486 | 2018 | After | 2018-12-07 07:03 | 2018-12-07 08:55 | 11 | 1239.333 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Turkey | DISTRIBUTION | DEVICE | AUTO | 2018-12-07 10:15 | COMPLETED |  | 2018-12-07 07:03 | 2018-12-07 09:33 | 2018-12-07 09:35 | -118.4614 | 46.0511
5W150 | 1920120 | CPCC | CPCC1247729 | PP | WA | WALLA WALLA | BOWMAN | OH_358800_1540858501 | 2018 | After | 2018-12-14 09:21 | 2018-12-14 19:33 | 8 | 4892.667 | 0 | 0 | 2 | Y | N | N | N | N |  | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: 2 spans Wire down, across river | DISTRIBUTION | DEVICE | MANUAL | 2018-12-14 21:00 | COMPLETED |  | 2018-12-14 09:22 | 2018-12-14 19:37 | 2018-12-14 19:40 | -118.5152 | 46.0469
5W150 | 1922290 | CPCC | CPCC1251646 | PP | WA | WALLA WALLA | BOWMAN | TR_236260_593050188 | 2018 | After | 2018-12-21 09:00 | 2018-12-21 10:22 | 7 | 569.1 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown transformer fuse, caused by squirrel | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2018-12-21 12:00 | COMPLETED |  | 2018-12-21 09:01 | 2018-12-21 13:27 | 2018-12-21 13:30 | -118.396 | 46.0678
5W150 | 1926581 | CPCC | CPCC1255309 | PP | WA | WALLA WALLA | BOWMAN | TR_268002_302080417 | 2019 | After | 2019-01-09 08:03 | 2019-01-09 11:23 | 1 | 199.083 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | SOURCE: B/O secondary connector | DISTRIBUTION | CUSTOMER | MANUAL | 2019-01-09 13:00 | COMPLETED |  | 2019-01-09 08:04 | 2019-01-09 12:50 | 2019-01-09 12:55 | -118.3915 | 46.0496
5W150 | 1932325 | CPCC | CPCC1258999 | PP | WA | WALLA WALLA | BOWMAN | TR_236100_593050200 | 2019 | After | 2019-02-02 22:24 | 2019-02-02 23:02 | 6 | 229.6 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | B/O EQUIPMENT | CUT-OUT B/O OH |  |  |  | SOURCE: Cut outs and connectors replaced, customers in service | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2019-02-02 22:24 | 2019-02-02 23:03 | 2019-02-02 23:05 | -118.397 | 46.0653
5W202 | 598283 | CPCC | CPCC391443 | PP | OR | PENDLETON | BUCKAROO | TR_126200_842710161 | 2007 | Before | 2007-01-02 09:09 | 2007-01-02 10:18 | 1 | 69.483 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: Serviceman replaced B/O connectors at the weatherhead, customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 603413 | CPCC | CPCC399434 | PP | OR | PENDLETON | BUCKAROO | TR_213909_752850248 | 2007 | Before | 2007-02-14 08:07 | 2007-02-14 09:48 | 2 | 202.1 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT | ENVIRONMENT | FIRE/SMOKE (NOT DUE TO FAULTS) | TRANSFORMER OH |  |  |  | PROSPER: crew to replace burnt up trf., xfmr rpl'd, crew 07408, cause of fire unknown | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 623608 | CPCC | CPCC424225 | PP | OR | PENDLETON | BUCKAROO | TR_166841_619850632 | 2007 | Before | 2007-06-28 19:53 | 2007-06-28 21:37 | 1 | 104.817 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: replaced fuse, squirrel | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 623688 | CPCC | CPCC425240 | PP | OR | PENDLETON | BUCKAROO | TR_211909_752850201 | 2007 | Before | 2007-07-05 20:22 | 2007-07-05 20:28 | 1 | 6.133 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Associated with outage 425218. Bad connectivity in CADOPS. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 620257 | CPCC | CPCC422594 | PP | OR | PENDLETON | BUCKAROO | OH_210603_1550004111 | 2007 | Before | 2007-06-18 08:37 | 2007-06-18 11:04 | 65 | 9560.417 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: Crew made repairs to a burnt up cutout and the overhead primary that burnt down due to a squirrel that got on the top of a transformer, all customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8264 | 45.6411
5W202 | 621496 | CPCC | CPCC421442 | PP | OR | PENDLETON | BUCKAROO | TR_349700_886280575 | 2007 | Before | 2007-06-09 07:48 | 2007-06-09 08:36 | 1 | 47.5 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: found fuse open, no cause obvious. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 623421 | CPCC | CPCC425218 | PP | OR | PENDLETON | BUCKAROO | OH_210603_1550004111 | 2007 | Before | 2007-07-05 19:25 | 2007-07-05 20:28 | 25 | 1579.583 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Associated with outage 425218. Bad connectivity in CADOPS. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8264 | 45.6411
5W202 | 623422 | CPCC | CPCC425221 | PP | OR | PENDLETON | BUCKAROO | OH_214900_752850252 | 2007 | Before | 2007-07-05 19:25 | 2007-07-05 20:29 | 259 | 16635.65 | 0 | 0 | 2 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Fuse on pole 214900 is open serviceman is patrolling. Found no cause re fused and customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8194 | 45.6454
5W202 | 614420 | CPCC | CPCC418795 | PP | OR | PENDLETON | BUCKAROO | TR_166850_619850629 | 2007 | Before | 2007-05-23 08:06 | 2007-05-23 08:56 | 1 | 50.15 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: Associate to outage# 418796. B/O connectivity in cadops, mapping change made. Serviceman refused tapline at pole# 165740 and it held, the cause was a squirrel that got into transformer# 164745. crew will need to change out cutout | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 614421 | CPCC | CPCC418796 | PP | OR | PENDLETON | BUCKAROO | OH_165740_619850637 | 2007 | Before | 2007-05-23 08:07 | 2007-05-23 09:34 | 139 | 6752.9 | 0 | 0 | 2 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: Serviceman refused tapline at pole# 165740 and it held, the cause was a squirrel that got into transformer# 164745 and damaged the cutout, crew is enroute to change out the cutout. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8166 | 45.6568
5W202 | 614422 | CPCC | CPCC418798 | PP | OR | PENDLETON | BUCKAROO | TR_164546_619850473 | 2007 | Before | 2007-05-23 08:14 | 2007-05-23 08:56 | 1 | 41.367 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: Associate to outage# 418796. B/O connectivity in cadops, mapping change made. Serviceman refused tapline at pole# 165740 and it held, the cause was a squirrel that got into transformer# 164745. crew will need to change out cutout | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 615663 | CPCC | CPCC417608 | PP | OR | PENDLETON | BUCKAROO | TR_340000_132440005 | 2007 | Before | 2007-05-13 07:57 | 2007-05-13 09:50 | 1 | 112.783 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Span of secondary down. Made repairs. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 613906 | CPCC | CPCC415523 | PP | OR | PENDLETON | BUCKAROO | OH_163501_619850475 | 2007 | Before | 2007-04-25 15:06 | 2007-04-25 16:01 | 26 | 1095.2 | 0 | 0 | 2 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: svcman reports squirrel on a trf caused the trf cutout fuse to blow along with a 100 amp line fuse. the squirrel cleared and both fuses replaced. all customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8213 | 45.6534
5W202 | 617181 | CPCC | CPCC420017 | PP | OR | PENDLETON | BUCKAROO | TR_345803_886280548 | 2007 | Before | 2007-05-31 16:17 | 2007-05-31 17:25 | 1 | 68.167 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: refused transformer, squrrel | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 616425 | CPCC | CPCC416590 | PP | OR | PENDLETON | BUCKAROO | TR_164740_619850499 | 2007 | Before | 2007-05-04 07:49 | 2007-05-04 08:34 | 1 | 44.633 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: refused xfmr, squirrel | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 616427 | CPCC | CPCC416592 | PP | OR | PENDLETON | BUCKAROO | TR_164841_619850498 | 2007 | Before | 2007-05-04 08:16 | 2007-05-04 08:34 | 1 | 18.167 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: refused xfmr, squirrel | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 628876 | CPCC | CPCC431172 | PP | OR | PENDLETON | BUCKAROO | TR_211982_752850181 | 2007 | Before | 2007-07-21 22:42 | 2007-07-22 01:01 | 1 | 139.75 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: bad ug pri this customer is being accounted for in outage # 431169 | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 628877 | CPCC | CPCC431173 | PP | OR | PENDLETON | BUCKAROO | OH_211900_752850180 | 2007 | Before | 2007-07-21 22:44 | 2007-07-22 03:44 | 16 | 3155.367 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: bad ug pri | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8247 | 45.6454
5W202 | 629281 | CPCC | CPCC432686 | PP | OR | PENDLETON | BUCKAROO | TR_161380_619850384 | 2007 | Before | 2007-08-01 11:06 | 2007-08-01 14:26 | 1 | 199.783 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | PROSPER: Crew is enroute to make repairs to a B/O underground secondary service. repairs complete and customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 626493 | CPCC | CPCC426287 | PP | OR | PENDLETON | BUCKAROO | TR_211606_752850229 | 2007 | Before | 2007-07-10 08:27 | 2007-07-10 09:32 | 2 | 131.233 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer # 211606 and it held, the cause was a squrrel, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 629306 | CPCC | CPCC429674 | PP | OR | PENDLETON | BUCKAROO | OH_270302_886280424 | 2007 | Before | 2007-07-15 19:05 | 2007-07-15 20:20 | 100 | 7476.667 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Open line fuse on pole 270302. Serviceman patrolling. No cause found, refused and customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8067 | 45.6209
5W202 | 629307 | CPCC | CPCC429675 | PP | OR | PENDLETON | BUCKAROO | TR_344600_886280534 | 2007 | Before | 2007-07-15 19:13 | 2007-07-15 20:21 | 1 | 67.933 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Asscoiated with outage 429674. Bad connectivity in CADOPS. Transformer is off of C phase and should be off of A phase. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 629308 | CPCC | CPCC429676 | PP | OR | PENDLETON | BUCKAROO | TR_343101_886280486 | 2007 | Before | 2007-07-15 19:12 | 2007-07-15 20:21 | 1 | 68.433 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Asscoiated with outage 429674. Bad connectivity in CADOPS. Transformer is off of C phase and should be off of A phase. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 629309 | CPCC | CPCC429679 | PP | OR | PENDLETON | BUCKAROO | TR_274204_886280442 | 2007 | Before | 2007-07-15 19:13 | 2007-07-15 20:21 | 1 | 67.133 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Asscoiated with outage 429674. Bad connectivity in CADOPS. Transformer is off of C phase and should be off of A phase. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 629310 | CPCC | CPCC429680 | PP | OR | PENDLETON | BUCKAROO | TR_276080_886280280 | 2007 | Before | 2007-07-15 19:15 | 2007-07-15 20:21 | 1 | 65.717 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Asscoiated with outage 429674. Bad connectivity in CADOPS. Transformer is off of C phase and should be off of A phase. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 629311 | CPCC | CPCC429684 | PP | OR | PENDLETON | BUCKAROO | TR_348702_886280573 | 2007 | Before | 2007-07-15 19:17 | 2007-07-15 20:21 | 1 | 63.467 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Asscoiated with outage 429674. Bad connectivity in CADOPS. Transformer is off of C phase and should be off of A phase. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 629312 | CPCC | CPCC429685 | PP | OR | PENDLETON | BUCKAROO | TR_346680_886280558 | 2007 | Before | 2007-07-15 19:16 | 2007-07-15 20:21 | 1 | 64.367 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Asscoiated with outage 429674. Bad connectivity in CADOPS. Transformer is off of C phase and should be off of A phase. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 629314 | CPCC | CPCC429693 | PP | OR | PENDLETON | BUCKAROO | TR_345500_886280563 | 2007 | Before | 2007-07-15 19:25 | 2007-07-15 20:21 | 1 | 55.65 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Asscoiated with outage 429674. Bad connectivity in CADOPS. Transformer is off of C phase and should be off of A phase. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 629316 | CPCC | CPCC429697 | PP | OR | PENDLETON | BUCKAROO | TR_274203_886280441 | 2007 | Before | 2007-07-15 19:58 | 2007-07-15 20:21 | 1 | 22.167 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Asscoiated with outage 429674. Bad connectivity in CADOPS. Transformer is off of C phase and should be off of A phase. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 629320 | CPCC | CPCC429705 | PP | OR | PENDLETON | BUCKAROO | TR_345803_886280548 | 2007 | Before | 2007-07-15 19:12 | 2007-07-15 20:21 | 1 | 68.533 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Asscoiated with outage 429674. Bad connectivity in CADOPS. Transformer is off of C phase and should be off of A phase. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 629321 | CPCC | CPCC429706 | PP | OR | PENDLETON | BUCKAROO | TR_344602_886280564 | 2007 | Before | 2007-07-15 19:25 | 2007-07-15 20:21 | 3 | 166.1 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Asscoiated with outage 429674. Bad connectivity in CADOPS. Transformer is off of C phase and should be off of A phase. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 626949 | CPCC | CPCC424973 | PP | OR | PENDLETON | BUCKAROO | TR_160604_619850519 | 2007 | Before | 2007-07-04 08:53 | 2007-07-04 09:35 | 5 | 210.333 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 160604 and it held, the cause was a squirrel, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 627379 | CPCC | CPCC432434 | PP | OR | PENDLETON | BUCKAROO | TR_343541_886280511 | 2007 | Before | 2007-07-30 08:56 | 2007-07-30 09:35 | 1 | 39.317 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: svcman reports squirrel caused the trf cutout fuse to blow. Squirrel cleared, cutout fuse replaced and customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 627784 | CPCC | CPCC430901 | PP | OR | PENDLETON | BUCKAROO | TR_164841_619850498 | 2007 | Before | 2007-07-20 12:05 | 2007-07-20 12:59 | 10 | 546.167 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transfomer# 164841 and it held, the cause was a squirrel, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 628601 | CPCC | CPCC431069 | PP | OR | PENDLETON | BUCKAROO | TR_137901_842710191 | 2007 | Before | 2007-07-21 09:55 | 2007-07-21 11:00 | 1 | 65.167 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Squirrel blew fuse. Refused transfromer and customer is back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 629050 | CPCC | CPCC429665 | PP | OR | PENDLETON | BUCKAROO | TR_344502_886280565 | 2007 | Before | 2007-07-15 19:05 | 2007-07-15 20:21 | 1 | 75.317 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Asscoiated with outage 429674. Bad connectivity in CADOPS. Transformer is off of C phase and should be off of A phase. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 629051 | CPCC | CPCC429666 | PP | OR | PENDLETON | BUCKAROO | TR_348700_886280571 | 2007 | Before | 2007-07-15 19:06 | 2007-07-15 20:21 | 1 | 74.6 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Asscoiated with outage 429674. Bad connectivity in CADOPS. Transformer is off of C phase and should be off of A phase. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 629053 | CPCC | CPCC429669 | PP | OR | PENDLETON | BUCKAROO | TR_033981_762510376 | 2007 | Before | 2007-07-15 19:08 | 2007-07-15 20:21 | 1 | 72.067 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Asscoiated with outage 429674. Bad connectivity in CADOPS. Transformer is off of C phase and should be off of A phase. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 627063 | CPCC | CPCC427066 | PP | OR | PENDLETON | BUCKAROO | TR_161440_619850403 | 2007 | Before | 2007-07-11 07:36 | 2007-07-11 08:11 | 4 | 141.6 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 161440 and it held, the cause was a squirrel, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 624742 | CPCC | CPCC424620 | PP | OR | PENDLETON | BUCKAROO | OH_210603_1550004111 | 2007 | Before | 2007-07-02 07:19 | 2007-07-02 08:09 | 25 | 1234.167 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Associate to outage# 424621. These A phase customers were not out of power, Serviceman refused the B phase tapline at pole# 210603 and it held, some of these customers are not modeled correctly in cadops. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8264 | 45.6411
5W202 | 624743 | CPCC | CPCC424621 | PP | OR | PENDLETON | BUCKAROO | OH_210603_1550004111 | 2007 | Before | 2007-07-02 07:17 | 2007-07-02 08:09 | 65 | 3171.033 | 0 | 0 | 2 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused the B phase tapline at pole# 210603 and it held, some of these customers are not modeled correctly in cadops. The cause was a squirrel. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8264 | 45.6411
5W202 | 625600 | CPCC | CPCC425466 | PP | OR | PENDLETON | BUCKAROO | OH_211902_1550257187 | 2007 | Before | 2007-07-06 09:48 | 2007-07-06 10:00 | 42 | 531.3 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | CONSTRUCTION |  |  | PLANNED OUTAGE |  |  |  | PROSPER: crew doing load swapping. this dip has been temp put on A phase due to loading. do not know at this time weather is is perm or not. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8249 | 45.6454
5W202 | 625602 | CPCC | CPCC425471 | PP | OR | PENDLETON | BUCKAROO | OH_212902_1550257177 | 2007 | Before | 2007-07-06 10:01 | 2007-07-06 10:03 | 0 | 0 | 47 | 94.783 | 1 | Y | N | N | N | N |  | PLANNED | CONSTRUCTION |  |  | PLANNED OUTAGE |  |  |  | PROSPER: crew doing load swapping. this dip has been temp put on A phase due to loading. do not know at this time weather is is perm or not. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8238 | 45.6454
5W202 | 609604 | CPCC | CPCC411517 | PP | OR | PENDLETON | BUCKAROO | TR_085500_802520469 | 2007 | Before | 2007-03-26 08:31 | 2007-03-26 09:18 | 1 | 46.75 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD SUSPECTED, NO MORTALITY |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: per svcman bird 'do-do' caused trf fuse to blow. svcman replaced the fuse and customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 610045 | CPCC | CPCC414403 | PP | OR | PENDLETON | BUCKAROO | TR_164542_619850488 | 2007 | Before | 2007-04-14 11:59 | 2007-04-14 12:43 | 1 | 43.483 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Squirrel | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 609252 | CPCC | CPCC410131 | PP | OR | PENDLETON | BUCKAROO | BCK_CB5W202 | 2007 | Before | 2007-03-12 17:45 | 2007-03-12 23:39 | 1511 | 482950.9 | 0 | 0 | 2 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | OTHER SUB (EXPLAIN IN COMMENTS) |  |  |  | PROSPER: Squirrel on substation Bus work damaging insulators | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8367 | 45.6762
5W202 | 610935 | CPCC | CPCC415331 | PP | OR | PENDLETON | BUCKAROO | TR_084600_802520491 | 2007 | Before | 2007-04-23 13:31 | 2007-04-23 14:36 | 1 | 64.883 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 084600 and it held, the cause was a squirrel, Customer is back in full service, they might have a possible claim for a damaged compressor. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 606587 | CPCC | CPCC409780 | PP | OR | PENDLETON | BUCKAROO | TR_192201_886280336 | 2007 | Before | 2007-03-09 14:56 | 2007-03-09 15:49 | 2 | 107 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: svcman replaced b/o trf cutout, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 648189 | CPCC | CPCC454382 | PP | OR | PENDLETON | BUCKAROO | TR_214300_752850166 | 2007 | Before | 2007-11-12 18:29 | 2007-11-12 21:03 | 1 | 153.75 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 648964 | CPCC | CPCC464256 | PP | OR | PENDLETON | BUCKAROO | TR_179660_886280346 | 2007 | Before | 2007-12-06 17:55 | 2007-12-06 19:15 | 1 | 79.95 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: replaced bad fuse | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 644147 | CPCC | CPCC442357 | PP | OR | PENDLETON | BUCKAROO | TR_139203_842710174 | 2007 | Before | 2007-09-15 19:13 | 2007-09-15 20:17 | 1 | 63.6 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 648290 | CPCC | CPCC451349 | PP | OR | PENDLETON | BUCKAROO | TR_085500_802520469 | 2007 | Before | 2007-10-31 10:18 | 2007-10-31 11:06 | 1 | 47.85 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 085500 and it held, the cause was a squirrel, customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 647622 | CPCC | CPCC451286 | PP | OR | PENDLETON | BUCKAROO | TR_070102_802520533 | 2007 | Before | 2007-10-30 14:06 | 2007-10-30 15:00 | 1 | 53.9 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: squirrel | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 645625 | CPCC | CPCC451720 | PP | OR | PENDLETON | BUCKAROO | OH_163501_619850475 | 2007 | Before | 2007-11-03 15:09 | 2007-11-03 17:00 | 25 | 2764.583 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Squirell blown line fuse | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8213 | 45.6534
5W202 | 638422 | CPCC | CPCC441293 | PP | OR | PENDLETON | BUCKAROO | TR_343202_886280489 | 2007 | Before | 2007-09-06 13:11 | 2007-09-06 13:49 | 1 | 37.4 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | POLE OH |  |  |  | PROSPER: Associate to outage# 441305. B/O connectivity in cadops, mapping change made. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 638423 | CPCC | CPCC441294 | PP | OR | PENDLETON | BUCKAROO | TR_344701_886280555 | 2007 | Before | 2007-09-06 13:18 | 2007-09-06 13:50 | 1 | 32.233 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | POLE OH |  |  |  | PROSPER: Assocaite to outage# 441305. B/O connectivity in cadops, mapping change made. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 638425 | CPCC | CPCC441304 | PP | OR | PENDLETON | BUCKAROO | TR_344805_886280310 | 2007 | Before | 2007-09-06 13:26 | 2007-09-06 13:49 | 1 | 22.633 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | POLE OH |  |  |  | PROSPER: Associate to outage# 441305. B/O connectivity in cadops, mapping change made. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 638426 | CPCC | CPCC441305 | PP | OR | PENDLETON | BUCKAROO | OH_270302_886280424 | 2007 | Before | 2007-09-06 13:12 | 2007-09-06 14:12 | 160 | 6541.5 | 0 | 0 | 2 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | POLE OH |  |  |  | PROSPER: Crew isolated the carhit pole and customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8067 | 45.6209
5W202 | 643340 | CPCC | CPCC442252 | PP | OR | PENDLETON | BUCKAROO | TR_165843_619850638 | 2007 | Before | 2007-09-14 10:43 | 2007-09-14 11:19 | 10 | 356.833 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 165843 and it held, the cause was a squirrel, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 643341 | CPCC | CPCC442253 | PP | OR | PENDLETON | BUCKAROO | TR_166840_619850633 | 2007 | Before | 2007-09-14 10:50 | 2007-09-14 11:20 | 1 | 29.7 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Associate to outage# 442252. B/O connectivity in cadops, mapping change made. Serviceman refused transformer# 165843 and it held, the cause was a squirrel, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 638175 | CPCC | CPCC441292 | PP | OR | PENDLETON | BUCKAROO | TR_343001_886280484 | 2007 | Before | 2007-09-06 13:16 | 2007-09-06 13:48 | 1 | 32.5 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | POLE OH |  |  |  | PROSPER: Associate to outage# 441305. B/O connectivity in cadops, mapping change made. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 654854 | CPCC | CPCC464482 | PP | OR | PENDLETON | BUCKAROO | OH_278500_886280419 | 2007 | Before | 2007-12-07 10:37 | 2007-12-07 15:03 | 9 | 2401.5 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | SNOW, SLEET AND BLIZZARD |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Crew needed to make reparis to the overhead primary that was taken down by snow load. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.7904 | 45.624
5W202 | 654528 | CPCC | CPCC471753 | PP | OR | PENDLETON | BUCKAROO | TR_273102_886280454 | 2008 | Before | 2008-01-04 09:31 | 2008-01-04 18:40 | 1 | 549.433 | 0 | 0 | 1 | Y | N | N | N | Y | 711 - 2008-01-04 to 2008-01-04 OR Pendlteton | WEATHER | WIND |  |  | TRANSFORMER OH |  |  |  | PROSPER: Refuse - held - power restored | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 650883 | CPCC | CPCC462941 | PP | OR | PENDLETON | BUCKAROO | TR_087300_802520473 | 2007 | Before | 2007-12-03 18:46 | 2007-12-03 20:32 | 1 | 105.083 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Line fuse was blown, no cause found. Refused and customer is back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 634888 | CPCC | CPCC434675 | PP | OR | PENDLETON | BUCKAROO | TR_161440_619850403 | 2007 | Before | 2007-08-12 06:34 | 2007-08-12 07:43 | 1 | 68.667 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: squirell blown cut out | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 675385 | CPCC | CPCC498120 | PP | OR | PENDLETON | BUCKAROO | TR_272100_886280447 | 2008 | Before | 2008-04-27 12:34 | 2008-04-27 13:22 | 1 | 48.25 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 675879 | CPCC | CPCC502014 | PP | OR | PENDLETON | BUCKAROO | OH_163501_619850475 | 2008 | Before | 2008-05-16 07:22 | 2008-05-16 08:45 | 62 | 5178.033 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: squirrel blew transformer fuse and line fuse. Refused both of them and they held. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8213 | 45.6534
5W202 | 671067 | CPCC | CPCC491135 | PP | OR | PENDLETON | BUCKAROO | TR_274204_886280442 | 2008 | Before | 2008-03-05 10:38 | 2008-03-05 11:35 | 5 | 285 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 274204 and it held, the cause was a squirrel. Customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 675502 | CPCC | CPCC505664 | PP | OR | PENDLETON | BUCKAROO | TR_163309_619850408 | 2008 | Before | 2008-06-10 17:21 | 2008-06-10 18:43 | 5 | 407.75 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: squirrel | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 665330 | CPCC | CPCC488081 | PP | OR | PENDLETON | BUCKAROO | OH_210603_1550004111 | 2008 | Before | 2008-02-07 06:03 | 2008-02-07 08:12 | 90 | 11625 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: Repaired burned open connector | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8264 | 45.6411
5W202 | 665344 | CPCC | CPCC488611 | PP | OR | PENDLETON | BUCKAROO | TR_165747_619850635 | 2008 | Before | 2008-02-10 18:05 | 2008-02-10 19:08 | 1 | 63.533 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | CONNECTOR OH |  |  |  | PROSPER: Made repairs to broken service neutral on transformer side due to tree limb. Made repairs and customer is back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 665882 | CPCC | CPCC488150 | PP | OR | PENDLETON | BUCKAROO | TR_164405_619850434 | 2008 | Before | 2008-02-07 10:21 | 2008-02-07 11:10 | 1 | 49.033 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Serviceman made repairs the customers overhead secondary service neutral that was broken at the weatherhead, customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 679408 | CPCC | CPCC505547 | PP | OR | PENDLETON | BUCKAROO | TR_072000_802520536 | 2008 | Before | 2008-06-10 05:19 | 2008-06-10 05:49 | 1 | 30.4 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: Broken primary lead on transformer. Made repairs and customers are back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 679410 | CPCC | CPCC505549 | PP | OR | PENDLETON | BUCKAROO | TR_165645_619850618 | 2008 | Before | 2008-06-10 05:35 | 2008-06-10 08:35 | 1 | 179.8 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Service wire down in back yard. GF knows and will send serviceman | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 679412 | CPCC | CPCC505552 | PP | OR | PENDLETON | BUCKAROO | OH_162042_619850311 | 2008 | Before | 2008-06-10 05:52 | 2008-06-10 08:30 | 55 | 7486.85 | 0 | 0 | 2 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: Line fuse is open. Serviceman is patrolling. squriell damaged the cutout on pole# 162401. Crew changed out and all customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8234 | 45.6459
5W202 | 682688 | CPCC | CPCC509614 | PP | OR | PENDLETON | BUCKAROO | TR_212903_752850204 | 2008 | Before | 2008-06-30 15:47 | 2008-06-30 16:40 | 1 | 52.383 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: open neutral conn | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 681930 | CPCC | CPCC510739 | PP | OR | PENDLETON | BUCKAROO | OH_289701_886280471 | 2008 | Before | 2008-07-06 11:01 | 2008-07-06 14:09 | 7 | 605.85 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: cut out | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8093 | 45.6266
5W202 | 679105 | CPCC | CPCC505316 | PP | OR | PENDLETON | BUCKAROO | TR_211501_752850239 | 2008 | Before | 2008-06-09 09:38 | 2008-06-09 10:53 | 3 | 225.75 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman replaced a B/O fuse on pole# 211501 and it held, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 680461 | CPCC | CPCC508161 | PP | OR | PENDLETON | BUCKAROO | TR_070101_802520532 | 2008 | Before | 2008-06-28 08:53 | 2008-06-28 09:55 | 3 | 186.5 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: squirrel refuse transformer | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 682961 | CPCC | CPCC509653 | PP | OR | PENDLETON | BUCKAROO | TR_162905_619850462 | 2008 | Before | 2008-06-30 16:56 | 2008-06-30 18:21 | 1 | 85.267 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Associate to outage# 509747.Serviceman removed a limb from the overhead primary and closed FR# 5W490 and it held, the cause was a tree limb that came out of a tree due to high wind. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 682972 | CPCC | CPCC509747 | PP | OR | PENDLETON | BUCKAROO | RC_087504_802520343 | 2008 | Before | 2008-06-30 16:43 | 2008-06-30 18:20 | 1259 | 122227.917 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman removed a limb from the overhead primary and closed FR# 5W490 and it held, the cause was a tree limb that came out of a tree due to high wind. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8323 | 45.6669
5W202 | 681755 | CPCC | CPCC506414 | PP | OR | PENDLETON | BUCKAROO | TR_163309_619850408 | 2008 | Before | 2008-06-18 06:43 | 2008-06-18 07:11 | 5 | 136.833 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: serviceman refused transformer 163309 and held squirrel was cause | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 682593 | CPCC | CPCC506748 | PP | OR | PENDLETON | BUCKAROO | TR_342301_886280493 | 2008 | Before | 2008-06-20 07:49 | 2008-06-20 08:36 | 1 | 47.033 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 342301 and it held, the cause was a squirrel, customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 681413 | CPCC | CPCC511547 | PP | OR | PENDLETON | BUCKAROO | TR_167744_619850617 | 2008 | Before | 2008-07-09 09:01 | 2008-07-09 10:18 | 16 | 1217.867 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 167744 and it held, the cause was a squirrel, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 683049 | CPCC | CPCC511250 | PP | OR | PENDLETON | BUCKAROO | TR_288703_886280474 | 2008 | Before | 2008-07-08 07:21 | 2008-07-08 08:10 | 1 | 48.283 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: squirell | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 663070 | CPCC | CPCC483757 | PP | OR | PENDLETON | BUCKAROO | OH_215360_752850152 | 2008 | Before | 2008-01-27 18:24 | 2008-01-28 00:49 | 8 | 2023.5 | 0 | 0 | 2 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | SNOW, SLEET AND BLIZZARD | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Crew completed repairs to wire down due to trees with heavy snow. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8158 | 45.6361
5W202 | 700322 | CPCC | CPCC530996 | PP | OR | PENDLETON | BUCKAROO | TR_129002_842710155 | 2008 | Before | 2008-11-08 17:57 | 2008-11-08 22:13 | 1 | 256 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Bird removed. Refused and holding. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 700533 | CPCC | CPCC531907 | PP | OR | PENDLETON | BUCKAROO | TR_164745_619850494 | 2008 | Before | 2008-11-16 11:36 | 2008-11-16 12:49 | 1 | 73 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | PROSPER: Replaced connectors | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 701422 | CPCC | CPCC530675 | PP | OR | PENDLETON | BUCKAROO | TR_212600_752850228 | 2008 | Before | 2008-11-06 13:01 | 2008-11-06 15:25 | 2 | 288.367 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 212600 and it held, the cause was a squirrel, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 699064 | CPCC | CPCC526154 | PP | OR | PENDLETON | BUCKAROO | TR_214602_752850243 | 2008 | Before | 2008-10-09 09:12 | 2008-10-09 10:12 | 3 | 180.5 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Refused transformer due to starling. Power restored | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 699485 | CPCC | CPCC530814 | PP | OR | PENDLETON | BUCKAROO | RC_087504_802520343 | 2008 | Before | 2008-11-07 08:30 | 2008-11-07 09:20 | 1265 | 63123.5 | 0 | 0 | 1 | Y | N | Y | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman removed a squirrel and refused transformer# 214500 and it held, there was a saftey hold on FR#5W490 and it locked out, Customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8323 | 45.6669
5W202 | 694238 | CPCC | CPCC522083 | PP | OR | PENDLETON | BUCKAROO | TR_161906_619850524 | 2008 | Before | 2008-09-10 09:50 | 2008-09-10 10:13 | 7 | 161.933 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 161906 and it held, the cause was a squirrel, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 691801 | CPCC | CPCC517868 | PP | OR | PENDLETON | BUCKAROO | TR_073204_802520527 | 2008 | Before | 2008-08-18 10:53 | 2008-08-18 11:46 | 2 | 106.533 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused transformer# 073204 and it held, the cause a B/O fuse, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 695975 | CPCC | CPCC520705 | PP | OR | PENDLETON | BUCKAROO | TR_215100_752850164 | 2008 | Before | 2008-09-02 08:44 | 2008-09-02 09:22 | 4 | 150.333 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 215100 and it held, the cause was a squirrel, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 695208 | CPCC | CPCC525712 | PP | OR | PENDLETON | BUCKAROO | OH_211900_752850180 | 2008 | Before | 2008-10-05 19:20 | 2008-10-06 03:27 | 16 | 4629.567 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: b/o ug | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8247 | 45.6454
5W202 | 694427 | CPCC | CPCC521697 | PP | OR | PENDLETON | BUCKAROO | OH_274105_1550180141 | 2008 | Before | 2008-09-07 11:19 | 2008-09-07 12:29 | 124 | 8671.733 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.797 | 45.6189
5W202 | 695661 | CPCC | CPCC524243 | PP | OR | PENDLETON | BUCKAROO | TR_164646_619850484 | 2008 | Before | 2008-09-25 09:22 | 2008-09-25 10:40 | 3 | 233.5 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: Serviceman changed out a B/O cutout on pole# 164646, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 695684 | CPCC | CPCC524542 | PP | OR | PENDLETON | BUCKAROO | OH_211900_752850180 | 2008 | Before | 2008-09-28 18:24 | 2008-09-28 22:14 | 16 | 2603.1 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: bad ug Primary crew to repair | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8247 | 45.6454
5W202 | 689964 | CPCC | CPCC520630 | PP | OR | PENDLETON | BUCKAROO | OH_344702_886280554 | 2008 | Before | 2008-09-01 13:29 | 2008-09-01 20:39 | 4 | 1572.4 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: Crew needed to make repairs to the B/O underground primary between? | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.7969 | 45.6122
5W202 | 692463 | CPCC | CPCC520014 | PP | OR | PENDLETON | BUCKAROO | TR_164003_619850329 | 2008 | Before | 2008-08-27 10:49 | 2008-08-27 11:51 | 1 | 61.817 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: Serviceman replaced the B/O secondary connections at the pole, customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 691686 | CPCC | CPCC515863 | PP | OR | PENDLETON | BUCKAROO | TR_210900_752850177 | 2008 | Before | 2008-08-07 09:34 | 2008-08-07 11:35 | 2 | 241.667 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | PROSPER: Crew changed out a B/O transformer on pole# 210900, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 707470 | CPCC | CPCC535896 | PP | OR | PENDLETON | BUCKAROO | RC_072201_802520342 | 2008 | Before | 2008-12-16 05:53 | 2008-12-16 07:05 | 75 | 5397.5 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Had to open recloser in order to get line back up. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8664 | 45.6634
5W202 | 705863 | CPCC | CPCC555427 | PP | OR | PENDLETON | BUCKAROO | OH_079600_802520520 | 2009 | Before | 2009-03-02 14:24 | 2009-03-02 15:24 | 10 | 331.233 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | INSULATOR OH |  |  |  | PROSPER: Serviceman found a floater. Crew to make repairs. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8514 | 45.6691
5W202 | 707216 | CPCC | CPCC535892 | PP | OR | PENDLETON | BUCKAROO | RC_072201_802520342 | 2008 | Before | 2008-12-16 02:56 | 2008-12-16 07:05 | 178 | 36483.767 | 0 | 0 | 2 | Y | N | N | N | N |  | WEATHER | ICE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Line down. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8664 | 45.6634
5W202 | 704852 | CPCC | CPCC556184 | PP | OR | PENDLETON | BUCKAROO | TR_162401_619850405 | 2009 | Before | 2009-03-08 09:26 | 2009-03-08 10:37 | 1 | 71.783 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: squirell blown fuse | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 704853 | CPCC | CPCC556185 | PP | OR | PENDLETON | BUCKAROO | TR_162404_619850406 | 2009 | Before | 2009-03-08 09:30 | 2009-03-08 10:37 | 1 | 67.183 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: squirell blown fuse | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 706897 | CPCC | CPCC556880 | PP | OR | PENDLETON | BUCKAROO | OH_119000_842710139 | 2009 | Before | 2009-03-15 06:51 | 2009-03-15 07:20 | 9 | 257.1 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Blown line fuse, patrolling line. See outage 556877 for arrival times. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.893 | 45.6614
5W202 | 705322 | CPCC | CPCC555347 | PP | OR | PENDLETON | BUCKAROO | TR_162404_619850406 | 2009 | Before | 2009-03-02 08:32 | 2009-03-02 09:18 | 2 | 91.967 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Squirrel blew transformer fuse. Serviceman replaced and customer back in servie, | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 685108 | CPCC | CPCC512937 | PP | OR | PENDLETON | BUCKAROO | TR_162144_619850431 | 2008 | Before | 2008-07-18 09:02 | 2008-07-18 09:57 | 6 | 332.4 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 162144 and it held, the cause was a squirrel, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 687185 | CPCC | CPCC513966 | PP | OR | PENDLETON | BUCKAROO | TR_165741_619850636 | 2008 | Before | 2008-07-27 20:05 | 2008-07-27 20:56 | 9 | 460.5 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer ok. Cause was squirrel. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 685559 | CPCC | CPCC515323 | PP | OR | PENDLETON | BUCKAROO | TR_345901_886280544 | 2008 | Before | 2008-08-02 12:35 | 2008-08-02 13:53 | 3 | 233.9 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: refuse transformer squirrel | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 684037 | CPCC | CPCC508028 | PP | OR | PENDLETON | BUCKAROO | TR_344800_886280272 | 2008 | Before | 2008-06-27 06:57 | 2008-06-27 07:41 | 2 | 87.733 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 344800 and it held, the cause was a squirrel, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 683239 | CPCC | CPCC509803 | PP | OR | PENDLETON | BUCKAROO | OH_274105_1550180141 | 2008 | Before | 2008-06-30 18:26 | 2008-06-30 21:57 | 111 | 23394.583 | 0 | 0 | 2 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Trees on line, removed trees off of line and refused. Customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.797 | 45.6189
5W202 | 683242 | CPCC | CPCC509816 | PP | OR | PENDLETON | BUCKAROO | OH_274105_1550180141 | 2008 | Before | 2008-06-30 19:56 | 2008-06-30 21:57 | 12 | 1451.8 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Trees on line, removed trees off of line and refused. Customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.797 | 45.6189
5W202 | 683244 | CPCC | CPCC509822 | PP | OR | PENDLETON | BUCKAROO | TR_212501_752850236 | 2008 | Before | 2008-06-30 20:10 | 2008-06-30 22:44 | 1 | 153.917 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: service cut in clear, till repairs made | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 685874 | CPCC | CPCC515499 | PP | OR | PENDLETON | BUCKAROO | TR_359700_886280381 | 2008 | Before | 2008-08-05 07:25 | 2008-08-05 08:34 | 3 | 208.75 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Servicman refused transformer# 359700 and it held, the cause was a squirrel, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 686693 | CPCC | CPCC515583 | PP | OR | PENDLETON | BUCKAROO | OH_216160_752850163 | 2008 | Before | 2008-08-05 14:07 | 2008-08-05 17:50 | 8 | 1140.933 | 0 | 0 | 2 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | ANIMALS | ANIMALS | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Crew needed to make repairs to the overhead primary that was taken down by a tree that was fallen by a beaver. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8147 | 45.6336
5W202 | 683420 | CPCC | CPCC507049 | PP | OR | PENDLETON | BUCKAROO | TR_342301_886280493 | 2008 | Before | 2008-06-21 07:58 | 2008-06-21 08:47 | 1 | 48.55 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 726449 | CPCC | CPCC578394 | PP | OR | PENDLETON | BUCKAROO | OH_343003_1550180119 | 2009 | Before | 2009-07-29 01:01 | 2009-07-29 04:20 | 32 | 6372.8 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: Crew isolated B/O U/G primary cable and restored all load at 0420. Crew completed making repairs at 0520. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8 | 45.6019
5W202 | 722217 | CPCC | CPCC570503 | PP | OR | PENDLETON | BUCKAROO | TR_342302_886280492 | 2009 | Before | 2009-06-10 08:21 | 2009-06-10 09:19 | 2 | 115.8 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused transformer# 342302 and it held, the cause is unknown, customers are back in full service. Serviceman installed a bird guard to prevent this from happening again. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 726698 | CPCC | CPCC578404 | PP | OR | PENDLETON | BUCKAROO | TR_164507_619850467 | 2009 | Before | 2009-07-29 06:04 | 2009-07-29 07:04 | 5 | 296.5 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: squirrel, refused transformer, power on | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 725596 | CPCC | CPCC576989 | PP | OR | PENDLETON | BUCKAROO | TR_129001_842710154 | 2009 | Before | 2009-07-22 11:42 | 2009-07-22 13:02 | 2 | 160.833 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 129001 and it held, the cause was a squirrel, customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 716354 | CPCC | CPCC534524 | PP | OR | PENDLETON | BUCKAROO | TR_342302_886280492 | 2008 | Before | 2008-12-10 08:48 | 2008-12-10 11:13 | 2 | 289.1 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Squirrel | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 720834 | CPCC | CPCC569930 | PP | OR | PENDLETON | BUCKAROO | OH_138904_842710193 | 2009 | Before | 2009-06-04 21:49 | 2009-06-05 03:43 | 34 | 12054.7 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8758 | 45.6587
5W202 | 715994 | CPCC | CPCC540471 | PP | OR | PENDLETON | BUCKAROO | TR_164541_619850489 | 2008 | Before | 2008-12-22 15:35 | 2008-12-22 16:03 | 1 | 27.6 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Car hit pole, bad connectivity in cad-ops, associate to outage # 540467 | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 719662 | CPCC | CPCC566081 | PP | OR | PENDLETON | BUCKAROO | OH_211900_752850180 | 2009 | Before | 2009-05-22 16:03 | 2009-05-22 20:01 | 16 | 2264.933 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: Bad order primary UG cable. Made repairs and customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8247 | 45.6454
5W202 | 718877 | CPCC | CPCC544252 | PP | OR | PENDLETON | BUCKAROO | RC_072201_802520342 | 2008 | Before | 2008-12-29 13:12 | 2008-12-29 15:58 | 178 | 29589.533 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | POLE FIRE | POLE OH |  |  |  | PROSPER: Burning pole top. Had to open to make repairs. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8664 | 45.6634
5W202 | 720903 | CPCC | CPCC564263 | PP | OR | PENDLETON | BUCKAROO | OH_165740_619850637 | 2009 | Before | 2009-05-06 16:42 | 2009-05-06 19:20 | 59 | 9320.033 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8166 | 45.6568
5W202 | 720908 | CPCC | CPCC564277 | PP | OR | PENDLETON | BUCKAROO | OH_165740_619850637 | 2009 | Before | 2009-05-06 19:02 | 2009-05-06 19:20 | 138 | 2394.3 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8166 | 45.6568
5W202 | 720909 | CPCC | CPCC564278 | PP | OR | PENDLETON | BUCKAROO | TR_163745_619850500 | 2009 | Before | 2009-05-06 19:03 | 2009-05-06 19:21 | 1 | 18 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 720910 | CPCC | CPCC564279 | PP | OR | PENDLETON | BUCKAROO | TR_163640_619850502 | 2009 | Before | 2009-05-06 19:05 | 2009-05-06 19:21 | 11 | 178.017 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 720912 | CPCC | CPCC564283 | PP | OR | PENDLETON | BUCKAROO | TR_166840_619850633 | 2009 | Before | 2009-05-06 19:16 | 2009-05-06 19:21 | 0 | 0 | 1 | 4.35 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 720913 | CPCC | CPCC564285 | PP | OR | PENDLETON | BUCKAROO | OH_165740_619850637 | 2009 | Before | 2009-05-06 19:20 | 2009-05-06 19:21 | 0 | 0 | 138 | 151.8 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8166 | 45.6568
5W202 | 720914 | CPCC | CPCC564286 | PP | OR | PENDLETON | BUCKAROO | TR_166850_619850629 | 2009 | Before | 2009-05-06 19:22 | 2009-05-06 20:11 | 1 | 49.6 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 720915 | CPCC | CPCC564287 | PP | OR | PENDLETON | BUCKAROO | OH_165740_619850637 | 2009 | Before | 2009-05-06 19:22 | 2009-05-06 19:23 | 0 | 0 | 138 | 200.1 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8166 | 45.6568
5W202 | 720916 | CPCC | CPCC564290 | PP | OR | PENDLETON | BUCKAROO | TR_165645_619850618 | 2009 | Before | 2009-05-06 19:26 | 2009-05-06 20:11 | 1 | 44.967 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 720917 | CPCC | CPCC564291 | PP | OR | PENDLETON | BUCKAROO | OH_162701_619850507 | 2009 | Before | 2009-05-06 19:22 | 2009-05-06 20:10 | 210 | 10160.5 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8224 | 45.6559
5W202 | 719710 | CPCC | CPCC567996 | PP | OR | PENDLETON | BUCKAROO | TR_033781_762510379 | 2009 | Before | 2009-06-02 14:30 | 2009-06-02 17:33 | 1 | 183.45 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | DIG-IN (NON-PACIFICORP PERSONNEL) |  |  | SECONDARY CABLE UG |  |  |  | PROSPER: Serviceman needs another crew member to help make repairs to a secondary service that was dug into. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 720555 | CPCC | CPCC569797 | PP | OR | PENDLETON | BUCKAROO | OH_216160_752850163 | 2009 | Before | 2009-06-04 20:22 | 2009-06-05 04:36 | 9 | 4446 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Blown line fuse, cause was lightning. Refused and customer are back on | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8147 | 45.6336
5W202 | 720664 | CPCC | CPCC565425 | PP | OR | PENDLETON | BUCKAROO | TR_215201_752850157 | 2009 | Before | 2009-05-17 07:18 | 2009-05-17 10:31 | 1 | 192.633 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | PROSPER: Bad cutout and transformer, Crew to replace, Wilkerson, Wanous | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 720287 | CPCC | CPCC569623 | PP | OR | PENDLETON | BUCKAROO | Line Cut-35388 | 2009 | Before | 2009-06-04 19:10 | 2009-06-05 02:57 | 69 | 32240.25 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: primary down repalced primary | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8173 | 45.6576
5W202 | 721190 | CPCC | CPCC564964 | PP | OR | PENDLETON | BUCKAROO | OH_211900_752850180 | 2009 | Before | 2009-05-13 01:53 | 2009-05-13 05:17 | 16 | 3264 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Blown dip fuse, all cable tested good. No cause found. Refused and customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8247 | 45.6454
5W202 | 732440 | CPCC | CPCC561163 | PP | OR | PENDLETON | BUCKAROO | TR_215100_752850164 | 2009 | Before | 2009-04-15 14:04 | 2009-04-15 15:11 | 4 | 270 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused transformer# 215100 and it held, the cause is unknown, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 730870 | CPCC | CPCC570666 | PP | OR | PENDLETON | BUCKAROO | TR_134401_842710182 | 2009 | Before | 2009-06-11 15:53 | 2009-06-11 21:22 | 2 | 659.033 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Wilkerson/Wanous/McCormack was completed at 1900 | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 731740 | CPCC | CPCC574598 | PP | OR | PENDLETON | BUCKAROO | TR_166746_619850619 | 2009 | Before | 2009-07-07 17:58 | 2009-07-07 19:20 | 1 | 82.35 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Tree rubbed on service and it burnt down. Made repairs and customers are back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 729787 | CPCC | CPCC562759 | PP | OR | PENDLETON | BUCKAROO | Line Cut-34673 | 2009 | Before | 2009-04-28 12:23 | 2009-04-28 13:35 | 8 | 577.2 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | POLE FIRE | POLE OH |  |  |  | PROSPER: Serviceman opened the jumper at pole# 229701 to clear a pole fire, serviceman is going to get help to reframe the pole lower to get the customers on until the pole can be replaced. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.7882 | 45.6414
5W202 | 729788 | CPCC | CPCC562760 | PP | OR | PENDLETON | BUCKAROO | OH_277500_886280420 | 2009 | Before | 2009-04-28 12:26 | 2009-04-28 12:31 | 0 | 0 | 12 | 50.8 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | POLE OH |  |  |  | PROSPER: While serviceman was trying to lift the jumpers the pole top burnt off and the wire fell, tapline fuses at pole# 277500 blew, serviceman refused and they held | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.7906 | 45.6244
5W202 | 733802 | CPCC | CPCC569946 | PP | OR | PENDLETON | BUCKAROO | TR_288502_886280466 | 2009 | Before | 2009-06-05 06:08 | 2009-06-05 10:14 | 1 | 246.833 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Serviceman made repairs to the overhead secondary service and cut it in the clear until the customer makes repairs to their equipment. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 731471 | CPCC | CPCC574542 | PP | OR | PENDLETON | BUCKAROO | OH_343003_1550180119 | 2009 | Before | 2009-07-07 09:45 | 2009-07-07 11:24 | 32 | 3156.267 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: Blown dip fuse. Serviceman investigating. B/O primary between pad mount 033680 and normal open on 033681. Line has been switched out and all customers back in service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8 | 45.6019
5W202 | 734318 | CPCC | CPCC566554 | PP | OR | PENDLETON | BUCKAROO | TR_129000_842710152 | 2009 | Before | 2009-05-27 08:44 | 2009-05-27 09:45 | 4 | 246 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 129000 and it held, the cause was a starling, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 709865 | CPCC | CPCC559077 | PP | OR | PENDLETON | BUCKAROO | TR_164403_619850437 | 2009 | Before | 2009-03-31 16:20 | 2009-03-31 16:53 | 5 | 165.5 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND | EQUIPMENT FAILURE | B/O EQUIPMENT | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: broken jumper | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 713140 | CPCC | CPCC557183 | PP | OR | PENDLETON | BUCKAROO | TR_136402_842710180 | 2009 | Before | 2009-03-16 09:12 | 2009-03-16 10:31 | 1 | 78.483 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman found blown xfmr fuse. He refused and it held. No cause found. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 711599 | CPCC | CPCC533599 | PP | OR | PENDLETON | BUCKAROO | TR_211909_752850201 | 2008 | Before | 2008-12-03 10:50 | 2008-12-03 12:27 | 3 | 290.75 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 211909 and it held, the cause was a squirrel, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 714480 | CPCC | CPCC556346 | PP | OR | PENDLETON | BUCKAROO | TR_162401_619850405 | 2009 | Before | 2009-03-09 10:31 | 2009-03-09 11:29 | 1 | 57.467 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: serviceman found squirrel, refused transformer | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 750002 | CPCC | CPCC599088 | PP | OR | PENDLETON | BUCKAROO | TR_273105_886280452 | 2009 | Before | 2009-11-18 15:42 | 2009-11-18 16:20 | 1 | 37.067 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 273105 and it held, the cause was a squirrel, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 749257 | CPCC | CPCC602395 | PP | OR | PENDLETON | BUCKAROO | TR_162401_619850405 | 2009 | Before | 2009-12-01 15:22 | 2009-12-01 16:15 | 1 | 52.183 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman found an open transformer fuse at pole# 162404 due to a squirrel, refused and it held, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 749258 | CPCC | CPCC602397 | PP | OR | PENDLETON | BUCKAROO | TR_162404_619850406 | 2009 | Before | 2009-12-01 15:31 | 2009-12-01 16:15 | 2 | 88.8 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Associate to outage# 602395. Serviceman found an open transformer fuse at pole# 162404 due to a squirrel, refused and it held, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 750189 | CPCC | CPCC595053 | PP | OR | PENDLETON | BUCKAROO | RC_072201_802520342 | 2009 | Before | 2009-10-26 13:26 | 2009-10-26 14:29 | 177 | 11162.8 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Crew onsite making repairs to the overhead primary that was taken down by a tree. Customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8664 | 45.6634
5W202 | 748305 | CPCC | CPCC582593 | PP | OR | PENDLETON | BUCKAROO | TR_164540_619850492 | 2009 | Before | 2009-08-16 09:15 | 2009-08-16 09:46 | 1 | 30.767 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 741265 | CPCC | CPCC584516 | PP | OR | PENDLETON | BUCKAROO | TR_161905_619850525 | 2009 | Before | 2009-08-27 12:59 | 2009-08-27 14:08 | 4 | 276.933 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Blown x-fmr fuse on pole# 161905 due to bird (starling). Serviceman replaced fuse and fuse held. Customers back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 754698 | CPCC | CPCC624596 | PP | OR | PENDLETON | BUCKAROO | TR_164649_619850485 | 2010 | Before | 2010-03-29 11:54 | 2010-03-29 17:45 | 5 | 1754.75 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Tree branch fell on secondary service affecting 923 Sw 33rd St. Serviceman cut secondary in clear and crew will make repairs. (not all customers on xfmr are affected, CADOPS rolled calls up to device level) | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 756852 | CPCC | CPCC628500 | PP | OR | PENDLETON | BUCKAROO | OH_138904_842710193 | 2010 | Before | 2010-04-17 22:15 | 2010-04-17 23:29 | 23 | 1691.267 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: serviceman ask for help to patrol, line fuse open, found phases crossed, repaired, refused line fuse, power on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8758 | 45.6587
5W202 | 758495 | CPCC | CPCC619807 | PP | OR | PENDLETON | BUCKAROO | RC_072201_802520342 | 2010 | Before | 2010-02-28 18:45 | 2010-02-28 21:37 | 178 | 25007.466 | 0 | 0 | 2 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Field Recloser 5W502 is locked open. Primary conductor down, cause is unknown. Repairs made and customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8664 | 45.6634
5W202 | 739648 | CPCC | CPCC580949 | PP | OR | PENDLETON | BUCKAROO | TR_359700_886280381 | 2009 | Before | 2009-08-06 07:48 | 2009-08-06 09:30 | 3 | 307.9 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 359700 and it held, the cause was a starling, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 738468 | CPCC | CPCC588778 | PP | OR | PENDLETON | BUCKAROO | TR_212400_752850171 | 2009 | Before | 2009-09-22 09:24 | 2009-09-22 11:59 | 4 | 620.6 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 212400 and it held, the cause was a squirrel, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 736964 | CPCC | CPCC580505 | PP | OR | PENDLETON | BUCKAROO | TR_213702_752850222 | 2009 | Before | 2009-08-04 08:25 | 2009-08-04 09:04 | 3 | 116.55 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Squirrel blew xfmr fuse. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 737087 | CPCC | CPCC586220 | PP | OR | PENDLETON | BUCKAROO | OH_211900_752850180 | 2009 | Before | 2009-09-07 07:37 | 2009-09-07 11:05 | 16 | 2197.333 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: Crew needed to make repairs to the B/O underground primary between transformer# 211981 and transformer# 211982. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8247 | 45.6454
5W202 | 777054 | CPCC | CPCC636481 | PP | OR | PENDLETON | BUCKAROO | OH_138904_842710193 | 2010 | Before | 2010-05-24 03:40 | 2010-05-24 07:33 | 40 | 9281.333 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD SUSPECTED, NO MORTALITY |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Crew to put pri. wire back up. Believe cause was due to bird slapping phases together. Work complete. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8758 | 45.6587
5W202 | 775857 | CPCC | CPCC632166 | PP | OR | PENDLETON | BUCKAROO | TR_348801_886280572 | 2010 | Before | 2010-05-03 20:27 | 2010-05-03 22:18 | 1 | 110.9 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: Serviceman repaired the B/O jumper on pole# 348801. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 777910 | CPCC | CPCC647204 | PP | OR | PENDLETON | BUCKAROO | Line Cut-44282 | 2010 | Before | 2010-07-28 13:24 | 2010-07-28 15:15 | 1527 | 169853.3 | 0 | 0 | 1 | Y | N | N | N | Y | 910 - 2010-07-28 to 2010-07-28 OR Pendleton | LOSS OF SUPPLY | LOSS OF FEED FROM SUPPLIER |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Loss of feed from BPA. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8368 | 45.676
5W202 | 778029 | CPCC | CPCC643956 | PP | OR | PENDLETON | BUCKAROO | TR_343001_886280484 | 2010 | Before | 2010-07-15 10:39 | 2010-07-15 11:20 | 1 | 40.817 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | POLE OH |  |  |  | PROSPER: Associate to outage# 643968. B/O mapping in cadops, mapping change made. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 778031 | CPCC | CPCC643963 | PP | OR | PENDLETON | BUCKAROO | TR_343302_1550003716 | 2010 | Before | 2010-07-15 10:46 | 2010-07-15 11:20 | 1 | 34 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | POLE OH |  |  |  | PROSPER: Associate to outage# 643968. B/O mapping in cadops, mapping change made. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 778033 | CPCC | CPCC643965 | PP | OR | PENDLETON | BUCKAROO | TR_343202_886280489 | 2010 | Before | 2010-07-15 10:49 | 2010-07-15 11:20 | 1 | 30.617 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | POLE OH |  |  |  | PROSPER: Associate to outage# 643968. B/O mapping in cadops, mapping change made. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 778035 | CPCC | CPCC643968 | PP | OR | PENDLETON | BUCKAROO | OH_270302_886280424 | 2010 | Before | 2010-07-15 10:29 | 2010-07-15 14:39 | 159 | 13926.283 | 0 | 0 | 2 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | POLE OH |  |  |  | PROSPER: Crew needed to replace a carhit pole. Customers are back in full service | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8067 | 45.6209
5W202 | 777318 | CPCC | CPCC636502 | PP | OR | PENDLETON | BUCKAROO | TR_343541_886280511 | 2010 | Before | 2010-05-24 09:11 | 2010-05-24 10:27 | 1 | 76.033 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: Crew replaced a cutout on pole# 343541 that was damaged by a squirrel, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 778093 | CPCC | CPCC636070 | PP | OR | PENDLETON | BUCKAROO | OH_138904_842710193 | 2010 | Before | 2010-05-21 00:58 | 2010-05-21 02:42 | 23 | 2400.05 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Blown line fuse. Patrolled and did not find anything. Refused and customers are back on. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8758 | 45.6587
5W202 | 771790 | CPCC | CPCC640516 | PP | OR | PENDLETON | BUCKAROO | TR_166746_619850619 | 2010 | Before | 2010-06-26 17:04 | 2010-06-26 18:21 | 1 | 77.2 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: limb on service | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 769460 | CPCC | CPCC619835 | PP | OR | PENDLETON | BUCKAROO | OH_119000_842710139 | 2010 | Before | 2010-03-01 06:34 | 2010-03-01 08:00 | 20 | 1731.333 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD SUSPECTED, NO MORTALITY |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Blown line fuse. (No cause found but serviceman suspects it was a bird. There was no carcass but geese were roosting on a cliff near the line). Serviceman replaced fuse and fuse held. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.893 | 45.6614
5W202 | 772327 | CPCC | CPCC640594 | PP | OR | PENDLETON | BUCKAROO | TR_164547_619850472 | 2010 | Before | 2010-06-27 11:44 | 2010-06-27 17:43 | 1 | 359.2 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | PROSPER: bad transformer | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 767569 | CPCC | CPCC606742 | PP | OR | PENDLETON | BUCKAROO | TR_213900_752850254 | 2009 | Before | 2009-12-15 10:12 | 2009-12-15 12:19 | 1 | 126.533 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: Serviceman replaced the B/O secondary connections at the weatherhead, customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 771146 | CPCC | CPCC645511 | PP | OR | PENDLETON | BUCKAROO | TR_129000_842710152 | 2010 | Before | 2010-07-21 19:54 | 2010-07-21 21:49 | 1 | 115.183 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: replaced cut out | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 772059 | CPCC | CPCC640561 | PP | OR | PENDLETON | BUCKAROO | OH_163501_619850475 | 2010 | Before | 2010-06-27 07:38 | 2010-06-27 08:38 | 26 | 1545.267 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: line fuse bad | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8213 | 45.6534
5W202 | 771700 | CPCC | CPCC639457 | PP | OR | PENDLETON | BUCKAROO | OH_165740_619850637 | 2010 | Before | 2010-06-16 14:22 | 2010-06-16 16:34 | 139 | 18292.4 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Crew made reparis to the overhead primary that was taken down by fault current caused by a squirrel that got on top of a transformer, customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8166 | 45.6568
5W202 | 782510 | CPCC | CPCC646019 | PP | OR | PENDLETON | BUCKAROO | OH_344702_886280554 | 2010 | Before | 2010-07-25 02:09 | 2010-07-25 10:49 | 4 | 1952.067 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: bad u/g primary. Crew to make repairs. Crew found 2 bad spots. Between Dip and 1st transformer and between 1st transformer and 2nd transformer. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.7969 | 45.6122
5W202 | 784103 | CPCC | CPCC633194 | PP | OR | PENDLETON | BUCKAROO | TR_164405_619850434 | 2010 | Before | 2010-05-11 20:27 | 2010-05-11 22:40 | 3 | 397.8 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: replaced grass hopper cut out | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 784159 | CPCC | CPCC633797 | PP | OR | PENDLETON | BUCKAROO | TR_163280_619850396 | 2010 | Before | 2010-05-18 10:02 | 2010-05-18 12:16 | 1 | 134.083 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | PROSPER: Serviceman and another journeyman are installing the service saver due to a B/O underground secondary. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 785363 | CPCC | CPCC638209 | PP | OR | PENDLETON | BUCKAROO | TR_273101_886280446 | 2010 | Before | 2010-06-09 10:44 | 2010-06-09 12:03 | 2 | 158.167 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transfomer# 273101 and it held, the cause was a squirrel, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 784190 | CPCC | CPCC642931 | PP | OR | PENDLETON | BUCKAROO | BCK_CB5W202 | 2010 | Before | 2010-07-09 06:21 | 2010-07-09 06:21 | 0 | 0 | 1527 | 407.2 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: T and R. the cause was a squirrel that got on top of a transformer and damaged the cutout. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8367 | 45.6762
5W202 | 781435 | CPCC | CPCC638019 | PP | OR | PENDLETON | BUCKAROO | OH_138904_842710193 | 2010 | Before | 2010-06-07 04:27 | 2010-06-07 07:14 | 40 | 6678 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (PROTECTED SPECIES) (BMTS) |  |  | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: Wire down, crew to put wire back up in the air, replace line fuses. Peilicans caused outage. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8758 | 45.6587
5W202 | 782015 | CPCC | CPCC632627 | PP | OR | PENDLETON | BUCKAROO | TR_137704_842710188 | 2010 | Before | 2010-05-07 10:26 | 2010-05-07 11:27 | 2 | 122.167 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: left message at 1030, serviceman located open fuse @ FP# 137704, trouble shooting, found no cause, outage restored | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 784426 | CPCC | CPCC633864 | PP | OR | PENDLETON | BUCKAROO | TR_164647_619850483 | 2010 | Before | 2010-05-18 16:12 | 2010-05-18 17:24 | 5 | 361.667 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: squirrel , replaced fuse | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 784440 | CPCC | CPCC642935 | PP | OR | PENDLETON | BUCKAROO | TR_070101_802520532 | 2010 | Before | 2010-07-09 07:13 | 2010-07-09 08:01 | 3 | 143.2 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: Servicemen are onsite replacing a cutout on pole# 070101 that was damaged by a squirrel, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 780091 | CPCC | CPCC636670 | PP | OR | PENDLETON | BUCKAROO | OH_085804_802520495 | 2010 | Before | 2010-05-25 14:34 | 2010-05-25 16:22 | 7 | 759.167 | 0 | 0 | 2 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused the tapline fuses at pole# 085804 and they held, the cause is unknown, customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8378 | 45.6721
5W202 | 784448 | CPCC | CPCC642953 | PP | OR | PENDLETON | BUCKAROO | TR_163300_619850417 | 2010 | Before | 2010-07-09 06:58 | 2010-07-09 10:06 | 6 | 1129.8 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: Servicemen onsite replacing a cutout on pole# 163300 that was damaged by a squirrel. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 766565 | CPCC | CPCC620528 | PP | OR | PENDLETON | BUCKAROO | OH_152600_842710111 | 2010 | Before | 2010-03-05 19:27 | 2010-03-05 23:04 | 17 | 3695.233 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: blown line fuse on pole 152600 | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.928 | 45.6547
5W202 | 766566 | CPCC | CPCC620529 | PP | OR | PENDLETON | BUCKAROO | TR_164200_842710093 | 2010 | Before | 2010-03-05 19:58 | 2010-03-05 23:03 | 1 | 185.5 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: should be on B phase blown line fuse on pole 152600 | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 766570 | CPCC | CPCC620534 | PP | OR | PENDLETON | BUCKAROO | TR_151780_842710116 | 2010 | Before | 2010-03-05 22:19 | 2010-03-05 23:03 | 1 | 44.017 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: should be on be b phase blown line fuse on pole 152600 | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 765183 | CPCC | CPCC622521 | PP | OR | PENDLETON | BUCKAROO | OH_152600_842710111 | 2010 | Before | 2010-03-19 13:52 | 2010-03-19 15:07 | 21 | 1571.85 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused the tapline fuse at pole# 152600 and it held, the cause is unknown, customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.928 | 45.6547
5W202 | 765184 | CPCC | CPCC622522 | PP | OR | PENDLETON | BUCKAROO | TR_029100_836510012 | 2010 | Before | 2010-03-19 14:11 | 2010-03-19 15:07 | 1 | 55.75 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Associate to outage# 622521. Serviceman refused the tapline fuse at pole# 152600 and it held, the cause is unknown, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 800845 | CPCC | CPCC660995 | PP | OR | PENDLETON | BUCKAROO | TR_071203_802520539 | 2010 | Before | 2010-10-24 12:45 | 2010-10-24 13:57 | 1 | 72.45 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: tree limb knocked fuse door open. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 799777 | CPCC | CPCC650850 | PP | OR | PENDLETON | BUCKAROO | OH_343003_1550180119 | 2010 | Before | 2010-08-19 09:11 | 2010-08-19 10:35 | 32 | 2696.533 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Associate to outage# 650864, this outage got verified by mistake, Serviceman found an open tapline fuse at pole# 274105, he is patrolling | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8 | 45.6019
5W202 | 804451 | CPCC | CPCC678852 | PP | OR | PENDLETON | BUCKAROO | RC_087504_802520343 | 2011 | Before | 2011-02-10 13:49 | 2011-02-10 14:28 | 1265 | 48976.583 | 0 | 0 | 1 | Y | N | Y | N | N |  | ANIMALS | ANIMALS |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: Serviceman verified field recloser is locked out. Service heading to call (customer heard a loud bang) to investigate. Serviceman patrolled line, no cause found. (Outage end time should be 14:28) Crew found a broken cut-out that was damaged by a squirrel | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8323 | 45.6669
5W202 | 800203 | CPCC | CPCC654858 | PP | OR | PENDLETON | BUCKAROO | TR_163644_619850481 | 2010 | Before | 2010-09-18 15:52 | 2010-09-18 17:03 | 6 | 423 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: squirrel, serviceman refused | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 803699 | CPCC | CPCC659822 | PP | OR | PENDLETON | BUCKAROO | TR_273102_886280454 | 2010 | Before | 2010-10-19 15:03 | 2010-10-19 15:54 | 4 | 206.667 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: serviceman located open transformer fuse due to squirrel, investigated for damage, none found, refused, refused outage restored | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 803804 | CPCC | CPCC665418 | PP | OR | PENDLETON | BUCKAROO | OH_138904_842710193 | 2010 | Before | 2010-11-19 10:10 | 2010-11-19 12:23 | 24 | 3182.8 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused the tapline fuse at pole# 138904 and it held, the cause is unknown, customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8758 | 45.6587
5W202 | 802339 | CPCC | CPCC652569 | PP | OR | PENDLETON | BUCKAROO | TR_070102_802520533 | 2010 | Before | 2010-08-31 15:53 | 2010-08-31 17:07 | 6 | 442.6 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 070102 and it held, the cause was a squirrel, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 801183 | CPCC | CPCC665647 | PP | OR | PENDLETON | BUCKAROO | TR_164545_619850474 | 2010 | Before | 2010-11-21 12:17 | 2010-11-21 12:53 | 6 | 217.3 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Blown tansformer fuse, cause was squirrel. Refused and customers are back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 796478 | CPCC | CPCC668099 | PP | OR | PENDLETON | BUCKAROO | TR_344401_886280483 | 2010 | Before | 2010-12-02 09:50 | 2010-12-02 10:25 | 1 | 35.15 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Blown x-fmr fuse (no cause found) Servicman replaced fuse and it held. Customer back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 795751 | CPCC | CPCC656639 | PP | OR | PENDLETON | BUCKAROO | TR_162144_619850431 | 2010 | Before | 2010-09-30 09:39 | 2010-09-30 10:47 | 6 | 408.5 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 162144 and it held, the cause was a squirrel, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 795782 | CPCC | CPCC650864 | PP | OR | PENDLETON | BUCKAROO | OH_274105_1550180141 | 2010 | Before | 2010-08-19 09:11 | 2010-08-19 10:35 | 97 | 8173.867 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused the tapline fuse at pole# 274105, and it held the cause is unknown, customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.797 | 45.6189
5W202 | 792209 | CPCC | CPCC663444 | PP | OR | PENDLETON | BUCKAROO | BCK_CB5W202 | 2010 | Before | 2010-11-06 10:24 | 2010-11-06 10:24 | 0 | 0 | 1533 | 383.25 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: T & R | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8367 | 45.6762
5W202 | 798328 | CPCC | CPCC668742 | PP | OR | PENDLETON | BUCKAROO | OH_216160_752850163 | 2010 | Before | 2010-12-07 20:36 | 2010-12-07 22:51 | 9 | 1212.6 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | ANIMALS | ANIMALS | PRIMARY CONDUCTOR OH |  |  |  | PROSPER: bever fell a tree through the line | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8147 | 45.6336
5W202 | 793185 | CPCC | CPCC664826 | PP | OR | PENDLETON | BUCKAROO | TR_164441_619850439 | 2010 | Before | 2010-11-16 06:47 | 2010-11-16 08:06 | 4 | 316.8 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 164441 and it held, the cause was wind that blew the high side jumper into the pole. Customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 806245 | CPCC | CPCC698824 | PP | OR | PENDLETON | BUCKAROO | TR_229101_752850145 | 2011 | Before | 2011-03-28 09:58 | 2011-03-28 11:39 | 1 | 100.783 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | POLE OH |  |  |  | PROSPER: modeled incorrectly due improper location in CAAD OPs, need crew to verify if customer is at correct location(10:38), associated to outage# 698810, customer has power | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 807425 | CPCC | CPCC687971 | PP | OR | PENDLETON | BUCKAROO | TR_162144_619850431 | 2011 | Before | 2011-03-12 09:53 | 2011-03-12 11:04 | 6 | 427.6 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman arrived, found squirrel on xfrmr and requested second man. Removed squirrel and put squirrel guard on closed fuse in and it held. Outage restored | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 804717 | CPCC | CPCC678898 | PP | OR | PENDLETON | BUCKAROO | TR_273200_886280435 | 2011 | Before | 2011-02-10 16:35 | 2011-02-10 17:53 | 1 | 77.933 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS | EQUIPMENT FAILURE | B/O EQUIPMENT | CUT-OUT B/O OH |  |  |  | PROSPER: blown fuse and damaged cut-out due to squirrel. Crew to replace cut-out. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 805998 | CPCC | CPCC698810 | PP | OR | PENDLETON | BUCKAROO | OH_277500_886280420 | 2011 | Before | 2011-03-28 08:10 | 2011-03-28 11:39 | 21 | 2197.7 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | POLE OH |  |  |  | PROSPER: serviceman located open fuse @ FP# 277500, patroling for cause/damage(09:01), located burned pole top @ FP# 229200, lifting Jumper @ FP# 229101 to isolate, step restored(09:37)crew assigned for repairs/restored(09:37) completed, outage restored | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.7906 | 45.6244
5W202 | 806398 | CPCC | CPCC676792 | PP | OR | PENDLETON | BUCKAROO | TR_070102_802520533 | 2011 | Before | 2011-01-19 20:58 | 2011-01-19 21:53 | 1 | 54.35 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | PROSPER: replaced deteriorated connector at the weatherhead | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 786355 | CPCC | CPCC637068 | PP | OR | PENDLETON | BUCKAROO | OH_138904_842710193 | 2010 | Before | 2010-05-28 02:59 | 2010-05-28 05:05 | 40 | 5040 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD SUSPECTED, NO MORTALITY |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Pelican was on the road when serviceman was on site it was alive at that time when he patrolled the line and went back to the site bird was gone2 of three fuses blown open the other fuse was opened till it was patroled and re-fused | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8758 | 45.6587
5W202 | 789925 | CPCC | CPCC662340 | PP | OR | PENDLETON | BUCKAROO | OH_343003_1550180119 | 2010 | Before | 2010-10-31 00:05 | 2010-10-31 02:41 | 32 | 5016 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: Blown dip fuse, Bad primary UG, switched bad section out, customers back on | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8 | 45.6019
5W202 | 786365 | CPCC | CPCC637091 | PP | OR | PENDLETON | BUCKAROO | TR_167744_619850617 | 2010 | Before | 2010-05-28 10:39 | 2010-05-28 11:26 | 1 | 47.75 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: Serviceman replaced a B/O secondary connection at the weatherhead, customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 789559 | CPCC | CPCC655631 | PP | OR | PENDLETON | BUCKAROO | TR_164440_619850441 | 2010 | Before | 2010-09-22 06:56 | 2010-09-22 07:51 | 7 | 383.133 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused transformer# 164440 and it held, the cause was a rotted fuse, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 788802 | CPCC | CPCC661992 | PP | OR | PENDLETON | BUCKAROO | TR_212903_752850204 | 2010 | Before | 2010-10-27 14:36 | 2010-10-27 15:08 | 4 | 129.867 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused transformer# 212903 and it held, the cause is unknown, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 788445 | CPCC | CPCC649828 | PP | OR | PENDLETON | BUCKAROO | TR_344804_886280512 | 2010 | Before | 2010-08-15 09:05 | 2010-08-15 09:28 | 2 | 44.6 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: starling. refused xfmr | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 825853 | CPCC | CPCC706402 | PP | OR | PENDLETON | BUCKAROO | TR_164001_619850324 | 2011 | Before | 2011-05-24 12:14 | 2011-05-24 13:12 | 1 | 58.233 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: Serviceman replaced secondary connector. Customer back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 829842 | CPCC | CPCC705802 | PP | OR | PENDLETON | BUCKAROO | Line Cut-50017 | 2011 | Before | 2011-05-17 08:25 | 2011-05-17 09:37 | 90 | 4714.367 | 0 | 0 | 2 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman onsite refused transformer# 163645 and the tapline fuse at pole# 166846 that were open due to a squirrel. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8141 | 45.657
5W202 | 826749 | CPCC | CPCC708262 | PP | OR | PENDLETON | BUCKAROO | TR_342301_886280493 | 2011 | Before | 2011-06-12 07:56 | 2011-06-12 09:05 | 1 | 68.217 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Blown fuse, cause squirrel. Refused and customer is back on. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 827268 | CPCC | CPCC703822 | PP | OR | PENDLETON | BUCKAROO | TR_342300_886280497 | 2011 | Before | 2011-05-01 08:58 | 2011-05-01 10:46 | 1 | 108.433 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | CUT-OUT B/O OH |  |  |  | PROSPER: Squirrel. Replaced cutout | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 824211 | CPCC | CPCC705094 | PP | OR | PENDLETON | BUCKAROO | TR_162044_619850457 | 2011 | Before | 2011-05-12 12:30 | 2011-05-12 13:50 | 6 | 476.6 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 162044 and it held, the cause was a squirrel, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 821523 | CPCC | CPCC700784 | PP | OR | PENDLETON | BUCKAROO | TR_271304_886280432 | 2011 | Before | 2011-04-11 09:25 | 2011-04-11 13:39 | 1 | 253.783 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | PROSPER: Serviceman found a B/O underground secondary service he will call for help and make repairs. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 819144 | CPCC | CPCC674878 | PP | OR | PENDLETON | BUCKAROO | TR_129003_842710151 | 2011 | Before | 2011-01-07 16:16 | 2011-01-07 16:52 | 1 | 36.217 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | PROSPER: Semi truck tore service down and damaged customers mast. Customer needs to have electrician make repairs. Case# 11-49 | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 821621 | CPCC | CPCC713995 | PP | OR | PENDLETON | BUCKAROO | TR_228501_752850149 | 2011 | Before | 2011-07-27 12:33 | 2011-07-27 13:13 | 2 | 79.767 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 228501 and it held, the cause was a small bird, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 822414 | CPCC | CPCC701548 | PP | OR | PENDLETON | BUCKAROO | TR_175800_842710092 | 2011 | Before | 2011-04-17 14:28 | 2011-04-17 15:46 | 1 | 77.967 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman arrived and found deteriorated fuse on bank. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 833049 | CPCC | CPCC710584 | PP | OR | PENDLETON | BUCKAROO | TR_073204_802520527 | 2011 | Before | 2011-06-27 17:40 | 2011-06-27 18:22 | 1 | 42.117 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: fuse blown, squirrel, fuse replaced, customer power on | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 832283 | CPCC | CPCC709759 | PP | OR | PENDLETON | BUCKAROO | TR_162404_619850406 | 2011 | Before | 2011-06-21 18:58 | 2011-06-21 20:14 | 3 | 227.8 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Squirrel on transformer blew transformer fuse, fuse replaced, customer power restored. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 832663 | CPCC | CPCC712335 | PP | OR | PENDLETON | BUCKAROO | TR_346801_886280550 | 2011 | Before | 2011-07-13 09:02 | 2011-07-13 11:26 | 2 | 287.3 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused transformer# 346801 and it held, the cause was a rotted fuse, customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 833898 | CPCC | CPCC702093 | PP | OR | PENDLETON | BUCKAROO | OH_344702_886280554 | 2011 | Before | 2011-04-21 15:29 | 2011-04-21 20:57 | 4 | 1308.8 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | PROSPER: Crew to make repairs to the B/O undeground primary. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.7969 | 45.6122
5W202 | 833229 | CPCC | CPCC713112 | PP | OR | PENDLETON | BUCKAROO | OH_271300_1550180129 | 2011 | Before | 2011-07-20 06:10 | 2011-07-20 07:30 | 46 | 3689.967 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused the tapline fuse at pole# 271300 and it held, the cause was a squirrel, customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8035 | 45.6209
5W202 | 816596 | CPCC | CPCC672709 | PP | OR | PENDLETON | BUCKAROO | TR_126200_842710161 | 2010 | Before | 2010-12-26 12:34 | 2010-12-26 14:07 | 1 | 92.833 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | PROSPER: bad order connector at weatherhead | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 859277 | CPCC | CPCC730253 | PP | OR | PENDLETON | BUCKAROO | OH_211901_752850172 | 2011 | Before | 2011-11-16 19:23 | 2011-11-16 22:01 | 60 | 9500 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown line fuse, serviceman is patrolling. Patrolled and did not find a cause. Fuse melted out. Refused and customers are back on. | DISTRIBUTION | DEVICE | AUTO | 2011-11-16 22:30 | COMPLETED |  | 2011-11-16 19:27 | 2011-11-16 22:01 | 2011-11-16 22:04 | -118.8248 | 45.6453
5W202 | 854611 | CPCC | CPCC727547 | PP | OR | PENDLETON | BUCKAROO | OH_138904_842710193 | 2011 | Before | 2011-10-28 10:46 | 2011-10-28 11:41 | 27 | 1484.1 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman refused the tapline fuse at pole# 138904 and it held, the cause is unknown, customers are back in full service. | DISTRIBUTION | DEVICE | AUTO | 2011-10-28 14:00 | COMPLETED |  | 2011-10-28 11:01 | 2011-10-28 11:48 | 2011-10-28 11:59 | -118.8758 | 45.6587
5W202 | 860786 | CPCC | CPCC731686 | PP | OR | PENDLETON | BUCKAROO | TR_164540_619850492 | 2011 | Before | 2011-11-22 12:13 | 2011-11-22 13:52 | 2 | 196.967 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman refused transformer# 164540 and it held, the cause was a squirrel, customers are back in full service. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2011-11-22 15:15 | COMPLETED |  | 2011-11-22 12:13 | 2011-11-22 13:52 | 2011-11-22 14:11 | -118.8177 | 45.6537
5W202 | 844792 | CPCC | CPCC717193 | PP | OR | PENDLETON | BUCKAROO | TR_270304_886280433 | 2011 | Before | 2011-08-14 07:33 | 2011-08-14 11:06 | 1 | 212.717 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman arrived and found deteriorated xfrmr fuse, replaced and outage restored. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 844471 | CPCC | CPCC718358 | PP | OR | PENDLETON | BUCKAROO | TR_273105_886280452 | 2011 | Before | 2011-08-23 15:42 | 2011-08-23 17:14 | 1 | 91.883 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 273105 and it held, the cause was a squirrel. Customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 843772 | CPCC | CPCC716983 | PP | OR | PENDLETON | BUCKAROO | TR_162045_619850432 | 2011 | Before | 2011-08-12 07:14 | 2011-08-12 07:56 | 4 | 170.933 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 162045 and it held, the cause was a squirrel, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 843435 | CPCC | CPCC718449 | PP | OR | PENDLETON | BUCKAROO | TR_249601_842710104 | 2011 | Before | 2011-08-24 12:49 | 2011-08-24 14:43 | 2 | 227.4 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Serviceman refused transformer# 249601 and it held, the cause is unknown, customer is back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 844262 | CPCC | CPCC717928 | PP | OR | PENDLETON | BUCKAROO | TR_070101_802520532 | 2011 | Before | 2011-08-19 09:31 | 2011-08-19 10:39 | 4 | 271.267 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman refused transformer# 070101 and it held the cause was a squirrel, customers are back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 858737 | CPCC | CPCC729939 | PP | OR | PENDLETON | BUCKAROO | TR_137705_842710099 | 2011 | Before | 2011-11-14 09:29 | 2011-11-14 10:52 | 1 | 83.55 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Seviceman refused transformer and it held, the cause is unknown, customer is back in full service. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2011-11-14 12:30 | COMPLETED |  | 2011-11-14 09:29 | 2011-11-14 10:52 | 2011-11-14 13:53 | -118.8761 | 45.6566
5W202 | 858192 | CPCC | CPCC729583 | PP | OR | PENDLETON | BUCKAROO | TR_163241_619850419 | 2011 | Before | 2011-11-12 08:41 | 2011-11-12 13:16 | 3 | 824.35 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT | ANIMALS | ANIMALS | CUT-OUT B/O OH |  |  |  | SOURCE: blown transformer fuse squirrel, cut out failed need crew | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2011-11-12 11:45 | COMPLETED |  | 2011-11-12 08:41 | 2011-11-12 13:16 | 2011-11-12 13:18 | -118.821 | 45.6489
5W202 | 849544 | CPCC | CPCC725391 | PP | OR | PENDLETON | BUCKAROO | BCK_CB5W202 | 2011 | Before | 2011-10-12 09:48 | 2011-10-12 09:48 | 0 | 0 | 1524 | 127 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: T & R, the cause is unknown | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2011-10-12 09:48 | 2011-10-12 09:48 | 2011-10-12 14:29 | -118.8367 | 45.6762
5W202 | 856875 | CPCC | CPCC728783 | PP | OR | PENDLETON | BUCKAROO | TR_212500_752850237 | 2011 | Before | 2011-11-06 15:14 | 2011-11-06 15:55 | 3 | 121.3 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Replaced blown fuse, cause unknown | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2011-11-06 18:15 | COMPLETED |  | 2011-11-06 15:14 | 2011-11-06 15:55 | 2011-11-06 16:04 | -118.8235 | 45.6394
5W202 | 837805 | CPCC | CPCC712815 | PP | OR | PENDLETON | BUCKAROO | TR_249601_842710104 | 2011 | Before | 2011-07-17 19:29 | 2011-07-17 21:37 | 1 | 128.467 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: blown fuses, probably blown by lightning yesterday. fuses replaced, power restored. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 840567 | CPCC | CPCC720269 | PP | OR | PENDLETON | BUCKAROO | TR_162404_619850406 | 2011 | Before | 2011-09-03 11:31 | 2011-09-03 12:26 | 1 | 55.55 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: refused xfmr, unknown cause | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 838216 | CPCC | CPCC719953 | PP | OR | PENDLETON | BUCKAROO | OH_274105_1550180141 | 2011 | Before | 2011-09-01 08:11 | 2011-09-01 09:47 | 98 | 6906.967 | 0 | 0 | 2 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Serviceman onsite refusing the tapline fuse and the transformer fuse that were both open due to a squirel, customers are back in full service. | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.797 | 45.6189
5W202 | 838221 | CPCC | CPCC719965 | PP | OR | PENDLETON | BUCKAROO | TR_343301_886280490 | 2011 | Before | 2011-09-01 09:11 | 2011-09-01 09:21 | 1 | 10.2 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Associate to outage# 719953. Serviceman refused the tapline fuse at pole# 274105 and it held the cause was a squirrel that got on top of transformer# 342301. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 841415 | CPCC | CPCC716628 | PP | OR | PENDLETON | BUCKAROO | OH_166846_1550448349 | 2011 | Before | 2011-08-08 17:30 | 2011-08-08 18:48 | 90 | 7074 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: bad mapping, associated to outage716636 | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.814 | 45.657
5W202 | 841416 | CPCC | CPCC716635 | PP | OR | PENDLETON | BUCKAROO | TR_166846_619850621 | 2011 | Before | 2011-08-08 17:57 | 2011-08-08 18:50 | 4 | 214.067 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: Bad mapping, associated to outage 716636 | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 841417 | CPCC | CPCC716636 | PP | OR | PENDLETON | BUCKAROO | OH_162701_619850507 | 2011 | Before | 2011-08-08 17:32 | 2011-08-08 18:47 | 144 | 10797.6 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | PROSPER: serviceman refused cutout. no cause found | DISTRIBUTION | DEVICE |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10 | -118.8224 | 45.6559
5W202 | 841036 | CPCC | CPCC719772 | PP | OR | PENDLETON | BUCKAROO | TR_084802_802520497 | 2011 | Before | 2011-08-30 09:53 | 2011-08-30 11:29 | 2 | 191.4 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | PROSPER: returning from Weston resulting in exteneded response time,customer notified(10:06) Deteriorated jumper on xfmr cut out. 2nd man to assist for repairs.(10:46) Repairs done. Customer back in full service. | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 840680 | CPCC | CPCC719095 | PP | OR | PENDLETON | BUCKAROO | TR_073204_802520527 | 2011 | Before | 2011-08-27 15:48 | 2011-08-27 21:02 | 1 | 314.517 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD SUSPECTED, NO MORTALITY |  |  | NO DISTRIBUTION DAMAGE |  |  |  | PROSPER: Servicxeman located an arc mark on the top of xfmr. Suspects bird but unable to locate bird | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 841141 | CPCC | CPCC718194 | PP | OR | PENDLETON | BUCKAROO | TR_163280_619850396 | 2011 | Before | 2011-08-22 07:31 | 2011-08-22 10:36 | 1 | 185.067 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | PROSPER: cell(07:36), customer has check breakers, serviceman suspects faulted UG Secondary Cable, onsite w/2nd man locating, repairing, restoring(08:49), completed restored | DISTRIBUTION |  |  |  | COMPLETED |  | 2011-09-28 10:10 | 2011-09-28 10:10 | 2011-09-28 10:10
5W202 | 878897 | CPCC | CPCC745118 | PP | OR | PENDLETON | BUCKAROO | RC_072201_802520342 | 2012 | Before | 2012-01-26 13:24 | 2012-01-26 15:15 | 182 | 20104.933 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | OTHER INTERFERING OBJECT |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Crew needed to make repairs to the overhead primary that was taken down by a tin roof that flew off a hotel in a wind gust. Customers are back in full service. | DISTRIBUTION | DEVICE | MANUAL | 2012-01-26 18:00 | COMPLETED |  | 2012-01-26 13:37 | 2012-01-26 15:18 | 2012-01-26 15:22 | -118.8664 | 45.6634
5W202 | 881198 | CPCC | CPCC746777 | PP | OR | PENDLETON | BUCKAROO | TR_212603_752850209 | 2012 | Before | 2012-02-09 09:16 | 2012-02-09 10:18 | 6 | 372.1 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman refused transformer# 212603 and it held, the cause was a squirrel, customers are back in full service. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2012-02-09 09:16 | 2012-02-09 10:18 | 2012-02-09 10:41 | -118.8228 | 45.6408
5W202 | 879669 | CPCC | CPCC745666 | PP | OR | PENDLETON | BUCKAROO | OH_119000_842710139 | 2012 | Before | 2012-01-30 22:47 | 2012-01-30 23:55 | 21 | 1414 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman arrived and found open line fuse, needs second guy to help patrol.Patrolled line found nothing, closed on test and it held. Outage restored. | DISTRIBUTION | DEVICE | AUTO | 2012-01-31 02:00 | COMPLETED |  | 2012-01-30 22:47 | 2012-01-30 23:55 | 2012-01-31 09:06 | -118.893 | 45.6614
5W202 | 875412 | CPCC | CPCC740594 | PP | OR | PENDLETON | BUCKAROO | TR_164405_619850434 | 2012 | Before | 2012-01-18 05:45 | 2012-01-18 07:25 | 1 | 100.917 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman found blown fuse on transformer, replaced fuse, held reports ,leaking, need to change out at later date | DISTRIBUTION | CUSTOMER | AUTO | 2012-01-18 08:45 | COMPLETED |  | 2012-01-18 05:45 | 2012-01-23 14:41 | 2012-01-18 21:02 | -118.8196 | 45.6516
5W202 | 864588 | CPCC | CPCC733908 | PP | OR | PENDLETON | BUCKAROO | OH_344702_886280554 | 2011 | Before | 2011-12-02 07:12 | 2011-12-02 12:08 | 4 | 1184.2 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Crew needed to make repairs to the B/O underground primary between dip pole# 344702 and transformer# 346780, customers are back in full service. | DISTRIBUTION | DEVICE | MANUAL | 2011-12-02 13:00 | COMPLETED |  | 2011-12-02 07:12 | 2011-12-02 12:24 | 2011-12-02 13:11 | -118.7969 | 45.6122
5W202 | 880174 | CPCC | CPCC746110 | PP | OR | PENDLETON | BUCKAROO | TR_137704_842710188 | 2012 | Before | 2012-02-02 13:54 | 2012-02-02 16:01 | 2 | 255.467 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: Broken jumpers due to wind. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-02-02 17:00 | COMPLETED |  | 2012-02-02 13:54 | 2012-02-02 16:01 | 2012-02-02 16:11 | -118.8761 | 45.6561
5W202 | 878520 | CPCC | CPCC744816 | PP | OR | PENDLETON | BUCKAROO | OH_274105_1550180141 | 2012 | Before | 2012-01-24 22:27 | 2012-01-25 03:18 | 36 | 2241.055 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | POLE OH |  |  |  | SOURCE: Pole fire burned top of pole off and blew line fuse. Crew needed. Repairs made. | DISTRIBUTION | DEVICE | MANUAL | 2012-01-25 04:00 | COMPLETED |  | 2012-01-24 22:29 | 2012-01-27 15:53 | 2012-01-25 03:21 | -118.797 | 45.6189
5W202 | 897444 | CPCC | CPCC764175 | PP | OR | PENDLETON | BUCKAROO | TR_165645_619850618 | 2012 | Before | 2012-04-05 13:24 | 2012-04-05 16:05 | 1 | 160.65 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman states that the neutral is broken on service to house due to a tree limb, he made repairs. Serviceman trimmed the trees and the customer said they will clean them up. | DISTRIBUTION | CUSTOMER | AUTO | 2012-04-05 16:30 | COMPLETED |  | 2012-04-05 13:24 | 2012-04-05 16:05 | 2012-04-05 16:10 | -118.8164 | 45.6551
5W202 | 903894 | CPCC | CPCC768120 | PP | OR | PENDLETON | BUCKAROO | OH_124000_842710162 | 2012 | Before | 2012-05-03 17:19 | 2012-05-03 20:54 | 14 | 3009.067 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Crew arrived and found a fuse open. will investigate and report. Closed in on test and fuse held. Outage restored. | DISTRIBUTION | DEVICE | AUTO | 2012-05-03 20:30 | COMPLETED |  | 2012-05-03 17:19 | 2012-05-03 20:54 | 2012-05-04 06:35 | -118.8829 | 45.6608
5W202 | 886651 | CPCC | CPCC751227 | PP | OR | PENDLETON | BUCKAROO | OH_212902_1550257177 | 2012 | Before | 2012-02-29 06:11 | 2012-02-29 10:33 | 114 | 8875.8 | 0 | 0 | 3 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | SOURCE: Crew needed to replace the B/O transformer on pole# 210900. Customer is back in full service. PROSPER: added 46 cust to second restore from 751230 | DISTRIBUTION | DEVICE | MANUAL | 2012-02-29 10:29 | COMPLETED |  | 2012-02-29 06:16 | 2012-03-02 11:02 | 2012-02-29 11:05 | -118.8238 | 45.6454
5W202 | 897191 | CPCC | CPCC763902 | PP | OR | PENDLETON | BUCKAROO | OH_176701_842710130 | 2012 | Before | 2012-04-04 10:06 | 2012-04-04 11:44 | 10 | 977.5 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman refused the tapline fuse at pole# 176701 and it held, the cause is unknown, customers are back in full service. | DISTRIBUTION | DEVICE | AUTO | 2012-04-04 13:15 | COMPLETED |  | 2012-04-04 10:06 | 2012-04-04 11:44 | 2012-04-04 12:35 | -118.9609 | 45.6567
5W202 | 902985 | CPCC | CPCC767578 | PP | OR | PENDLETON | BUCKAROO | Line Cut-61828 | 2012 | Before | 2012-04-30 08:40 | 2012-04-30 12:06 | 4 | 824.8 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: serviceman found wire down at pole #178000, lifted the jumpers at pole179000 which feeds idle facilities, district to decide whether to remove facilities, customers back in service | DISTRIBUTION | DEVICE | MANUAL | 2012-04-30 13:15 | COMPLETED |  | 2012-04-30 08:40 | 2012-04-30 12:06 | 2012-04-30 16:15 | -119.0201 | 45.675
5W202 | 907647 | CPCC | CPCC770483 | PP | OR | PENDLETON | BUCKAROO | TR_274103_886280451 | 2012 | Before | 2012-05-20 17:47 | 2012-05-20 18:55 | 1 | 67.55 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman arrived and found b/o secondary. made repairs, outage restored. | DISTRIBUTION | CUSTOMER | AUTO | 2012-05-20 21:00 | COMPLETED |  | 2012-05-20 17:47 | 2012-05-20 18:55 | 2012-05-21 06:38 | -118.7988 | 45.6179
5W202 | 905947 | CPCC | CPCC769411 | PP | OR | PENDLETON | BUCKAROO | TR_085400_802520468 | 2012 | Before | 2012-05-14 09:54 | 2012-05-14 11:18 | 1 | 84.333 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: blown xfmr fuse due to squirrel, serviceman made all the necessary repairs, customers are back in service | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-05-14 13:00 | COMPLETED |  | 2012-05-14 09:54 | 2012-05-14 11:18 | 2012-05-14 11:55 | -118.8367 | 45.6661
5W202 | 905380 | CPCC | CPCC769151 | PP | OR | PENDLETON | BUCKAROO | OH_163501_619850475 | 2012 | Before | 2012-05-11 07:34 | 2012-05-11 09:34 | 37 | 1533.267 | 0 | 0 | 2 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman found an open transformer in a backyard, crew is enroute to investigate, tapline fuse is closed and holding. Cause of x-fmr fuse being blown was a squirrel. Crew replaced fuse and it held. | DISTRIBUTION | DEVICE | AUTO | 2012-05-11 10:45 | COMPLETED |  | 2012-05-11 07:35 | 2012-05-11 09:34 | 2012-05-11 10:00 | -118.8213 | 45.6534
5W202 | 924490 | CPCC | CPCC779458 | PP | OR | PENDLETON | BUCKAROO | BCK_CB5W202 | 2012 | Before | 2012-07-17 09:17 | 2012-07-17 09:18 | 0 | 0 | 236 | 59 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: T & R | DISTRIBUTION | DEVICE | AUTO | 2012-07-17 12:30 | COMPLETED |  | 2012-07-17 09:17 | 2012-07-17 09:18 | 2012-07-17 17:07 | -118.8367 | 45.6762
5W202 | 915770 | CPCC | CPCC774672 | PP | OR | PENDLETON | BUCKAROO | TR_273101_886280446 | 2012 | Before | 2012-06-21 11:49 | 2012-06-21 13:34 | 2 | 210.467 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown x-fmr fuse due to squirrel. Serviceman replaced fuse and it held. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-06-21 15:00 | COMPLETED |  | 2012-06-21 11:49 | 2012-06-21 13:34 | 2012-06-21 14:22 | -118.7992 | 45.6187
5W202 | 921076 | CPCC | CPCC777658 | PP | OR | PENDLETON | BUCKAROO | TR_084802_802520497 | 2012 | Before | 2012-07-09 13:27 | 2012-07-09 14:21 | 2 | 108.133 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman refused transformer# 084802 and it held, the cause was a truck that snagged the phone line and shook the pole, customer is back in full service. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-07-09 16:30 | COMPLETED |  | 2012-07-09 13:27 | 2012-07-09 14:21 | 2012-07-09 20:18 | -118.8385 | 45.6719
5W202 | 925336 | CPCC | CPCC780288 | PP | OR | PENDLETON | BUCKAROO | TR_212807_752850214 | 2012 | Before | 2012-07-19 22:55 | 2012-07-20 01:37 | 1 | 162.483 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING | TREES | TREE - NON-PREVENTABLE | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Associated to earlier outage 780284, customer has power. | DISTRIBUTION | CUSTOMER | AUTO | 2012-07-20 02:00 | COMPLETED |  | 2012-07-19 22:55 | 2012-07-20 03:24 | 2012-07-20 05:01 | -118.8231 | 45.6426
5W202 | 925349 | CPCC | CPCC780313 | PP | OR | PENDLETON | BUCKAROO | TR_160609_619850522 | 2012 | Before | 2012-07-20 02:33 | 2012-07-20 06:35 | 2 | 484.133 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | TRANSFORMER OH |  |  |  | SOURCE: Blown transformer fuse, Crew found B/O xfrmr crew needed. Replace transformer and customers are back on. | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2012-07-20 07:15 | COMPLETED |  | 2012-07-20 02:33 | 2012-07-20 06:35 | 2012-07-20 06:41 | -118.8276 | 45.6549
5W202 | 925353 | CPCC | CPCC780318 | PP | OR | PENDLETON | BUCKAROO | TR_213601_752850224 | 2012 | Before | 2012-07-20 04:13 | 2012-07-20 06:00 | 1 | 107.55 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown transformer fuse, cause lightning. Refused and customer is back on. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-07-20 07:15 | COMPLETED |  | 2012-07-20 04:13 | 2012-07-20 06:00 | 2012-07-20 06:41 | -118.8213 | 45.6404
5W202 | 929892 | CPCC | CPCC782263 | PP | OR | PENDLETON | BUCKAROO | TR_343001_886280484 | 2012 | Before | 2012-08-04 08:41 | 2012-08-04 09:23 | 1 | 42.65 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown transformer fuse, cause was starling. Refused and customer is back on. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-08-04 11:45 | COMPLETED |  | 2012-08-04 08:41 | 2012-08-04 09:23 | 2012-08-04 13:05 | -118.8008 | 45.6026
5W202 | 917356 | CPCC | CPCC775579 | PP | OR | PENDLETON | BUCKAROO | TR_349700_886280575 | 2012 | Before | 2012-06-26 19:56 | 2012-06-26 20:33 | 1 | 37.067 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman arrived and found fuse blown caused by starling. refused outage restored. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-06-26 23:00 | COMPLETED |  | 2012-06-26 19:56 | 2012-06-26 20:33 | 2012-06-27 05:42 | -118.788 | 45.6126
5W202 | 924401 | CPCC | CPCC779459 | PP | OR | PENDLETON | BUCKAROO | BCK_CB5W202 | 2012 | Before | 2012-07-17 09:18 | 2012-07-17 11:36 | 240 | 20404 | 0 | 0 | 2 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Crew onsite making repairs to the overhead primary that was taken down by lightning. Customers are back in full service. | DISTRIBUTION | DEVICE | AUTO | 2012-07-17 12:30 | COMPLETED |  | 2012-07-17 09:18 | 2012-07-17 11:39 | 2012-07-17 12:32 | -118.8367 | 45.6762
5W202 | 925319 | CPCC | CPCC780284 | PP | OR | PENDLETON | BUCKAROO | OH_214900_752850252 | 2012 | Before | 2012-07-19 22:34 | 2012-07-20 01:37 | 128 | 23409.067 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING | TREES | TREE - NON-PREVENTABLE | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown line fuse. Tree limb on line, Associated with outage 780292. | DISTRIBUTION | DEVICE | AUTO | 2012-07-20 02:00 | COMPLETED |  | 2012-07-19 22:50 | 2012-07-20 01:37 | 2012-07-20 03:01 | -118.8194 | 45.6454
5W202 | 925480 | CPCC | CPCC780326 | PP | OR | PENDLETON | BUCKAROO | TR_207400_886280326 | 2012 | Before | 2012-07-20 05:34 | 2012-07-20 12:10 | 2 | 791.233 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | TRANSFORMER OH |  |  |  | SOURCE: Bad transformer, cause lightning. Crew replaced x-fmr. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-07-20 08:45 | COMPLETED |  | 2012-07-20 05:34 | 2012-07-20 12:10 | 2012-07-20 13:52 | -118.8337 | 45.637
5W202 | 911707 | CPCC | CPCC772790 | PP | OR | PENDLETON | BUCKAROO | OH_118900_1550129157 | 2012 | Before | 2012-06-05 09:45 | 2012-06-05 13:16 | 2 | 423.467 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | OTHER INTERFERING OBJECT |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman removed the railroads bird reflectors and refused the tapline fuse at pole# 118900, customers are back in full service. | DISTRIBUTION | DEVICE | AUTO | 2012-06-05 12:45 | COMPLETED |  | 2012-06-05 09:45 | 2012-06-05 14:17 | 2012-06-05 14:20 | -119.0199 | 45.6743
5W202 | 927033 | CPCC | CPCC781002 | PP | OR | PENDLETON | BUCKAROO | TR_215100_752850164 | 2012 | Before | 2012-07-25 08:10 | 2012-07-25 15:26 | 1 | 436.183 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman onsite making repairs to the overhead secondary service that was taken down by a tree. Pump is back in full service. | DISTRIBUTION | CUSTOMER | MANUAL | 2012-07-25 16:00 | COMPLETED |  | 2012-07-25 08:10 | 2012-07-25 15:26 | 2012-07-25 15:33 | -118.8159 | 45.6332
5W202 | 926065 | CPCC | CPCC780627 | PP | OR | PENDLETON | BUCKAROO | TR_161341_619850400 | 2012 | Before | 2012-07-22 15:46 | 2012-07-22 16:37 | 1 | 50.467 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: removed tree branch | DISTRIBUTION | CUSTOMER | AUTO | 2012-07-22 19:00 | COMPLETED |  | 2012-07-22 15:46 | 2012-07-22 16:37 | 2012-07-22 17:01 | -118.8242 | 45.6501
5W202 | 915701 | CPCC | CPCC774634 | PP | OR | PENDLETON | BUCKAROO | TR_162404_619850406 | 2012 | Before | 2012-06-21 07:36 | 2012-06-21 09:59 | 3 | 430.05 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman onsite refusing the transformer that is open due to a squirrel, customers are back in full service. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-06-21 10:45 | COMPLETED |  | 2012-06-21 07:36 | 2012-06-21 09:59 | 2012-06-21 10:07 | -118.8218 | 45.6517
5W202 | 925317 | CPCC | CPCC780310 | PP | OR | PENDLETON | BUCKAROO | TR_160608_619850520 | 2012 | Before | 2012-07-19 23:10 | 2012-07-20 02:15 | 8 | 1485.2 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman arrived and found open xfrmr fuse, will test and close then report.refused and holding. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-07-20 02:15 | COMPLETED |  | 2012-07-19 23:10 | 2012-07-20 02:15 | 2012-07-20 03:01 | -118.8266 | 45.6549
5W202 | 925320 | CPCC | CPCC780292 | PP | OR | PENDLETON | BUCKAROO | OH_212902_1550257177 | 2012 | Before | 2012-07-19 22:33 | 2012-07-20 01:37 | 59 | 10846.167 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING | TREES | TREE - NON-PREVENTABLE | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Fuse blown, tree limb on line. Associated with outage 780284 | DISTRIBUTION | DEVICE | AUTO | 2012-07-20 02:15 | COMPLETED |  | 2012-07-19 23:09 | 2012-07-20 01:37 | 2012-07-20 03:01 | -118.8238 | 45.6454
5W202 | 925333 | CPCC | CPCC780316 | PP | OR | PENDLETON | BUCKAROO | TR_213702_752850222 | 2012 | Before | 2012-07-20 03:12 | 2012-07-20 04:03 | 3 | 152.25 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown transformer fuse, cause lightning. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-07-20 06:15 | COMPLETED |  | 2012-07-20 03:12 | 2012-07-20 04:03 | 2012-07-20 05:01 | -118.8215 | 45.6414
5W202 | 918224 | CPCC | CPCC775944 | PP | OR | PENDLETON | BUCKAROO | TR_164540_619850492 | 2012 | Before | 2012-06-30 10:31 | 2012-06-30 11:32 | 2 | 123.467 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown transformer fuse, cause was squirrel. Refused and customers are back on. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-06-30 13:30 | COMPLETED |  | 2012-06-30 10:31 | 2012-06-30 11:32 | 2012-06-30 16:41 | -118.8177 | 45.6537
5W202 | 1303644 | CPCC | CPCC785582 | PP | OR | PENDLETON | BUCKAROO | TR_214500_752850242 | 2012 | Before | 2012-08-23 10:46 | 2012-08-23 11:26 | 3 | 118.85 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown xfmr fuse due to a squirrel. Serviceman replaced fuse. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-08-23 14:00 | COMPLETED |  | 2012-08-23 10:46 | 2012-08-23 11:26 | 2012-08-23 11:45 | -118.8193 | 45.6394
5W202 | 1308510 | CPCC | CPCC787554 | PP | OR | PENDLETON | BUCKAROO | TR_129102_842710145 | 2012 | Before | 2012-09-12 08:39 | 2012-09-12 09:23 | 1 | 44.367 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Serviceman replaced the cutout on pole# 129102 that was damaged by a squirrel, customer is back in full service. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-09-12 11:45 | COMPLETED |  | 2012-09-12 08:39 | 2012-09-12 09:23 | 2012-09-12 09:35 | -118.8716 | 45.6616
5W202 | 1308567 | CPCC | CPCC787556 | PP | OR | PENDLETON | BUCKAROO | TR_345300_886280479 | 2012 | Before | 2012-09-12 09:09 | 2012-09-12 11:30 | 1 | 141.433 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (PROTECTED SPECIES) (BMTS) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman refused transformer# 345300 and it held, the cause is unknown, customer is back in full service. PROSPER: protected species per Environmental | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-09-12 12:15 | COMPLETED |  | 2012-09-12 09:09 | 2012-10-04 13:25 | 2012-09-12 13:31 | -118.7953 | 45.6074
5W202 | 1305014 | CPCC | CPCC786185 | PP | OR | PENDLETON | BUCKAROO | TR_129002_842710155 | 2012 | Before | 2012-08-28 19:38 | 2012-08-28 20:15 | 1 | 36.817 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: per service man, customer does not need the power on tonight to the pump, service man will turn this into the meter dept in the am and have them come back out to change meter and find cause for melting | DISTRIBUTION | CUSTOMER | AUTO | 2012-08-28 22:45 | COMPLETED |  | 2012-08-28 19:38 | 2012-08-28 20:15 | 2012-08-28 20:21 | -118.873 | 45.6604
5W202 | 1303166 | CPCC | CPCC785275 | PP | OR | PENDLETON | BUCKAROO | TR_162404_619850406 | 2012 | Before | 2012-08-21 12:21 | 2012-08-21 14:46 | 3 | 437.4 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman refused transformer# 162404 and it held, the cause was squirrel, customers are back in full service. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-08-21 15:30 | COMPLETED |  | 2012-08-21 12:21 | 2012-08-21 14:46 | 2012-08-21 15:01 | -118.8218 | 45.6517
5W202 | 1321150 | CPCC | CPCC796101 | PP | OR | PENDLETON | BUCKAROO | TR_136300_842710178 | 2012 | Before | 2012-11-09 09:26 | 2012-11-09 09:56 | 1 | 29.667 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: serviceman closed cutout door, customers are back in service | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-11-09 12:30 | COMPLETED |  | 2012-11-09 09:26 | 2012-11-09 09:56 | 2012-11-09 10:00 | -118.8792 | 45.6519
5W202 | 1311999 | CPCC | CPCC789477 | PP | OR | PENDLETON | BUCKAROO | TR_273105_886280452 | 2012 | Before | 2012-09-29 09:55 | 2012-09-29 11:30 | 1 | 95.483 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Squirrel caused blown fuse on transformer, re-fused and held, power restored | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-09-29 13:00 | COMPLETED |  | 2012-09-29 09:55 | 2012-09-29 11:30 | 2012-09-29 13:30 | -118.7994 | 45.6179
5W202 | 1315036 | CPCC | CPCC792068 | PP | OR | PENDLETON | BUCKAROO | Line Cut-67611 | 2012 | Before | 2012-10-13 12:07 | 2012-10-13 15:42 | 7 | 1504.65 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman says we are missing a phase. Wire down, crew needed. Repairs made. | DISTRIBUTION | DEVICE | MANUAL | 2012-10-13 19:15 | COMPLETED |  | 2012-10-13 12:07 | 2012-10-13 15:42 | 2012-10-13 15:46 | -118.9727 | 45.6605
5W202 | 1314153 | CPCC | CPCC791098 | PP | OR | PENDLETON | BUCKAROO | OH_274105_1550180141 | 2012 | Before | 2012-10-10 09:15 | 2012-10-10 10:34 | 99 | 7779.717 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman refused the tapline fuse at pole# 274105 and it held, the cause is unknown, customers are back in full service. | DISTRIBUTION | DEVICE | AUTO | 2012-10-10 12:30 | COMPLETED |  | 2012-10-10 09:18 | 2012-10-11 14:34 | 2012-10-10 11:06 | -118.797 | 45.6189
5W202 | 1315010 | CPCC | CPCC792071 | PP | OR | PENDLETON | BUCKAROO | TR_086600_802520487 | 2012 | Before | 2012-10-13 12:34 | 2012-10-13 14:10 | 2 | 191.4 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown transformer fuse, cause was squirrel. Refused and customers are back on. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-10-13 15:45 | COMPLETED |  | 2012-10-13 12:34 | 2012-10-13 14:10 | 2012-10-13 14:16 | -118.8349 | 45.6699
5W202 | 1315035 | CPCC | CPCC792103 | PP | OR | PENDLETON | BUCKAROO | OH_176701_842710130 | 2012 | Before | 2012-10-13 13:29 | 2012-10-13 15:42 | 7 | 931.583 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | B/O EQUIPMENT | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Associated to outage 792068. Opened fuses to isolate wire down burning on the ground. Repairs made. | DISTRIBUTION | DEVICE | AUTO | 2012-10-13 16:30 | COMPLETED |  | 2012-10-13 13:29 | 2012-10-13 15:42 | 2012-10-13 15:46 | -118.9609 | 45.6567
5W202 | 1316890 | CPCC | CPCC793596 | PP | OR | PENDLETON | BUCKAROO | BCK_CB5W202 | 2012 | Before | 2012-10-20 16:29 | 2012-10-20 16:29 | 0 | 0 | 1535 | 383.75 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: T&R Unknown cause. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2012-10-20 16:29 | 2012-10-20 16:29 | 2012-10-20 17:55 | -118.8367 | 45.6762
5W202 | 1315665 | CPCC | CPCC792775 | PP | OR | PENDLETON | BUCKAROO | TR_056000_1550116195 | 2012 | Before | 2012-10-16 07:42 | 2012-10-16 09:11 | 2 | 177.7 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: crew made repairs customers are back in service | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-10-16 10:45 | COMPLETED |  | 2012-10-16 07:42 | 2012-10-16 09:11 | 2012-10-16 09:30 | -118.8358 | 45.6746
5W202 | 1328959 | CPCC | CPCC802666 | PP | OR | PENDLETON | BUCKAROO | TR_165645_619850618 | 2012 | Before | 2012-12-02 21:37 | 2012-12-02 23:24 | 1 | 107.367 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | SOURCE: modeled transformer in error, single customer outage, bad connector at wx/head. | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2012-12-03 01:00 | COMPLETED |  | 2012-12-02 21:37 | 2012-12-03 14:14 | 2012-12-02 23:25 | -118.8164 | 45.6551
5W202 | 1313988 | CPCC | CPCC791010 | PP | OR | PENDLETON | BUCKAROO | TR_161380_619850384 | 2012 | Before | 2012-10-09 08:53 | 2012-10-09 10:41 | 1 | 107.667 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING | EQUIPMENT FAILURE | DETERIORATION OR ROTTING | SECONDARY CABLE UG |  |  |  | SOURCE: B/O Secondary Leg, crew to install service saver. | DISTRIBUTION | CUSTOMER | AUTO | 2012-10-09 12:00 | COMPLETED |  | 2012-10-09 08:53 | 2012-10-09 10:42 | 2012-10-09 11:55 | -118.8253 | 45.6505
5W202 | 1314357 | CPCC | CPCC791214 | PP | OR | PENDLETON | BUCKAROO | TR_082606_802520509 | 2012 | Before | 2012-10-11 06:55 | 2012-10-11 07:40 | 2 | 88.8 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman refused transformer# 082606 and it held, the cause was rotted fuse, customers are back in full service. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2012-10-11 10:00 | COMPLETED |  | 2012-10-11 06:55 | 2012-10-11 07:40 | 2012-10-11 09:26 | -118.8432 | 45.6687
5W202 | 1332608 | CPCC | CPCC806402 | PP | OR | PENDLETON | BUCKAROO | RC_072201_802520342 | 2012 | Before | 2012-12-17 05:01 | 2012-12-17 09:19 | 183 | 42801.75 | 0 | 0 | 2 | Y | N | N | N | Y | 2012-12-17 to 2012-12-17 OR Northeast | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Crew made repairs to the overhead primary that is down. | DISTRIBUTION | DEVICE | AUTO | 2012-12-17 08:15 | COMPLETED |  | 2012-12-17 05:10 | 2012-12-17 09:19 | 2012-12-17 09:40 | -118.8664 | 45.6634
5W202 | 1339358 | CPCC | CPCC816228 | PP | OR | PENDLETON | BUCKAROO | TR_213500_752850234 | 2013 | Before | 2013-01-09 10:47 | 2013-01-09 12:06 | 3 | 236.9 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: B/O cut-out. Crew to replace | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-01-09 14:00 | COMPLETED |  | 2013-01-09 10:47 | 2013-01-09 12:06 | 2013-01-09 12:15 | -118.8209 | 45.6394
5W202 | 1337883 | CPCC | CPCC814991 | PP | OR | PENDLETON | BUCKAROO | TR_345702_886280551 | 2013 | Before | 2013-01-02 09:35 | 2013-01-02 10:36 | 1 | 61.2 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman refused transformer# 345702 and it held, the cause was a squirrel, customer is back in full service. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-01-02 12:45 | COMPLETED |  | 2013-01-02 09:35 | 2013-01-02 10:36 | 2013-01-02 11:06 | -118.7952 | 45.613
5W202 | 1343629 | CPCC | CPCC818585 | PP | OR | PENDLETON | BUCKAROO | OH_210603_1550004111 | 2013 | Before | 2013-01-30 11:10 | 2013-01-30 13:11 | 85 | 8908.1 | 0 | 0 | 2 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman refused the tapline fuse at pole# 210603 and the transformer fuse at pole# 212806, the cause was a squirrel, Customers are back in full service. | DISTRIBUTION | DEVICE | AUTO | 2013-01-30 14:15 | COMPLETED |  | 2013-01-30 11:10 | 2013-01-31 10:42 | 2013-01-30 13:16 | -118.8264 | 45.6411
5W202 | 1344835 | CPCC | CPCC819296 | PP | OR | PENDLETON | BUCKAROO | TR_163200_619850418 | 2013 | Before | 2013-02-06 14:27 | 2013-02-06 15:50 | 10 | 831.667 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Serviceman will need help to replace a cutout that was damaged by a squirrel. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-02-06 17:30 | COMPLETED |  | 2013-02-06 14:27 | 2013-02-06 15:50 | 2013-02-06 16:25 | -118.82 | 45.6488
5W202 | 1338866 | CPCC | CPCC815728 | PP | OR | PENDLETON | BUCKAROO | TR_249601_842710104 | 2013 | Before | 2013-01-07 06:45 | 2013-01-07 09:01 | 2 | 270.833 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD SUSPECTED, NO MORTALITY |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown x-fmr fuse (bird suspected). Serviceman replaced fuse and it held. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-01-07 09:45 | COMPLETED |  | 2013-01-07 06:45 | 2013-01-07 09:01 | 2013-01-07 11:15 | -118.8731 | 45.6403
5W202 | 1342834 | CPCC | CPCC818167 | PP | OR | PENDLETON | BUCKAROO | TR_271304_886280432 | 2013 | Before | 2013-01-26 10:03 | 2013-01-26 14:56 | 1 | 293.55 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | SOURCE: Bad order secondary UG. 2 man crew needed. Repairs made and customer is back on. | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2013-01-26 16:00 | COMPLETED |  | 2013-01-26 10:03 | 2013-01-26 14:56 | 2013-01-26 15:56 | -118.8041 | 45.6218
5W202 | 1352323 | CPCC | CPCC824210 | PP | OR | PENDLETON | BUCKAROO | RC_087504_802520343 | 2013 | Before | 2013-03-20 15:40 | 2013-03-20 16:02 | 1279 | 29011.983 | 0 | 0 | 1 | Y | N | N | N | Y | 2013-03-20 to 2013-03-20 OR Northeast | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Opened due to cold load pickup. | DISTRIBUTION | DEVICE | AUTO | 2013-03-20 18:45 | COMPLETED |  | 2013-03-20 15:43 | 2013-03-21 10:44 | 2013-03-20 18:55 | -118.8323 | 45.6669
5W202 | 1348091 | CPCC | CPCC821857 | PP | OR | PENDLETON | BUCKAROO | RC_072201_802520342 | 2013 | Before | 2013-02-27 10:12 | 2013-02-27 10:18 | 184 | 984.4 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | B/O EQUIPMENT | REGULATOR B/O OH |  |  |  | SOURCE: Crew opened field recloser to de-energize line to safely take regulator bank off line. | DISTRIBUTION | DEVICE | MANUAL | 2013-02-27 10:30 | COMPLETED |  | 2013-02-27 10:12 | 2013-02-27 10:30 | 2013-02-27 15:05 | -118.8664 | 45.6634
5W202 | 1351444 | CPCC | CPCC823772 | PP | OR | PENDLETON | BUCKAROO | TR_271304_886280432 | 2013 | Before | 2013-03-17 07:25 | 2013-03-17 11:09 | 1 | 224.883 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | SOURCE: Serviceman found bad ug secondary cable. Still has crew with him. Will pinpoint & repair. Repairs complete, power restored | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2013-03-17 12:00 | COMPLETED |  | 2013-03-17 07:25 | 2013-03-17 11:09 | 2013-03-17 11:20 | -118.8041 | 45.6218
5W202 | 1365699 | CPCC | CPCC832950 | PP | OR | PENDLETON | BUCKAROO | TR_204900_1550169527 | 2013 | Before | 2013-05-16 21:48 | 2013-05-16 22:29 | 1 | 40.767 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown transformer fuse, cause was squirrel. Refused and customer is back on. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-05-17 01:00 | COMPLETED |  | 2013-05-16 21:48 | 2013-05-16 22:29 | 2013-05-17 01:16 | -118.8389 | 45.6454
5W202 | 1360476 | CPCC | CPCC829073 | PP | OR | PENDLETON | BUCKAROO | OH_176701_842710130 | 2013 | Before | 2013-04-27 09:53 | 2013-04-27 12:20 | 10 | 1467.333 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman found blown line fuse @ 176701, no cause | DISTRIBUTION | DEVICE | AUTO | 2013-04-27 13:00 | COMPLETED |  | 2013-04-27 09:53 | 2013-04-27 12:30 | 2013-04-27 14:12 | -118.9609 | 45.6567
5W202 | 1361243 | CPCC | CPCC829374 | PP | OR | PENDLETON | BUCKAROO | Line Cut-74332 | 2013 | Before | 2013-04-30 09:22 | 2013-04-30 14:32 | 14 | 4346.767 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Crew needed to make repairs to the overhead primary that broke at the hotline clamp. Customers are back in full service. | DISTRIBUTION | DEVICE | MANUAL | 2013-04-30 16:30 | COMPLETED |  | 2013-04-30 09:22 | 2013-04-30 15:18 | 2013-04-30 15:21 | -118.9497 | 45.6526
5W202 | 1355901 | CPCC | CPCC826277 | PP | OR | PENDLETON | BUCKAROO | OH_165740_619850637 | 2013 | Before | 2013-04-06 14:57 | 2013-04-07 00:11 | 140 | 21783.7 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | POLE OH |  |  |  | SOURCE: Serviceman found top of pole # 164745 burned off with blown 'A' phase fuse @ 165740. Need 2 man crew. Repairs made outage resolved. | DISTRIBUTION | DEVICE | MANUAL | 2013-04-06 19:30 | COMPLETED |  | 2013-04-06 15:03 | 2013-04-07 00:11 | 2013-04-07 00:20 | -118.8166 | 45.6568
5W202 | 1355505 | CPCC | CPCC826019 | PP | OR | PENDLETON | BUCKAROO | RC_072201_802520342 | 2013 | Before | 2013-04-04 18:12 | 2013-04-05 01:10 | 190 | 79470.73 | 0 | 0 | 1 | Y | N | N | N | Y | 2013-04-04 to 2013-04-04 OR Northeast | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman found recloser 5w502 open to 'A' phase fault. Strong wind broke phase loose at pole 125000 (long caynon crossing). Crew made repairs PROSPER: Added 4 customers from CPCC826108. | DISTRIBUTION | DEVICE | MANUAL | 2013-04-05 04:15 | COMPLETED |  | 2013-04-04 18:15 | 2013-04-05 08:12 | 2013-04-05 03:10 | -118.8664 | 45.6634
5W202 | 1365992 | CPCC | CPCC833061 | PP | OR | PENDLETON | BUCKAROO | TR_343201_886280488 | 2013 | Before | 2013-05-18 09:00 | 2013-05-18 10:02 | 1 | 61.717 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: blown transformer fuse squirrel | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-05-18 12:00 | COMPLETED |  | 2013-05-18 09:00 | 2013-05-18 10:02 | 2013-05-18 10:12 | -118.8008 | 45.6056
5W202 | 1362657 | CPCC | CPCC830603 | PP | OR | PENDLETON | BUCKAROO | TR_073204_802520527 | 2013 | Before | 2013-05-06 07:46 | 2013-05-06 09:34 | 1 | 108.083 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman removed racoon from transformer bank, refused Transformer, it held , power restored | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-05-06 11:00 | COMPLETED |  | 2013-05-06 07:46 | 2013-05-06 09:34 | 2013-05-06 09:41 | -118.8631 | 45.6628
5W202 | 1364604 | CPCC | CPCC832481 | PP | OR | PENDLETON | BUCKAROO | TR_166742_619850624 | 2013 | Before | 2013-05-13 10:44 | 2013-05-13 11:40 | 4 | 226.067 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman found blown transformer fuse, no cause found, re-fused and it held , power restored | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-05-13 13:45 | COMPLETED |  | 2013-05-13 10:44 | 2013-05-13 11:40 | 2013-05-13 11:46 | -118.8152 | 45.6565
5W202 | 1368026 | CPCC | CPCC834244 | PP | OR | PENDLETON | BUCKAROO | TR_161900_619850529 | 2013 | Before | 2013-05-26 14:23 | 2013-05-26 14:53 | 1 | 29.317 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman found blown xfmr fuse, squrril. Refused & restored | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-05-26 17:30 | COMPLETED |  | 2013-05-26 14:23 | 2013-05-26 14:55 | 2013-05-26 15:00 | -118.8244 | 45.6598
5W202 | 1362049 | CPCC | CPCC829919 | PP | OR | PENDLETON | BUCKAROO | TR_121502_836510023 | 2013 | Before | 2013-05-04 10:11 | 2013-05-04 11:30 | 1 | 79.167 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: replaced transformer fuse - starling | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-05-04 13:15 | COMPLETED |  | 2013-05-04 10:11 | 2013-05-04 11:30 | 2013-05-04 11:35 | -119.015 | 45.6686
5W202 | 1379960 | CPCC | CPCC840803 | PP | OR | PENDLETON | BUCKAROO | TR_160280_619850370 | 2013 | Before | 2013-07-08 07:50 | 2013-07-08 11:42 | 1 | 231.967 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | SOURCE: B/O ug service neutral. Serviceman getting assistance to install service saver. | DISTRIBUTION | CUSTOMER | AUTO | 2013-07-08 11:00 | COMPLETED |  | 2013-07-08 07:50 | 2013-07-08 11:42 | 2013-07-08 15:05 | -118.826 | 45.6485
5W202 | 1387551 | CPCC | CPCC844379 | PP | OR | PENDLETON | BUCKAROO | Line Cut-77072 | 2013 | Before | 2013-08-01 10:34 | 2013-08-01 11:49 | 1542 | 116266.8 | 0 | 0 | 1 | Y | N | N | N | Y | 2013-08-01 to 2013-08-01 OR Northeast | LOSS OF SUPPLY | LOSS OF TRANSMISSION LINE | WEATHER | LIGHTNING | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Loss of transmission line to sub, due to lightning | DISTRIBUTION | DEVICE | AUTO | 2013-08-01 13:45 | COMPLETED |  | 2013-08-01 10:34 | 2013-08-02 10:13 | 2013-08-01 13:07 | -118.8367 | 45.676
5W202 | 1387661 | CPCC | CPCC844430 | PP | OR | PENDLETON | BUCKAROO | SB_128009_842710153 | 2013 | Before | 2013-08-01 18:26 | 2013-08-01 18:36 | 125 | 1216.667 | 0 | 0 | 1 | Y | N | N | N | Y | 2013-08-01 to 2013-08-01 OR Northeast | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | B/O EQUIPMENT | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Associated to outaeg 844422. Took emergency outage to make repairs to downed neutral. Repairs made and customers are back on. | DISTRIBUTION | DEVICE | MANUAL | 2013-08-01 19:27 | COMPLETED |  | 2013-08-01 18:26 | 2013-08-01 18:36 | 2013-08-01 18:42 | -118.8747 | 45.6603
5W202 | 1388471 | CPCC | CPCC844800 | PP | OR | PENDLETON | BUCKAROO | TR_161380_619850384 | 2013 | Before | 2013-08-05 10:01 | 2013-08-05 10:39 | 1 | 38.35 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | SOURCE: There is currently a service saver at this site due to b/o ug secondary. Breaker on service saver tripped. Serviceman reset breaker. | DISTRIBUTION | CUSTOMER | AUTO | 2013-08-05 13:00 | COMPLETED |  | 2013-08-05 10:01 | 2013-08-05 10:39 | 2013-08-05 11:12 | -118.8253 | 45.6505
5W202 | 1388646 | CPCC | CPCC844917 | PP | OR | PENDLETON | BUCKAROO | TR_161380_619850384 | 2013 | Before | 2013-08-05 17:04 | 2013-08-05 18:09 | 1 | 65.5 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | OTHER, KNOWN CAUSE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: sserviceman states that the service saver is installed and the custoemr has excessive load, asked them to not run so much load, we need to pull in new wire due to the customer building over our line | DISTRIBUTION | CUSTOMER | AUTO | 2013-08-05 20:15 | COMPLETED |  | 2013-08-05 17:04 | 2013-08-05 18:09 | 2013-08-05 18:12 | -118.8253 | 45.6505
5W202 | 1388086 | CPCC | CPCC844564 | PP | OR | PENDLETON | BUCKAROO | TR_161380_619850384 | 2013 | Before | 2013-08-03 08:42 | 2013-08-03 11:00 | 1 | 138.4 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | SOURCE: Serviceman found bad secondary UG leg, needs help & service Saver. Service Saver installed, power restored | DISTRIBUTION | CUSTOMER | AUTO | 2013-08-03 11:45 | COMPLETED |  | 2013-08-03 08:42 | 2013-08-03 11:02 | 2013-08-03 11:16 | -118.8253 | 45.6505
5W202 | 1381428 | CPCC | CPCC841631 | PP | OR | PENDLETON | BUCKAROO | OH_163600_619850477 | 2013 | Before | 2013-07-13 07:24 | 2013-07-13 08:14 | 31 | 1533.467 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: replaced tap fuse | DISTRIBUTION | DEVICE | AUTO | 2013-07-13 10:45 | COMPLETED |  | 2013-07-13 07:35 | 2013-07-13 08:14 | 2013-07-13 08:20 | -118.8215 | 45.6542
5W202 | 1395169 | CPCC | CPCC847357 | PP | OR | PENDLETON | BUCKAROO | OH_164300_619850447 | 2013 | Before | 2013-08-19 19:35 | 2013-08-19 21:43 | 9 | 1152.297 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown line fuse, cause was a blown grass hopper fuse on a OH transformer. Cause was squirrel. Re PROSPER: Added 1 customer from CPCC847392. | DISTRIBUTION | DEVICE | AUTO | 2013-08-19 22:45 | COMPLETED |  | 2013-08-19 19:41 | 2013-08-21 08:04 | 2013-08-19 22:22 | -118.8191 | 45.65
5W202 | 1398408 | CPCC | CPCC850787 | PP | OR | PENDLETON | BUCKAROO | TR_163200_619850418 | 2013 | Before | 2013-08-29 09:04 | 2013-08-29 11:34 | 1 | 149.717 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | DIG-IN (NON-PACIFICORP PERSONNEL) |  |  | SECONDARY CABLE UG |  |  |  | SOURCE: Secondary dig in. Serviceman to make repairs. | DISTRIBUTION | CUSTOMER | AUTO | 2013-08-29 12:15 | COMPLETED |  | 2013-08-29 09:04 | 2013-08-29 11:34 | 2013-08-29 11:47 | -118.82 | 45.6488
5W202 | 1399369 | CPCC | CPCC851237 | PP | OR | PENDLETON | BUCKAROO | BCK_CB5W202 | 2013 | Before | 2013-09-02 19:40 | 2013-09-02 19:41 | 0 | 0 | 1543 | 334.317 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | LIGHTNING | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: T & R caused by tree into line. See outage 851264 | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2013-09-02 19:40 | 2013-09-02 19:41 | 2013-09-03 03:21 | -118.8367 | 45.6762
5W202 | 1377982 | CPCC | CPCC840040 | PP | OR | PENDLETON | BUCKAROO | TR_165741_619850636 | 2013 | Before | 2013-07-03 02:35 | 2013-07-03 05:14 | 1 | 159.317 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Large tree came down and broke secondary arm and tore customers mast off of the home. Need 2 man crew to temp fix pole. Repairs made, customer will stay off untill electrician makes repairs. | DISTRIBUTION | CUSTOMER | AUTO | 2013-07-03 05:45 | COMPLETED |  | 2013-07-03 02:35 | 2013-07-03 05:14 | 2013-07-03 06:01 | -118.8171 | 45.6566
5W202 | 1394090 | CPCC | CPCC846684 | PP | OR | PENDLETON | BUCKAROO | TR_214501_752850241 | 2013 | Before | 2013-08-15 14:14 | 2013-08-15 15:47 | 1 | 92.733 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman refused transformer# 214501 and it held, the cause is unknown, pump is back in full service. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-08-15 17:15 | COMPLETED |  | 2013-08-15 14:14 | 2013-08-15 15:47 | 2013-08-15 16:22 | -118.8193 | 45.6386
5W202 | 1388756 | CPCC | CPCC845047 | PP | OR | PENDLETON | BUCKAROO | TR_167744_619850617 | 2013 | Before | 2013-08-06 07:28 | 2013-08-06 08:12 | 16 | 711.2 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown x-fmr fuse due to starling. Serviceman replaced fuse and it held. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-08-06 10:30 | COMPLETED |  | 2013-08-06 07:28 | 2013-08-06 08:13 | 2013-08-06 09:02 | -118.8123 | 45.6561
5W202 | 1399371 | CPCC | CPCC851264 | PP | OR | PENDLETON | BUCKAROO | OH_210603_1550004111 | 2013 | Before | 2013-09-02 19:37 | 2013-09-02 22:45 | 84 | 15782.2 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | WEATHER | LIGHTNING | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman found open 'B' phase fuse at 210603. Serviceman found tree pinning 'B' phase to neutral between 211600 & 211603. Cleared hazard, Refused & restored | DISTRIBUTION | DEVICE | AUTO | 2013-09-02 22:45 | COMPLETED |  | 2013-09-02 19:42 | 2013-09-02 22:55 | 2013-09-03 03:21 | -118.8264 | 45.6411
5W202 | 1399374 | CPCC | CPCC851277 | PP | OR | PENDLETON | BUCKAROO | OH_214600_752850173 | 2013 | Before | 2013-09-02 20:08 | 2013-09-03 01:28 | 7 | 2241.983 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman found open fuse at 214600 with phase down between 214600 & 214602. Also found broken cutout @ 213500. No cause found but thunder storm with high winds came through area. Crew to make repairs | DISTRIBUTION | DEVICE | MANUAL | 2013-09-03 02:00 | COMPLETED |  | 2013-09-02 20:08 | 2013-09-03 01:30 | 2013-09-03 03:26 | -118.818 | 45.6408
5W202 | 1399430 | CPCC | CPCC851308 | PP | OR | PENDLETON | BUCKAROO | TR_082606_802520509 | 2013 | Before | 2013-09-03 05:56 | 2013-09-03 09:01 | 3 | 554.35 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD NEST (BMTS) |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Damaged cut-outs on x-fmr bank due to osprey nest. Crew made repairs. | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2013-09-03 10:30 | COMPLETED |  | 2013-09-03 05:56 | 2013-09-03 09:01 | 2013-09-03 09:52 | -118.8432 | 45.6687
5W202 | 1384159 | CPCC | CPCC842750 | PP | OR | PENDLETON | BUCKAROO | OH_119000_842710139 | 2013 | Before | 2013-07-21 10:28 | 2013-07-21 11:42 | 38 | 2831.633 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: 2 Blown line fuses, patrolled and did not find a cause. Refused and customers are back on. | DISTRIBUTION | DEVICE | AUTO | 2013-07-21 14:00 | COMPLETED |  | 2013-07-21 10:48 | 2013-07-21 11:42 | 2013-07-21 11:55 | -118.893 | 45.6614
5W202 | 1388789 | CPCC | CPCC845050 | PP | OR | PENDLETON | BUCKAROO | TR_162242_619850429 | 2013 | Before | 2013-08-06 08:20 | 2013-08-06 10:22 | 7 | 850.383 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown x-fmr fuse (no cause found). Serviceman replaced fuse and it held. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-08-06 11:30 | COMPLETED |  | 2013-08-06 08:20 | 2013-08-06 10:22 | 2013-08-06 10:32 | -118.822 | 45.6487
5W202 | 1385990 | CPCC | CPCC843774 | PP | OR | PENDLETON | BUCKAROO | TR_138906_1550269074 | 2013 | Before | 2013-07-27 13:53 | 2013-07-27 13:54 | 0 | 0 | 1 | 1.35 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: serviceman got a call directly from the city of Pendleton, found a fuse blown on the transformer bank and refused the cutout and customer is back in full service, ike Mccormack was the responder | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2013-07-27 13:53 | 2013-07-29 13:57 | 2013-07-27 15:57 | -118.8755 | 45.6588
5W202 | 1401992 | CPCC | CPCC853776 | PP | OR | PENDLETON | BUCKAROO | OH_214600_752850173 | 2013 | Before | 2013-09-09 14:00 | 2013-09-09 15:10 | 7 | 490.467 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman reports blown fuse on Pole 214600, patrolled Line, found no cause, refused and it held, power restored | DISTRIBUTION | DEVICE | AUTO | 2013-09-09 17:00 | COMPLETED |  | 2013-09-09 14:00 | 2013-09-09 15:10 | 2013-09-09 15:17 | -118.818 | 45.6408
5W202 | 1406414 | CPCC | CPCC856613 | PP | OR | PENDLETON | BUCKAROO | TR_213702_752850222 | 2013 | Before | 2013-09-23 09:15 | 2013-09-23 11:59 | 3 | 494.2 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Crew reports that squirrel caused transfomer outage. Crew has replaced fuse and power is back on. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-09-23 12:15 | COMPLETED |  | 2013-09-23 09:15 | 2013-09-23 11:59 | 2013-09-23 12:12 | -118.8215 | 45.6414
5W202 | 1417452 | CPCC | CPCC864340 | PP | OR | PENDLETON | BUCKAROO | OH_118900_1550129157 | 2013 | Before | 2013-10-28 09:07 | 2013-10-28 12:30 | 4 | 813.133 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE | ANIMALS | ANIMALS | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman says beaver cut down cottonwood tree and slapped phases together. He has refuse and power is on. | DISTRIBUTION | DEVICE | AUTO | 2013-10-28 15:15 | COMPLETED |  | 2013-10-28 12:14 | 2013-10-28 12:30 | 2013-10-28 13:19 | -119.0188 | 45.6743
5W202 | 1405911 | CPCC | CPCC856146 | PP | OR | PENDLETON | BUCKAROO | OH_211900_752850180 | 2013 | Before | 2013-09-21 07:58 | 2013-09-21 13:06 | 16 | 4925.067 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: b/o UG Crew made repairs and restored power. | DISTRIBUTION | DEVICE | MANUAL | 2013-09-21 16:00 | COMPLETED |  | 2013-09-21 07:58 | 2013-09-21 13:06 | 2013-09-21 15:27 | -118.8247 | 45.6454
5W202 | 1421898 | CPCC | CPCC866671 | PP | OR | PENDLETON | BUCKAROO | TR_033980_762510375 | 2013 | Before | 2013-11-16 18:10 | 2013-11-17 01:29 | 1 | 438.15 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | SOURCE: crew to make repairs to bad UG sec | DISTRIBUTION | CUSTOMER | MANUAL | 2013-11-17 01:30 | COMPLETED |  | 2013-11-16 18:10 | 2013-11-17 01:29 | 2013-11-17 03:18 | -118.8006 | 45.601
5W202 | 1404028 | CPCC | CPCC854747 | PP | OR | PENDLETON | BUCKAROO | RC_072201_802520342 | 2013 | Before | 2013-09-15 18:07 | 2013-09-16 07:56 | 191 | 81033.259 | 0 | 0 | 2 | Y | N | N | N | Y | 2013-09-15 to 2013-09-15 OR Northeast | WEATHER | LIGHTNING |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Arrived and found field recloser locked open a - grnd fault. Isolated and closed recloser in on test for remaining customers and will make repairs. Line was down at 125000 PROSPER: Modeling problem. Added 1 customer from CPCC855259. | DISTRIBUTION | DEVICE | AUTO | 2013-09-15 21:45 | COMPLETED |  | 2013-09-15 18:33 | 2013-09-16 13:50 | 2013-09-16 10:47 | -118.8664 | 45.6634
5W202 | 1407256 | CPCC | CPCC856930 | PP | OR | PENDLETON | BUCKAROO | TR_138900_842710195 | 2013 | Before | 2013-09-26 08:54 | 2013-09-26 09:35 | 2 | 82.333 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman refused transformer# 138900 and it held, the cause is unknown, customers are back in full service. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-09-26 12:00 | COMPLETED |  | 2013-09-26 08:54 | 2013-09-26 11:46 | 2013-09-26 12:01 | -118.8752 | 45.6597
5W202 | 1404359 | CPCC | CPCC855336 | PP | OR | PENDLETON | BUCKAROO | TR_071203_802520539 | 2013 | Before | 2013-09-16 09:38 | 2013-09-17 01:29 | 3 | 2852.15 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: serviceman verified the xfmr fuse open, no access need two guys to climg the pole and test the xfmr | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-09-16 12:45 | COMPLETED |  | 2013-09-16 09:38 | 2013-09-17 01:29 | 2013-09-17 06:27 | -118.8672 | 45.6634
5W202 | 1404389 | CPCC | CPCC855507 | PP | OR | PENDLETON | BUCKAROO | TR_164440_619850441 | 2013 | Before | 2013-09-17 05:56 | 2013-09-17 08:28 | 1 | 151.9 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Serviceman made repairs to the B/O overhead secondary neutral, customer is back in full service. | DISTRIBUTION | CUSTOMER | AUTO | 2013-09-17 09:00 | COMPLETED |  | 2013-09-17 05:56 | 2013-09-17 08:28 | 2013-09-17 09:17 | -118.8177 | 45.6523
5W202 | 1421469 | CPCC | CPCC866477 | PP | OR | PENDLETON | BUCKAROO | OH_210904_752850179 | 2013 | Before | 2013-11-14 18:11 | 2013-11-15 01:25 | 1 | 434.133 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Blown UG dip fuse. B/O UG. Crew made repairs. | DISTRIBUTION | DEVICE | AUTO | 2013-11-14 21:15 | COMPLETED |  | 2013-11-14 18:11 | 2013-11-15 01:25 | 2013-11-15 05:59 | -118.8261 | 45.6454
5W202 | 1404235 | CPCC | CPCC855385 | PP | OR | PENDLETON | BUCKAROO | TR_211501_752850239 | 2013 | Before | 2013-09-16 13:17 | 2013-09-16 17:54 | 3 | 832.75 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman reports fuse blown on transformer, caused by squirrel, refused and it held, power restored | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-09-16 16:30 | COMPLETED |  | 2013-09-16 13:17 | 2013-09-16 17:54 | 2013-09-16 17:57 | -118.825 | 45.6394
5W202 | 1431979 | CPCC | CPCC872280 | PP | OR | PENDLETON | BUCKAROO | TR_163241_619850419 | 2013 | Before | 2013-12-25 10:56 | 2013-12-25 11:59 | 4 | 252.2 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Squirrel caused blown fuse, replaced fuse and restored power. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-12-25 14:00 | COMPLETED |  | 2013-12-25 10:56 | 2013-12-25 11:59 | 2013-12-25 18:49 | -118.821 | 45.6489
5W202 | 1425052 | CPCC | CPCC868093 | PP | OR | PENDLETON | BUCKAROO | TR_273105_886280452 | 2013 | Before | 2013-11-29 12:01 | 2013-11-29 12:35 | 1 | 34.017 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman found blown xfmr fuse, squrril. Refused & restored | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-11-29 15:00 | COMPLETED |  | 2013-11-29 12:01 | 2013-11-29 12:37 | 2013-11-29 12:38 | -118.7994 | 45.6179
5W202 | 1431016 | CPCC | CPCC871927 | PP | OR | PENDLETON | BUCKAROO | TR_083600_802520507 | 2013 | Before | 2013-12-20 21:39 | 2013-12-20 22:27 | 1 | 48.217 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: replaced transformer fuse | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-12-21 00:45 | COMPLETED |  | 2013-12-20 21:39 | 2013-12-20 22:27 | 2013-12-20 22:29 | -118.8413 | 45.6693
5W202 | 1427812 | CPCC | CPCC870538 | PP | OR | PENDLETON | BUCKAROO | TR_163241_619850419 | 2013 | Before | 2013-12-09 12:13 | 2013-12-09 13:37 | 4 | 333.133 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman reports blown transformer fuse caused by squirrel, refused and it held | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2013-12-09 15:15 | COMPLETED |  | 2013-12-09 12:13 | 2013-12-09 13:37 | 2013-12-09 14:34 | -118.821 | 45.6489
5W202 | 1426422 | CPCC | CPCC868881 | PP | OR | PENDLETON | BUCKAROO | TR_160608_619850520 | 2013 | Before | 2013-12-04 17:15 | 2013-12-04 18:48 | 1 | 93.333 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: Serviceman found bad secondary connection at xfmr. Replaced & restored | DISTRIBUTION | CUSTOMER | AUTO | 2013-12-04 20:15 | COMPLETED |  | 2013-12-04 17:15 | 2013-12-04 18:50 | 2013-12-04 18:54 | -118.8266 | 45.6549
5W202 | 1435879 | CPCC | CPCC876084 | PP | OR | PENDLETON | BUCKAROO | TR_121502_836510023 | 2014 | Before | 2014-01-13 10:34 | 2014-01-13 11:44 | 2 | 140.2 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: Serviceman replaced broken jumper on transformer | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-01-13 13:45 | COMPLETED |  | 2014-01-13 10:34 | 2014-01-13 11:44 | 2014-01-13 12:29 | -119.015 | 45.6686
5W202 | 1435563 | CPCC | CPCC875799 | PP | OR | PENDLETON | BUCKAROO | TR_029100_1550541152 | 2014 | Before | 2014-01-12 00:38 | 2014-01-12 03:04 | 1 | 145.517 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: found b/o neutral connection, made repairs and reported | DISTRIBUTION | CUSTOMER | AUTO | 2014-01-12 03:45 | COMPLETED |  | 2014-01-12 00:38 | 2014-01-12 03:04 | 2014-01-12 06:58 | -119.0169 | 45.6785
5W202 | 1469040 | CPCC | CPCC899098 | PP | OR | PENDLETON | BUCKAROO | TR_214500_752850242 | 2014 | Before | 2014-05-26 11:56 | 2014-05-26 12:46 | 1 | 49.583 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: squirrel, replaced transformer fuse | DISTRIBUTION | CUSTOMER | AUTO | 2014-05-26 15:00 | COMPLETED |  | 2014-05-26 11:56 | 2014-05-26 12:46 | 2014-05-26 12:48 | -118.8193 | 45.6394
5W202 | 1465332 | CPCC | CPCC897152 | PP | OR | PENDLETON | BUCKAROO | TR_211805_752850198 | 2014 | Before | 2014-05-11 14:44 | 2014-05-11 18:30 | 2 | 452.7 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | SOURCE: Servicman found bad order xfmr. Called for 2 man crew to replace | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2014-05-11 18:45 | COMPLETED |  | 2014-05-11 14:44 | 2014-05-11 18:38 | 2014-05-11 18:43 | -118.8255 | 45.6429
5W202 | 1462572 | CPCC | CPCC895644 | PP | OR | PENDLETON | BUCKAROO | TR_033980_762510375 | 2014 | Before | 2014-04-29 19:41 | 2014-04-29 21:22 | 1 | 101.467 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTORS UG |  |  |  | SOURCE: Replaced bad connectors | DISTRIBUTION | CUSTOMER | AUTO | 2014-04-29 22:45 | COMPLETED |  | 2014-04-29 19:41 | 2014-04-29 21:22 | 2014-04-29 21:58 | -118.8006 | 45.601
5W202 | 1455444 | CPCC | CPCC892084 | PP | OR | PENDLETON | BUCKAROO | TR_228501_752850149 | 2014 | Before | 2014-04-04 12:47 | 2014-04-04 13:47 | 2 | 120.567 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Serviceman replaced the B/O cutout on pole# 228501, customers are back in full service. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-04-04 16:00 | COMPLETED |  | 2014-04-04 12:47 | 2014-04-04 13:47 | 2014-04-04 16:28 | -118.7891 | 45.6381
5W202 | 1469901 | CPCC | CPCC899505 | PP | OR | PENDLETON | BUCKAROO | TR_164515_619850474 | 2014 | Before | 2014-05-29 07:53 | 2014-05-29 09:08 | 6 | 450.2 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Serviceman replaced the B/O cutout that was damaged by a squirrel, customers are back in full service. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-05-29 11:00 | COMPLETED |  | 2014-05-29 07:53 | 2014-05-29 09:08 | 2014-05-29 11:18 | -118.8193 | 45.6536
5W202 | 1470456 | CPCC | CPCC899798 | PP | OR | PENDLETON | BUCKAROO | TR_214500_752850242 | 2014 | Before | 2014-05-31 15:12 | 2014-05-31 15:51 | 3 | 116.4 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: blown transformer fuse , squirrel install animal guard and refuse | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-05-31 18:15 | COMPLETED |  | 2014-05-31 15:12 | 2014-05-31 15:51 | 2014-05-31 18:13 | -118.8193 | 45.6394
5W202 | 1469900 | CPCC | CPCC899502 | PP | OR | PENDLETON | BUCKAROO | OH_152600_842710111 | 2014 | Before | 2014-05-29 07:04 | 2014-05-29 08:56 | 25 | 2786.667 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman refused the tapline fuse at pole# 152600 and it held, no cause found. Customers are back in full service. | DISTRIBUTION | DEVICE | AUTO | 2014-05-29 10:15 | COMPLETED |  | 2014-05-29 07:04 | 2014-05-29 09:27 | 2014-05-29 11:18 | -118.928 | 45.6547
5W202 | 1469373 | CPCC | CPCC899297 | PP | OR | PENDLETON | BUCKAROO | TR_165642_619850493 | 2014 | Before | 2014-05-27 16:36 | 2014-05-27 18:46 | 1 | 129.817 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: located failed OH C/O in backyard easement; 2 men needed(1701) | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-05-27 19:45 | COMPLETED |  | 2014-05-27 16:36 | 2014-05-27 18:46 | 2014-05-27 20:23 | -118.8177 | 45.6541
5W202 | 1486072 | CPCC | CPCC908496 | PP | OR | PENDLETON | BUCKAROO | TR_249601_842710104 | 2014 | Before | 2014-07-22 18:10 | 2014-07-22 19:19 | 2 | 138.8 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: serviceman reports that he refused the cutout that was blown due to lightning, customer back in service | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-07-22 21:15 | COMPLETED |  | 2014-07-22 18:10 | 2014-07-22 19:19 | 2014-07-23 15:37 | -118.8731 | 45.6403
5W202 | 1472043 | CPCC | CPCC900845 | PP | OR | PENDLETON | BUCKAROO | TR_139204_842710173 | 2014 | Before | 2014-06-06 21:33 | 2014-06-06 22:35 | 1 | 61.717 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: serviceman stated that the customers pump was not working, refused the cutouts and customer is back in sevice | DISTRIBUTION | CUSTOMER | AUTO | 2014-06-07 00:45 | COMPLETED |  | 2014-06-06 21:33 | 2014-06-06 22:35 | 2014-06-06 23:49 | -118.8714 | 45.6487
5W202 | 1472333 | CPCC | CPCC901114 | PP | OR | PENDLETON | BUCKAROO | OH_343003_1550180119 | 2014 | Before | 2014-06-08 15:31 | 2014-06-08 17:49 | 14 | 1928.033 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Bad order UG. Isolated bad section | DISTRIBUTION | DEVICE | AUTO | 2014-06-08 18:45 | COMPLETED |  | 2014-06-08 15:35 | 2014-06-08 17:54 | 2014-06-08 18:08 | -118.8 | 45.6019
5W202 | 1482918 | CPCC | CPCC906855 | PP | OR | PENDLETON | BUCKAROO | OH_152600_842710111 | 2014 | Before | 2014-07-14 10:24 | 2014-07-14 12:59 | 8 | 1240.667 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman reports line fuse open due to phases wrapped together. Serviceman unwrapped phases and replaced fuse. | DISTRIBUTION | DEVICE | AUTO | 2014-07-14 13:30 | COMPLETED |  | 2014-07-14 10:24 | 2014-07-14 12:59 | 2014-07-14 15:48 | -118.928 | 45.6547
5W202 | 1483228 | CPCC | CPCC906901 | PP | OR | PENDLETON | BUCKAROO | TR_207400_886280326 | 2014 | Before | 2014-07-14 14:59 | 2014-07-14 19:30 | 1 | 271.217 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | SOURCE: Crew to repair secondary Ug Cable. Repairs made and customer is back on. | DISTRIBUTION | CUSTOMER | MANUAL | 2014-07-14 20:30 | COMPLETED |  | 2014-07-14 14:59 | 2014-07-14 19:30 | 2014-07-14 23:18 | -118.8337 | 45.637
5W202 | 1486447 | CPCC | CPCC908742 | PP | OR | PENDLETON | BUCKAROO | TR_272100_886280447 | 2014 | Before | 2014-07-23 17:07 | 2014-07-23 18:13 | 2 | 131.9 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: refuse transformer lightning | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-07-23 20:15 | COMPLETED |  | 2014-07-23 17:07 | 2014-07-23 18:13 | 2014-07-23 18:14 | -118.8031 | 45.6192
5W202 | 1488572 | CPCC | CPCC910102 | PP | OR | PENDLETON | BUCKAROO | TR_073204_802520527 | 2014 | Before | 2014-07-30 10:18 | 2014-07-30 11:15 | 1 | 57.267 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman tested transformer, good. Re-fused transformer and restored customer. Unknown cause. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-07-30 13:30 | COMPLETED |  | 2014-07-30 10:18 | 2014-07-30 11:39 | 2014-07-30 11:44 | -118.8631 | 45.6628
5W202 | 1486416 | CPCC | CPCC908688 | PP | OR | PENDLETON | BUCKAROO | TR_274204_886280442 | 2014 | Before | 2014-07-23 13:46 | 2014-07-23 14:53 | 4 | 267.667 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Transformer fuse | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-07-23 17:00 | COMPLETED |  | 2014-07-23 13:46 | 2014-07-23 14:53 | 2014-07-23 17:05 | -118.7982 | 45.6194
5W202 | 1475797 | CPCC | CPCC902584 | PP | OR | PENDLETON | BUCKAROO | TR_349700_886280575 | 2014 | Before | 2014-06-19 17:24 | 2014-06-19 18:42 | 1 | 77.283 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Starlings caused fuses to blow, replaced fuse and restored power. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-06-19 20:30 | COMPLETED |  | 2014-06-19 17:24 | 2014-06-19 18:42 | 2014-06-19 21:38 | -118.788 | 45.6126
5W202 | 1475895 | CPCC | CPCC902607 | PP | OR | PENDLETON | BUCKAROO | TR_167744_619850617 | 2014 | Before | 2014-06-20 07:11 | 2014-06-20 07:58 | 16 | 743.733 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown fuse due to squirrel. Serviceman replaced fuse and it held. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-06-20 10:15 | COMPLETED |  | 2014-06-20 07:11 | 2014-06-20 07:58 | 2014-06-20 11:08 | -118.8123 | 45.6561
5W202 | 1490630 | CPCC | CPCC911361 | PP | OR | PENDLETON | BUCKAROO | TR_167744_619850617 | 2014 | Before | 2014-08-05 09:48 | 2014-08-05 11:17 | 1 | 89.667 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: Serviceman made repairs to the overhead secondary service that burnt down at a bare connector. | DISTRIBUTION | CUSTOMER | AUTO | 2014-08-05 13:00 | COMPLETED |  | 2014-08-05 09:48 | 2014-08-05 11:17 | 2014-08-05 12:49 | -118.8123 | 45.6561
5W202 | 1483774 | CPCC | CPCC907083 | PP | OR | PENDLETON | BUCKAROO | TR_152603_842710117 | 2014 | Before | 2014-07-16 03:29 | 2014-07-16 05:30 | 1 | 121.5 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman arrived and found blown fuse, patrolled line found no cause. Closed on test and restorede power. | DISTRIBUTION | CUSTOMER | AUTO | 2014-07-16 06:30 | COMPLETED |  | 2014-07-16 03:29 | 2014-07-16 05:30 | 2014-07-16 05:49 | -118.9285 | 45.6547
5W202 | 1486413 | CPCC | CPCC908716 | PP | OR | PENDLETON | BUCKAROO | TR_271304_886280432 | 2014 | Before | 2014-07-23 15:27 | 2014-07-23 16:32 | 1 | 65.467 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown x-fmr fuses due to lightning. Crew replaced fuses. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-07-23 18:30 | COMPLETED |  | 2014-07-23 15:27 | 2014-07-23 16:32 | 2014-07-23 17:04 | -118.8041 | 45.6218
5W202 | 1486058 | CPCC | CPCC908478 | PP | OR | PENDLETON | BUCKAROO | OH_176701_842710130 | 2014 | Before | 2014-07-22 17:04 | 2014-07-22 18:43 | 12 | 1185.4 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Fuse blown cause unknown re-fused and it held. | DISTRIBUTION | DEVICE | AUTO | 2014-07-22 20:15 | COMPLETED |  | 2014-07-22 17:04 | 2014-07-22 18:43 | 2014-07-23 15:37 | -118.9609 | 45.6567
5W202 | 1486325 | CPCC | CPCC908623 | PP | OR | PENDLETON | BUCKAROO | TR_126900_836510015 | 2014 | Before | 2014-07-23 08:38 | 2014-07-23 11:39 | 2 | 363.133 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Refused and it held, the cause was lightning | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-07-23 11:45 | COMPLETED |  | 2014-07-23 08:38 | 2014-07-23 11:39 | 2014-07-23 15:47 | -119.0035 | 45.6754
5W202 | 1474195 | CPCC | CPCC901962 | PP | OR | PENDLETON | BUCKAROO | OH_176701_842710130 | 2014 | Before | 2014-06-14 08:06 | 2014-06-14 09:25 | 12 | 944.4 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman found open 25T fuse @ 176701. Patrolled found nothing, refused & restored. Reported on outage #901953 | DISTRIBUTION | DEVICE | AUTO | 2014-06-14 11:15 | COMPLETED |  | 2014-06-14 08:06 | 2014-06-14 10:10 | 2014-06-14 10:19 | -118.9609 | 45.6567
5W202 | 1501097 | CPCC | CPCC917894 | PP | OR | PENDLETON | BUCKAROO | TR_162242_619850429 | 2014 | Before | 2014-09-10 07:12 | 2014-09-10 07:55 | 7 | 297.733 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman refused transformer# 162242 and it held, the cause was a squirrel, customers are back in full service. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-09-10 10:15 | COMPLETED |  | 2014-09-10 07:12 | 2014-09-10 07:55 | 2014-09-10 08:03 | -118.822 | 45.6487
5W202 | 1509659 | CPCC | CPCC923128 | PP | OR | PENDLETON | BUCKAROO | TR_207201_886280277 | 2014 | Before | 2014-10-15 08:22 | 2014-10-15 09:17 | 1 | 54.867 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman found transformer fuse open on pole # 207201; re-fused and it held. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-10-15 11:30 | COMPLETED |  | 2014-10-15 08:22 | 2014-10-15 09:17 | 2014-10-15 13:08 | -118.8359 | 45.6346
5W202 | 1508852 | CPCC | CPCC922651 | PP | OR | PENDLETON | BUCKAROO | TR_249601_842710104 | 2014 | Before | 2014-10-11 12:42 | 2014-10-11 16:25 | 1 | 223.6 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | POLE OH |  |  |  | SOURCE: serviceman reports that the pole fire was caused by a cutout tracking over, will get crew to change the pole out | DISTRIBUTION | CUSTOMER | AUTO | 2014-10-11 15:45 | COMPLETED |  | 2014-10-11 12:42 | 2014-10-11 16:25 | 2014-10-11 16:43 | -118.8731 | 45.6403
5W202 | 1508851 | CPCC | CPCC922691 | PP | OR | PENDLETON | BUCKAROO | Line Cut-90953 | 2014 | Before | 2014-10-11 15:24 | 2014-10-11 16:25 | 4 | 246.533 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | POLE FIRE | POLE OH |  |  |  | SOURCE: Crew de-energized tap lien to make repairs to a pole fire on outage 922651 | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2014-10-11 15:24 | 2014-10-11 16:25 | 2014-10-11 16:43 | -118.8686 | 45.6403
5W202 | 1501623 | CPCC | CPCC918116 | PP | OR | PENDLETON | BUCKAROO | TR_215100_752850164 | 2014 | Before | 2014-09-11 10:37 | 2014-09-11 17:30 | 1 | 413.133 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | OTHER, KNOWN CAUSE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: customer problem | DISTRIBUTION | CUSTOMER | MANUAL | 2014-09-11 18:00 | COMPLETED |  | 2014-09-11 10:37 | 2014-09-11 17:30 | 2014-09-11 18:09 | -118.8159 | 45.6332
5W202 | 1511465 | CPCC | CPCC924796 | PP | OR | PENDLETON | BUCKAROO | TR_161905_619850525 | 2014 | Before | 2014-10-23 16:03 | 2014-10-23 17:46 | 1 | 103.317 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | SOURCE: serviceman reports a bad connector at the transformer, made repairs customer back in full service | DISTRIBUTION | CUSTOMER | AUTO | 2014-10-23 19:15 | COMPLETED |  | 2014-10-23 16:03 | 2014-10-23 17:46 | 2014-10-23 19:04 | -118.8248 | 45.6588
5W202 | 1516428 | CPCC | CPCC930325 | PP | OR | PENDLETON | BUCKAROO | OH_165400_619850346 | 2014 | Before | 2014-11-11 03:31 | 2014-11-11 07:28 | 9 | 2127.3 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: B/O ug primary. | DISTRIBUTION | DEVICE | AUTO | 2014-11-11 06:45 | COMPLETED |  | 2014-11-11 03:31 | 2014-11-11 07:28 | 2014-11-11 07:33 | -118.8171 | 45.6518
5W202 | 1503409 | CPCC | CPCC919276 | PP | OR | PENDLETON | BUCKAROO | TR_160181_619850376 | 2014 | Before | 2014-09-18 09:04 | 2014-09-18 16:00 | 1 | 416.35 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | SOURCE: Servicemen onsite making repairs to the B/O underground secondary service. | DISTRIBUTION | CUSTOMER | MANUAL | 2014-09-18 17:15 | COMPLETED |  | 2014-09-18 09:04 | 2014-09-18 16:12 | 2014-09-18 16:43 | -118.8263 | 45.6479
5W202 | 1496709 | CPCC | CPCC915795 | PP | OR | PENDLETON | BUCKAROO | TR_167744_619850617 | 2014 | Before | 2014-08-24 09:52 | 2014-08-24 10:31 | 16 | 631.733 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Starling caused blown fuse. Replaced it and restored power. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-08-24 13:00 | COMPLETED |  | 2014-08-24 09:52 | 2014-08-24 10:31 | 2014-08-24 13:43 | -118.8123 | 45.6561
5W202 | 1512267 | CPCC | CPCC925823 | PP | OR | PENDLETON | BUCKAROO | TR_156501_842710113 | 2014 | Before | 2014-10-25 12:18 | 2014-10-25 15:59 | 1 | 221.583 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Line down. Crew Reports Neutral Wire Repaired, Customer Restored | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-10-25 15:30 | COMPLETED |  | 2014-10-25 12:18 | 2014-10-25 16:00 | 2014-10-26 07:04 | -118.9188 | 45.6535
5W202 | 1526683 | CPCC | CPCC940402 | PP | OR | PENDLETON | BUCKAROO | TR_357001_132440014 | 2014 | Before | 2014-12-20 13:30 | 2014-12-21 02:39 | 3 | 2368.75 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | POLE OH |  |  |  | SOURCE: crew replaced pole top | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-12-20 16:30 | COMPLETED |  | 2014-12-20 13:30 | 2014-12-21 02:45 | 2014-12-21 02:53 | -118.8971 | 45.6892
5W202 | 1518171 | CPCC | CPCC932616 | PP | OR | PENDLETON | BUCKAROO | TR_164405_619850434 | 2014 | Before | 2014-11-16 10:28 | 2014-11-16 11:49 | 3 | 240.45 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: serviceman reports blown fuse investigating for cause, serviceman refuse the cutout and customers are back in service, outage due to bird | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-11-16 13:30 | COMPLETED |  | 2014-11-16 10:28 | 2014-12-08 08:16 | 2014-11-16 18:38 | -118.8196 | 45.6516
5W202 | 1518174 | CPCC | CPCC932623 | PP | OR | PENDLETON | BUCKAROO | TR_211605_752850208 | 2014 | Before | 2014-11-16 12:42 | 2014-11-16 13:11 | 4 | 112.333 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: serviceman reports blown fuse, refused the cutout and customers are back in service | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-11-16 15:45 | COMPLETED |  | 2014-11-16 12:42 | 2014-11-16 14:11 | 2014-11-16 18:38 | -118.8241 | 45.6409
5W202 | 1521755 | CPCC | CPCC935110 | PP | OR | PENDLETON | BUCKAROO | TR_067100_802520543 | 2014 | Before | 2014-12-02 00:48 | 2014-12-02 01:36 | 1 | 47.983 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown fuse. No cause found. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-12-02 04:00 | COMPLETED |  | 2014-12-02 00:48 | 2014-12-02 01:36 | 2014-12-02 03:48 | -118.8581 | 45.6757
5W202 | 1532252 | CPCC | CPCC943866 | PP | OR | PENDLETON | BUCKAROO | TR_164643_619850490 | 2015 | Before | 2015-01-15 10:06 | 2015-01-15 10:47 | 1 | 41.35 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: Serviceman changed out a bad connector. | DISTRIBUTION | CUSTOMER | AUTO | 2015-01-15 13:15 | COMPLETED |  | 2015-01-15 10:06 | 2015-01-15 12:46 | 2015-01-15 12:48 | -118.8179 | 45.6551
5W202 | 1519604 | CPCC | CPCC933684 | PP | OR | PENDLETON | BUCKAROO | OH_124000_842710162 | 2014 | Before | 2014-11-22 08:06 | 2014-11-22 17:34 | 10 | 5684.5 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | POLE OH |  |  |  | SOURCE: pole fire pole replace | DISTRIBUTION | DEVICE | AUTO | 2014-11-22 11:15 | COMPLETED |  | 2014-11-22 08:06 | 2014-11-22 17:34 | 2014-11-22 17:39 | -118.8829 | 45.6608
5W202 | 1524276 | CPCC | CPCC939049 | PP | OR | PENDLETON | BUCKAROO | TR_348801_886280572 | 2014 | Before | 2014-12-11 19:05 | 2014-12-11 20:53 | 2 | 217.033 | 0 | 0 | 1 | Y | N | N | N | Y | 2014-12-11 OR Northeast | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | JUMPER WIRE/STIRRUP OH |  |  |  |  | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-12-11 22:15 | COMPLETED |  | 2014-12-11 19:05 | 2014-12-12 03:30 | 2014-12-12 16:16 | -118.7906 | 45.6141
5W202 | 1519603 | CPCC | CPCC933675 | PP | OR | PENDLETON | BUCKAROO | OH_124000_842710162 | 2014 | Before | 2014-11-22 05:53 | 2014-11-22 17:34 | 11 | 7715.4 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | POLE OH |  |  |  | SOURCE: Serviceman found open line fuse, need crew to patrol. need crew from enterprise to replace pole | DISTRIBUTION | DEVICE | AUTO | 2014-11-22 09:00 | COMPLETED |  | 2014-11-22 05:53 | 2014-11-22 17:34 | 2014-11-22 17:38 | -118.8829 | 45.6608
5W202 | 1524269 | CPCC | CPCC938924 | PP | OR | PENDLETON | BUCKAROO | OH_119000_842710139 | 2014 | Before | 2014-12-11 17:44 | 2014-12-11 20:29 | 41 | 6752.7 | 0 | 0 | 1 | Y | N | N | N | Y | 2014-12-11 OR Northeast | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  |  | DISTRIBUTION | DEVICE | AUTO | 2014-12-11 20:45 | COMPLETED |  | 2014-12-11 17:46 | 2014-12-12 03:30 | 2014-12-12 16:15 | -118.893 | 45.6614
5W202 | 1518990 | CPCC | CPCC933365 | PP | OR | PENDLETON | BUCKAROO | TR_345901_886280544 | 2014 | Before | 2014-11-20 10:41 | 2014-11-20 11:22 | 3 | 122.7 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman refused transformer# 345901 and it held, the cause was a tree limb | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2014-11-20 13:45 | COMPLETED |  | 2014-11-20 10:41 | 2014-11-20 11:22 | 2014-11-20 11:53 | -118.795 | 45.6157
5W202 | 1526684 | CPCC | CPCC940660 | PP | OR | PENDLETON | BUCKAROO | OH_124000_842710162 | 2014 | Before | 2014-12-21 01:46 | 2014-12-21 02:39 | 18 | 965.7 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | ENERGY EMERGENCY INTERRUPTION |  |  | NO DISTRIBUTION DAMAGE |  |  |  |  | DISTRIBUTION | DEVICE | AUTO | 2014-12-21 04:45 | COMPLETED |  | 2014-12-21 01:46 | 2014-12-21 02:46 | 2014-12-21 02:53 | -118.8829 | 45.6608
5W202 | 1524450 | CPCC | CPCC937373 | PP | OR | PENDLETON | BUCKAROO | OH_274105_1550180141 | 2014 | Before | 2014-12-11 10:30 | 2014-12-11 14:34 | 113 | 27620.967 | 0 | 0 | 1 | Y | N | N | N | Y | 2014-12-11 OR Northeast | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Primary | DISTRIBUTION | DEVICE | AUTO | 2014-12-11 13:45 | COMPLETED |  | 2014-12-11 10:30 | 2014-12-12 05:30 | 2014-12-12 16:32 | -118.797 | 45.6189
5W202 | 1525414 | CPCC | CPCC939709 | PP | OR | PENDLETON | BUCKAROO | OH_119000_842710139 | 2014 | Before | 2014-12-14 17:15 | 2014-12-14 19:15 | 41 | 4915.217 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  |  | DISTRIBUTION | DEVICE | AUTO | 2014-12-14 20:45 | COMPLETED |  | 2014-12-14 17:15 | 2014-12-14 20:44 | 2014-12-14 20:48 | -118.893 | 45.6614
5W202 | 1529824 | CPCC | CPCC942715 | PP | OR | PENDLETON | BUCKAROO | TR_211601_752850221 | 2015 | Before | 2015-01-02 13:40 | 2015-01-02 13:48 | 11 | 91.667 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | B/O EQUIPMENT | CUT-OUT B/O OH |  |  |  | SOURCE: Crew took outage on transformer# 211601 to replace a B/O cutout | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2015-01-02 13:40 | 2015-01-02 16:21 | 2015-01-02 16:28 | -118.8252 | 45.6406
5W202 | 1532826 | CPCC | CPCC944311 | PP | OR | PENDLETON | BUCKAROO | OH_214800_752850247 | 2015 | Before | 2015-01-18 04:34 | 2015-01-18 10:48 | 12 | 4493 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: serviceman reports blown fuses at pole 214800 due to wire down, will get a crew to help make repairs. Repairs complete, all customers restored | DISTRIBUTION | DEVICE | AUTO | 2015-01-18 07:45 | COMPLETED |  | 2015-01-18 04:34 | 2015-01-18 11:05 | 2015-01-18 11:08 | -118.8187 | 45.6435
5W202 | 1564519 | CPCC | CPCC967127 | PP | OR | PENDLETON | BUCKAROO | TR_289501_886280467 | 2015 | Before | 2015-06-01 05:58 | 2015-06-01 07:37 | 1 | 99.217 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Replaced transformer fuse and holding | DISTRIBUTION | CUSTOMER | AUTO | 2015-06-01 09:00 | COMPLETED |  | 2015-06-01 05:59 | 2015-06-01 08:13 | 2015-06-01 08:13 | -118.8096 | 45.6246
5W202 | 1558398 | CPCC | CPCC963393 | PP | OR | PENDLETON | BUCKAROO | OH_138904_842710193 | 2015 | Before | 2015-05-07 11:48 | 2015-05-07 13:07 | 27 | 2132.55 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Crew needed to make repairs to the overhead primary that broke at the stirrup. | DISTRIBUTION | DEVICE | AUTO | 2015-05-07 15:00 | COMPLETED |  | 2015-05-07 11:49 | 2015-05-07 13:13 | 2015-05-07 13:19 | -118.8758 | 45.6587
5W202 | 1564131 | CPCC | CPCC966733 | PP | OR | PENDLETON | BUCKAROO | TR_165743_619850625 | 2015 | Before | 2015-05-30 07:47 | 2015-05-30 08:52 | 6 | 389 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman found transformer fuse blown due to squirrel, Re-fused and holding | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-05-30 11:30 | COMPLETED |  | 2015-05-30 08:20 | 2015-05-30 09:23 | 2015-05-30 09:28 | -118.8156 | 45.6564
5W202 | 1564451 | CPCC | CPCC966869 | PP | OR | PENDLETON | BUCKAROO | OH_289604_886280468 | 2015 | Before | 2015-05-31 19:23 | 2015-05-31 22:57 | 9 | 1923.15 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | POLE OH |  |  |  | SOURCE: crew to replace pole | DISTRIBUTION | DEVICE | AUTO | 2015-05-31 22:30 | COMPLETED |  | 2015-05-31 19:24 | 2015-06-01 01:52 | 2015-06-01 01:53 | -118.8074 | 45.6251
5W202 | 1562493 | CPCC | CPCC965643 | PP | OR | PENDLETON | BUCKAROO | OH_176701_842710130 | 2015 | Before | 2015-05-23 11:49 | 2015-05-23 14:36 | 15 | 2497.995 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman found two fuse open, Patrolled line and found no cause, re-fused and holding PROSPER: added cust form 965648 | DISTRIBUTION | DEVICE | AUTO | 2015-05-23 15:00 | COMPLETED |  | 2015-05-23 11:49 | 2015-05-26 10:20 | 2015-05-23 16:08 | -118.9609 | 45.6567
5W202 | 1544587 | CPCC | CPCC954329 | PP | OR | PENDLETON | BUCKAROO | TR_160180_619850378 | 2015 | Before | 2015-03-12 22:15 | 2015-03-13 03:33 | 1 | 317.9 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | SOURCE: bad sec ug, crew to make repairs | DISTRIBUTION | CUSTOMER | AUTO | 2015-03-13 01:30 | COMPLETED |  | 2015-03-12 22:16 | 2015-03-13 03:33 | 2015-03-13 03:38 | -118.8263 | 45.6472
5W202 | 1558399 | CPCC | CPCC963401 | PP | OR | PENDLETON | BUCKAROO | OH_138904_842710193 | 2015 | Before | 2015-05-07 12:45 | 2015-05-07 13:07 | 17 | 385.333 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR | EQUIPMENT FAILURE | B/O EQUIPMENT | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Crew took outage on the tapline fuses at pole# 138904 to make repairs to the overhead primary that broke at a stirrup | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2015-05-07 12:45 | 2015-05-07 13:14 | 2015-05-07 13:19 | -118.8758 | 45.6587
5W202 | 1544586 | CPCC | CPCC954335 | PP | OR | PENDLETON | BUCKAROO | OH_211902_1550257187 | 2015 | Before | 2015-03-13 02:42 | 2015-03-13 03:32 | 42 | 2104.2 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: deenergized UG pri to make repairs | DISTRIBUTION | DEVICE | AUTO | 2015-03-13 05:45 | COMPLETED |  | 2015-03-13 02:42 | 2015-03-13 03:33 | 2015-03-13 03:38 | -118.8249 | 45.6454
5W202 | 1546323 | CPCC | CPCC955592 | PP | OR | PENDLETON | BUCKAROO | OH_119000_842710139 | 2015 | Before | 2015-03-21 07:27 | 2015-03-21 08:35 | 15 | 1013.75 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown line fuse due to a tree branch. | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2015-03-21 07:28 | 2015-03-21 09:31 | 2015-03-21 09:33 | -118.893 | 45.6614
5W202 | 1562883 | CPCC | CPCC965877 | PP | OR | PENDLETON | BUCKAROO | OH_118904_1550606330 | 2015 | Before | 2015-05-26 05:33 | 2015-05-26 07:08 | 3 | 283.9 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown fuse. No cause found. | DISTRIBUTION | DEVICE | AUTO | 2015-05-26 08:45 | COMPLETED |  | 2015-05-26 05:33 | 2015-05-26 07:40 | 2015-05-26 07:44 | -119.0189 | 45.6749
5W202 | 1571425 | CPCC | CPCC970607 | PP | OR | PENDLETON | BUCKAROO | OH_163502_619850465 | 2015 | Before | 2015-06-22 15:32 | 2015-06-22 19:54 | 1 | 261.733 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | TERMINATION UG |  |  |  | SOURCE: Crews made reapirs, found contaminated/dirty pothead, cleaned and re-energized | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2015-06-22 15:32 | 2015-06-22 20:21 | 2015-06-22 20:23 | -118.8211 | 45.6528
5W202 | 1568972 | CPCC | CPCC969360 | PP | OR | PENDLETON | BUCKAROO | TR_167744_619850617 | 2015 | Before | 2015-06-15 05:18 | 2015-06-15 06:20 | 16 | 988 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Squirrell | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-06-15 08:30 | COMPLETED |  | 2015-06-15 05:18 | 2015-06-15 06:35 | 2015-06-15 06:38 | -118.8123 | 45.6561
5W202 | 1576684 | CPCC | CPCC974038 | PP | OR | PENDLETON | BUCKAROO | OH_088401_802520471 | 2015 | Before | 2015-07-06 06:54 | 2015-07-06 08:01 | 3 | 199.8 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (PROTECTED SPECIES) (BMTS) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman reports line fuses open due to Pelican, re-fused and Holding | DISTRIBUTION | DEVICE | AUTO | 2015-07-06 10:00 | COMPLETED |  | 2015-07-06 06:55 | 2015-07-06 17:31 | 2015-07-06 17:33 | -118.831 | 45.6655
5W202 | 1575920 | CPCC | CPCC973649 | PP | OR | PENDLETON | BUCKAROO | OH_215360_752850152 | 2015 | Before | 2015-07-04 11:58 | 2015-07-04 13:58 | 2 | 241.367 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman removed a dead squirrel from the transformer and replaced a blown 'B' phase fuse at Pole 215360 | DISTRIBUTION | DEVICE | AUTO | 2015-07-04 15:00 | COMPLETED |  | 2015-07-04 11:58 | 2015-07-04 14:52 | 2015-07-04 14:53 | -118.8158 | 45.6361
5W202 | 1579432 | CPCC | CPCC976542 | PP | OR | PENDLETON | BUCKAROO | TR_164643_619850490 | 2015 | Before | 2015-07-13 07:28 | 2015-07-13 08:21 | 4 | 210.6 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: squirrel | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-07-13 10:30 | COMPLETED |  | 2015-07-13 07:29 | 2015-07-13 13:53 | 2015-07-13 13:58 | -118.818 | 45.6551
5W202 | 1568264 | CPCC | CPCC969022 | PP | OR | PENDLETON | BUCKAROO | TR_164740_619850499 | 2015 | Before | 2015-06-12 01:14 | 2015-06-12 01:58 | 1 | 44.9 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - TRIMMABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: per service man ok for tonight he will have tre crew go by and trim | DISTRIBUTION | CUSTOMER | AUTO | 2015-06-12 04:30 | COMPLETED |  | 2015-06-12 01:17 | 2015-06-12 04:21 | 2015-06-12 04:23 | -118.8189 | 45.6569
5W202 | 1611669 | CPCC | CPCC998289 | PP | OR | PENDLETON | BUCKAROO | TR_137505_842710184 | 2015 | Before | 2015-11-12 09:34 | 2015-11-12 10:55 | 2 | 162.3 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman found blown transformer fuse due to a squirrel; re-fused and it held. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-11-12 12:45 | COMPLETED |  | 2015-11-12 09:34 | 2015-11-12 11:38 | 2015-11-12 11:39 | -118.8766 | 45.6529
5W202 | 1606732 | CPCC | CPCC995543 | PP | OR | PENDLETON | BUCKAROO | TR_163040_619850453 | 2015 | Before | 2015-10-21 15:51 | 2015-10-21 16:29 | 1 | 38.45 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: Serviceman replaced the B/O overhead secondary connector at the weatherhead | DISTRIBUTION | CUSTOMER | AUTO | 2015-10-21 19:00 | COMPLETED |  | 2015-10-21 15:51 | 2015-10-21 16:51 | 2015-10-21 16:54 | -118.8206 | 45.6466
5W202 | 1597850 | CPCC | CPCC989146 | PP | OR | PENDLETON | BUCKAROO | TR_274102_886280449 | 2015 | Before | 2015-09-13 07:55 | 2015-09-13 18:22 | 1 | 627.1 | 0 | 0 | 1 | Y | N | N | N | Y | 2015-09-13 OR Northeast | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | SOURCE: Crew replaced a bad transformer | DISTRIBUTION | CUSTOMER | AUTO | 2015-09-13 11:00 | COMPLETED |  | 2015-09-13 07:55 | 2015-09-13 18:50 | 2015-09-13 18:53 | -118.7986 | 45.6181
5W202 | 1591732 | CPCC | CPCC985058 | PP | OR | PENDLETON | BUCKAROO | TR_164541_619850489 | 2015 | Before | 2015-08-22 10:07 | 2015-08-22 10:33 | 3 | 78.15 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: outage due to squirrel, refused the cutout and customers are back in service | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2015-08-22 10:07 | 2015-08-22 13:52 | 2015-08-22 13:58 | -118.8177 | 45.6533
5W202 | 1605597 | CPCC | CPCC994681 | PP | OR | PENDLETON | BUCKAROO | TR_271304_886280432 | 2015 | Before | 2015-10-16 08:14 | 2015-10-16 15:08 | 1 | 414.067 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | SOURCE: Crew needed to make repairs to the B/O underground secondary service | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-10-16 11:15 | COMPLETED |  | 2015-10-16 08:14 | 2015-10-16 15:09 | 2015-10-16 15:09 | -118.8041 | 45.6218
5W202 | 1607325 | CPCC | CPCC995795 | PP | OR | PENDLETON | BUCKAROO | OH_138904_842710193 | 2015 | Before | 2015-10-25 00:07 | 2015-10-25 06:07 | 30 | 10805.5 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | VEHICLE ACCIDENT |  |  | POLE OH |  |  |  | SOURCE: Crew made pole safe and repaired damaged wire, pole will have to be replaced at another time, all customers restored | DISTRIBUTION | DEVICE | MANUAL | 2015-10-25 06:15 | COMPLETED |  | 2015-10-25 00:07 | 2015-10-25 06:09 | 2015-10-25 06:14 | -118.8758 | 45.6587
5W202 | 1601083 | CPCC | CPCC991016 | PP | OR | PENDLETON | BUCKAROO | OH_086601_802520480 | 2015 | Before | 2015-09-26 06:10 | 2015-09-26 07:07 | 2 | 113.533 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: serviceman reports that there was a blown fuse, patrolled the line and no cause found, refused the cutout and customers are back in service | DISTRIBUTION | DEVICE | AUTO | 2015-09-26 09:45 | COMPLETED |  | 2015-09-26 06:36 | 2015-09-26 07:53 | 2015-09-26 07:58 | -118.8346 | 45.669
5W202 | 1593188 | CPCC | CPCC985820 | PP | OR | PENDLETON | BUCKAROO | TR_162580_619850466 | 2015 | Before | 2015-08-27 17:20 | 2015-08-27 21:22 | 1 | 241.9 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Pri UG, Crew has repaired and restored all customers | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2015-08-27 22:30 | COMPLETED |  | 2015-08-27 17:20 | 2015-08-27 23:15 | 2015-08-27 23:19 | -118.8227 | 45.6529
5W202 | 1607326 | CPCC | CPCC995802 | PP | OR | PENDLETON | BUCKAROO | OH_138904_842710193 | 2015 | Before | 2015-10-25 04:51 | 2015-10-25 06:06 | 15 | 1129.75 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | PLANNED OUTAGE |  |  |  | SOURCE: Crew opened fuse to allow for repairs to be made on outage 995795 | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2015-10-25 04:51 | 2015-10-25 06:10 | 2015-10-25 06:14 | -118.8758 | 45.6587
5W202 | 1592327 | CPCC | CPCC985263 | PP | OR | PENDLETON | BUCKAROO | OH_163502_619850465 | 2015 | Before | 2015-08-24 15:09 | 2015-08-24 17:33 | 1 | 143.533 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Serviceman found blown dip fuse on pole 163502; calling for assistance. Crew made repairs and restored all customers | DISTRIBUTION | DEVICE | MANUAL | 2015-08-25 04:00 | COMPLETED |  | 2015-08-24 15:10 | 2015-08-25 08:20 | 2015-08-25 04:33 | -118.8211 | 45.6528
5W202 | 1592035 | CPCC | CPCC985177 | PP | OR | PENDLETON | BUCKAROO | OH_079600_802520520 | 2015 | Before | 2015-08-24 07:20 | 2015-08-24 07:51 | 10 | 312 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman found fuse open on pole 079600; unknown cause. Re-fused and it held. | DISTRIBUTION | DEVICE | AUTO | 2015-08-24 10:30 | COMPLETED |  | 2015-08-24 07:20 | 2015-08-24 09:41 | 2015-08-24 09:43 | -118.8514 | 45.6691
5W202 | 1592126 | CPCC | CPCC985243 | PP | OR | PENDLETON | BUCKAROO | TR_212806_752850216 | 2015 | Before | 2015-08-24 12:37 | 2015-08-24 13:18 | 1 | 41.017 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | OTHER, KNOWN CAUSE |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman found transformer fuse blown due to fatigue, re-fused and it held. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-08-24 15:45 | COMPLETED |  | 2015-08-24 12:37 | 2015-08-24 14:20 | 2015-08-24 14:23 | -118.8226 | 45.6439
5W202 | 1595980 | CPCC | CPCC988036 | PP | OR | PENDLETON | BUCKAROO | OH_152600_842710111 | 2015 | Before | 2015-09-05 07:18 | 2015-09-05 09:20 | 35 | 4279.333 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD NEST (BMTS) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman cleared birds nest and re-fused, all customers restored | DISTRIBUTION | DEVICE | AUTO | 2015-09-05 10:30 | COMPLETED |  | 2015-09-05 07:18 | 2015-09-05 11:50 | 2015-09-05 11:53 | -118.928 | 45.6547
5W202 | 1616922 | CPCC | CPCC1002821 | PP | OR | PENDLETON | BUCKAROO | OH_211900_752850180 | 2015 | Before | 2015-12-02 01:24 | 2015-12-02 08:27 | 14 | 5925.733 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: Crew made repairs to the B/O underground primary between dip pole# 211900 and transformer# 211980 | DISTRIBUTION | DEVICE | MANUAL | 2015-12-02 09:30 | COMPLETED |  | 2015-12-02 01:24 | 2015-12-02 12:08 | 2015-12-02 12:13 | -118.8248 | 45.6454
5W202 | 1628043 | CPCC | CPCC1016697 | PP | OR | PENDLETON | BUCKAROO | TR_072000_802520536 | 2015 | Before | 2015-12-30 01:46 | 2015-12-30 03:29 | 1 | 103.233 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman replaced a blown transformer fuse | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-12-30 04:45 | COMPLETED |  | 2015-12-30 01:46 | 2015-12-30 07:10 | 2015-12-30 07:13 | -118.8669 | 45.6609
5W202 | 1626196 | CPCC | CPCC1014765 | PP | OR | PENDLETON | BUCKAROO | RC_072201_802520342 | 2015 | Before | 2015-12-21 16:57 | 2015-12-21 20:05 | 184 | 34610.4 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Crew made repairs to the overhead primary that was taken down by the wind | DISTRIBUTION | DEVICE | AUTO | 2015-12-21 20:00 | COMPLETED |  | 2015-12-21 17:00 | 2015-12-22 15:50 | 2015-12-22 15:53 | -118.8664 | 45.6634
5W202 | 1614313 | CPCC | CPCC1001170 | PP | OR | PENDLETON | BUCKAROO | OH_343902_886280531 | 2015 | Before | 2015-11-20 10:01 | 2015-11-20 11:03 | 7 | 430.5 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TERMINATION UG |  |  |  | SOURCE: Crew replaced the B/O underground primary termination on dip pole# 343902 | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2015-11-20 10:01 | 2015-11-20 12:57 | 2015-11-20 12:59 | -118.7991 | 45.6162
5W202 | 1627466 | CPCC | CPCC1016341 | PP | OR | PENDLETON | BUCKAROO | TR_154600_842710114 | 2015 | Before | 2015-12-26 19:29 | 2015-12-26 20:17 | 1 | 48.067 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: replaced transformer fuse | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-12-26 22:30 | COMPLETED |  | 2015-12-26 19:29 | 2015-12-27 18:39 | 2015-12-27 18:43 | -118.9242 | 45.6544
5W202 | 1628306 | CPCC | CPCC1016864 | PP | OR | PENDLETON | BUCKAROO | TR_163309_619850408 | 2015 | Before | 2015-12-31 09:47 | 2015-12-31 11:13 | 5 | 430.083 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: squirrel | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2015-12-31 13:00 | COMPLETED |  | 2015-12-31 09:47 | 2015-12-31 12:47 | 2015-12-31 12:48 | -118.8212 | 45.6511
5W202 | 1618388 | CPCC | CPCC1004918 | PP | OR | PENDLETON | BUCKAROO | RC_072201_802520342 | 2015 | Before | 2015-12-07 16:09 | 2015-12-07 17:15 | 186 | 12285.3 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Wind blew phases together and burnt down primary conductor which locked out field recloser. Crew to make repairs. | DISTRIBUTION | DEVICE | AUTO | 2015-12-07 19:30 | COMPLETED |  | 2015-12-07 16:10 | 2015-12-07 17:35 | 2015-12-07 17:38 | -118.8664 | 45.6634
5W202 | 1626212 | CPCC | CPCC1015181 | PP | OR | PENDLETON | BUCKAROO | TR_288704_886280470 | 2015 | Before | 2015-12-21 23:23 | 2015-12-21 23:53 | 1 | 30.717 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | CONNECTOR OH |  |  |  | SOURCE: Secondary pole caused a problem with the secondary service | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2015-12-21 23:24 | 2015-12-22 16:12 | 2015-12-22 16:15 | -118.8113 | 45.6267
5W202 | 1613819 | CPCC | CPCC1000281 | PP | OR | PENDLETON | BUCKAROO | OH_214600_752850173 | 2015 | Before | 2015-11-17 20:37 | 2015-11-18 09:14 | 7 | 5297.833 | 0 | 0 | 1 | Y | N | N | N | Y | OR Northeast 11-17-2015 | EQUIPMENT FAILURE | POLE FIRE |  |  | POLE OH |  |  |  | SOURCE: crew closed in fuses, picked up all customers. | DISTRIBUTION | DEVICE | AUTO | 2015-11-17 23:45 | COMPLETED |  | 2015-11-17 20:37 | 2015-11-19 03:38 | 2015-11-19 03:38 | -118.818 | 45.6408
5W202 | 1650056 | CPCC | CPCC1034766 | PP | OR | PENDLETON | BUCKAROO | OH_138904_842710193 | 2016 | Before | 2016-03-31 08:21 | 2016-03-31 09:38 | 34 | 2633.867 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD NEST (BMTS) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: located open fuses, patroling(08:48), located open fuses on pole 139100, will close fuses at 138904 to step restore & report(09:18) | DISTRIBUTION | DEVICE | AUTO | 2016-03-31 11:30 | COMPLETED |  | 2016-03-31 08:21 | 2016-04-01 08:18 | 2016-03-31 10:18 | -118.8758 | 45.6587
5W202 | 1650057 | CPCC | CPCC1034779 | PP | OR | PENDLETON | BUCKAROO | OH_139100_842710171 | 2016 | Before | 2016-03-31 09:18 | 2016-03-31 10:09 | 1 | 51.217 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD NEST (BMTS) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Associate to outage# 1034766 | DISTRIBUTION | DEVICE | AUTO | 2016-03-31 12:30 | COMPLETED |  | 2016-03-31 09:18 | 2016-03-31 10:15 | 2016-03-31 10:18 | -118.8726 | 45.6479
5W202 | 1650725 | CPCC | CPCC1035390 | PP | OR | PENDLETON | BUCKAROO | TR_163309_619850408 | 2016 | Before | 2016-04-03 06:54 | 2016-04-03 12:04 | 5 | 1546.917 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Serviceman found B/O Cutout, Requested 2 Journeyman, No takers from Pendleton, Ingle and Weimer from Walla Walla accept callout, Cutout replaced and all customers restored | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2016-04-03 10:00 | COMPLETED |  | 2016-04-03 06:55 | 2016-04-03 15:24 | 2016-04-03 15:28 | -118.8212 | 45.6511
5W202 | 1648794 | CPCC | CPCC1034307 | PP | OR | PENDLETON | BUCKAROO | TR_136402_842710180 | 2016 | Before | 2016-03-27 10:06 | 2016-03-27 12:54 | 2 | 335.7 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: re-fused transformer -- squirrel | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2016-03-27 13:15 | COMPLETED |  | 2016-03-27 10:07 | 2016-03-27 18:30 | 2016-03-27 18:33 | -118.878 | 45.6523
5W202 | 1637793 | CPCC | CPCC1024572 | PP | OR | PENDLETON | BUCKAROO | OH_164003_1550004106 | 2016 | Before | 2016-02-14 08:03 | 2016-02-14 11:18 | 17 | 2007.8 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: crew replaced B/O cu tout | DISTRIBUTION | DEVICE | AUTO | 2016-02-14 11:15 | COMPLETED |  | 2016-02-14 08:03 | 2016-02-14 11:19 | 2016-02-14 11:22 | -118.8192 | 45.6458
5W202 | 1652342 | CPCC | CPCC1036099 | PP | OR | PENDLETON | BUCKAROO | OH_164300_619850447 | 2016 | After | 2016-04-09 07:25 | 2016-04-09 10:41 | 9 | 1762.35 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Crew repaired a bad cut out and replaced a blown fuse | DISTRIBUTION | DEVICE | AUTO | 2016-04-09 11:15 | COMPLETED |  | 2016-04-09 08:11 | 2016-04-10 04:53 | 2016-04-10 04:57 | -118.8191 | 45.65
5W202 | 1655520 | CPCC | CPCC1041526 | PP | OR | PENDLETON | BUCKAROO | OH_210603_1550004111 | 2016 | After | 2016-04-20 18:31 | 2016-04-20 23:02 | 84 | 10958.733 | 0 | 0 | 2 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Crew repaired down primary phase due to tree, all customers restored | DISTRIBUTION | DEVICE | AUTO | 2016-04-20 21:45 | COMPLETED |  | 2016-04-20 18:33 | 2016-04-20 23:03 | 2016-04-20 23:08 | -118.8265 | 45.6411
5W202 | 1676425 | CPCC | CPCC1052563 | PP | OR | PENDLETON | BUCKAROO | OH_138904_842710193 | 2016 | After | 2016-06-23 04:00 | 2016-06-23 06:54 | 15 | 2615.75 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: serviceman reports B and C phases open - refused the 65 amp fuses and they held - cause not found | DISTRIBUTION | DEVICE | AUTO | 2016-06-23 09:00 | COMPLETED |  | 2016-06-23 04:00 | 2016-06-23 07:37 | 2016-06-23 07:42 | -118.8758 | 45.6587
5W202 | 1673509 | CPCC | CPCC1050828 | PP | OR | PENDLETON | BUCKAROO | TR_085400_802520468 | 2016 | After | 2016-06-13 15:52 | 2016-06-13 16:06 | 1 | 14 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: de-energized so the crew could finish repairs to wire down | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2016-06-13 19:00 | COMPLETED |  | 2016-06-13 15:53 | 2016-06-13 16:11 | 2016-06-13 16:13 | -118.8367 | 45.6661
5W202 | 1665851 | CPCC | CPCC1045828 | PP | OR | PENDLETON | BUCKAROO | OH_274105_1550180141 | 2016 | After | 2016-05-18 22:10 | 2016-05-18 23:09 | 105 | 6259.75 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: serviceman found open fuse at FP 274105 'A' phase. patrolled line found no hazard, re fused and it held. Lightning reported in area PROSPER: The arrive time for #1045828 needs to by 2240 please……ML | DISTRIBUTION | DEVICE | AUTO | 2016-05-19 01:30 | COMPLETED |  | 2016-05-18 22:10 | 2016-05-19 07:56 | 2016-05-19 01:28 | -118.797 | 45.6189
5W202 | 1665882 | CPCC | CPCC1045945 | PP | OR | PENDLETON | BUCKAROO | TR_346600_886280562 | 2016 | After | 2016-05-19 06:17 | 2016-05-19 07:17 | 1 | 59.95 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman replaced blown transformer fuse caused by lightning, restored all customers | DISTRIBUTION | CUSTOMER | AUTO | 2016-05-19 09:30 | COMPLETED |  | 2016-05-19 06:18 | 2016-05-19 07:20 | 2016-05-19 07:23 | -118.7946 | 45.6114
5W202 | 1666033 | CPCC | CPCC1046093 | PP | OR | PENDLETON | BUCKAROO | OH_118904_1550606335 | 2016 | After | 2016-05-19 13:16 | 2016-05-19 14:24 | 2 | 135.533 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD SUSPECTED, NO MORTALITY |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Found fuse open on pole 118904 due to possibly a bird; patrolled, found nothing, re-fused and it held. | DISTRIBUTION | DEVICE | AUTO | 2016-05-19 16:30 | COMPLETED |  | 2016-05-19 13:17 | 2016-05-19 15:56 | 2016-05-19 15:58 | -119.0189 | 45.6749
5W202 | 1661122 | CPCC | CPCC1043532 | PP | OR | PENDLETON | BUCKAROO | OH_215360_752850152 | 2016 | After | 2016-05-04 19:22 | 2016-05-04 23:15 | 7 | 1630.767 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: tap fuse blown -- patrolling line -- tree branches -- re-fused | DISTRIBUTION | DEVICE | MANUAL | 2016-05-05 04:45 | COMPLETED |  | 2016-05-04 19:22 | 2016-05-05 02:18 | 2016-05-05 02:23 | -118.8158 | 45.6361
5W202 | 1667117 | CPCC | CPCC1046503 | PP | OR | PENDLETON | BUCKAROO | OH_211901_752850172 | 2016 | After | 2016-05-21 14:58 | 2016-05-21 17:58 | 29 | 2299 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | TRANSFORMER OH |  |  |  | SOURCE: Tap fuses blown -- isolated bad transformer -- re-fused tap line -- did callout for crew Wanous & Hatanpaa | DISTRIBUTION | DEVICE | AUTO | 2016-05-21 18:15 | COMPLETED |  | 2016-05-21 15:04 | 2016-05-21 17:59 | 2016-05-21 18:02 | -118.8248 | 45.6453
5W202 | 1671902 | CPCC | CPCC1049568 | PP | OR | PENDLETON | BUCKAROO | TR_288502_886280466 | 2016 | After | 2016-06-08 08:20 | 2016-06-08 11:52 | 3 | 636.1 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: squirrel PROSPER: 2) Outage 1049568: Reported as Bird Suspected, No Mortality – caused by a squirrel – please change to Animal. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2016-06-08 11:30 | COMPLETED |  | 2016-06-08 08:20 | 2016-06-09 07:52 | 2016-06-08 14:23 | -118.8101 | 45.6247
5W202 | 1682714 | CPCC | CPCC1056201 | PP | OR | PENDLETON | BUCKAROO | OH_138904_842710193 | 2016 | After | 2016-07-13 02:24 | 2016-07-13 05:06 | 43 | 6972.45 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD SUSPECTED, NO MORTALITY |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Tap fuses blown -- patrolling line -- found 2 phases wrapped together -- did callout for X-tra Man -- unwound primary & spliced a piece of it -- re-fused | DISTRIBUTION | DEVICE | MANUAL | 2016-07-13 06:00 | COMPLETED |  | 2016-07-13 02:24 | 2016-07-13 05:06 | 2016-07-13 05:08 | -118.8758 | 45.6587
5W202 | 1673510 | CPCC | CPCC1050782 | PP | OR | PENDLETON | BUCKAROO | TR_087500_802520482 | 2016 | After | 2016-06-13 09:05 | 2016-06-13 16:06 | 1 | 420.983 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Found wire down at pole 087501 (span of 3ph primary) | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2016-06-13 16:30 | COMPLETED |  | 2016-06-13 09:05 | 2016-06-13 16:11 | 2016-06-13 16:13 | -118.8326 | 45.6681
5W202 | 1674932 | CPCC | CPCC1051636 | PP | OR | PENDLETON | BUCKAROO | OH_152600_842710111 | 2016 | After | 2016-06-18 00:37 | 2016-06-18 03:42 | 27 | 4991.4 | 0 | 0 | 1 | Y | N | N | N | Y | OR Northeast 06-18-2016 | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: serviceman patrolled and found no cause, refused and restored all customers | DISTRIBUTION | DEVICE | AUTO | 2016-06-18 03:45 | COMPLETED |  | 2016-06-18 00:37 | 2016-06-18 05:47 | 2016-06-18 05:52 | -118.928 | 45.6547
5W202 | 1699282 | CPCC | CPCC1067871 | PP | OR | PENDLETON | BUCKAROO | BCK_CB5W202 | 2016 | After | 2016-09-06 10:02 | 2016-09-06 12:34 | 1532 | 233374.667 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD NEST (BMTS) |  |  | POLE OH |  |  |  | SOURCE: General Foreman found bird nest across all 3 phases at FP# 085501, sending crew to clear nest and check pole. | DISTRIBUTION | DEVICE | AUTO | 2016-09-06 13:15 | COMPLETED |  | 2016-09-06 10:02 | 2016-09-07 10:09 | 2016-09-06 16:03 | -118.8368 | 45.6762
5W202 | 1696291 | CPCC | CPCC1066069 | PP | OR | PENDLETON | BUCKAROO | OH_207201_886280328 | 2016 | After | 2016-08-25 23:32 | 2016-08-26 06:08 | 9 | 3559.8 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CABLE UG |  |  |  | SOURCE: B/O Primary UG Cable, Crew onsite making repairs, repairs completed, all customers restored | DISTRIBUTION | DEVICE | MANUAL | 2016-08-26 07:45 | COMPLETED |  | 2016-08-25 23:33 | 2016-08-26 06:08 | 2016-08-26 06:13 | -118.8359 | 45.6346
5W202 | 1701478 | CPCC | CPCC1069178 | PP | OR | PENDLETON | BUCKAROO | OH_274105_1550180141 | 2016 | After | 2016-09-14 15:32 | 2016-09-14 17:08 | 105 | 10109.75 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Squirrel on transformer, caused blown line fuse | DISTRIBUTION | DEVICE | AUTO | 2016-09-14 19:15 | COMPLETED |  | 2016-09-14 15:39 | 2016-09-14 17:24 | 2016-09-14 17:28 | -118.797 | 45.6189
5W202 | 1689703 | CPCC | CPCC1061235 | PP | OR | PENDLETON | BUCKAROO | TR_164643_619850490 | 2016 | After | 2016-08-03 09:50 | 2016-08-03 10:43 | 1 | 53.017 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | SOURCE: serviceman reports squirrel caused cut out to open, refused and holding | DISTRIBUTION | CUSTOMER | AUTO | 2016-08-03 13:00 | COMPLETED |  | 2016-08-03 09:50 | 2016-08-03 14:43 | 2016-08-03 14:48 | -118.818 | 45.6551
5W202 | 1686541 | CPCC | CPCC1059787 | PP | OR | PENDLETON | BUCKAROO | TR_067100_802520543 | 2016 | After | 2016-07-25 09:19 | 2016-07-25 10:34 | 1 | 74.4 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman refused transformer and restored all customers | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2016-07-25 09:19 | 2016-07-25 10:57 | 2016-07-25 10:58 | -118.8581 | 45.6757
5W202 | 1707056 | CPCC | CPCC1073016 | PP | OR | PENDLETON | BUCKAROO | OH_138904_842710193 | 2016 | After | 2016-10-02 21:45 | 2016-10-02 23:46 | 39 | 4704.05 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: 2 Tap fuses blown -- ran Arcos for a X-tra man to help patrol -- no trouble found -- re-fused | DISTRIBUTION | DEVICE | MANUAL | 2016-10-03 01:00 | COMPLETED |  | 2016-10-02 21:45 | 2016-10-03 04:27 | 2016-10-03 04:28 | -118.8758 | 45.6587
5W202 | 1727590 | CPCC | CPCC1092324 | PP | OR | PENDLETON | BUCKAROO | OH_152600_842710111 | 2016 | After | 2016-12-16 13:55 | 2016-12-16 14:58 | 22 | 1390.033 | 0 | 0 | 1 | Y | N | N | N | Y | OR Consolidated 12-14-2016 | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman found open line fuse, no cause found, refused and holding PROSPER: Arrive time of 1430 | DISTRIBUTION | DEVICE | AUTO | 2016-12-16 17:30 | COMPLETED |  | 2016-12-16 14:56 | 2016-12-19 08:27 | 2016-12-16 16:53 | -118.928 | 45.6547
5W202 | 1710653 | CPCC | CPCC1075536 | PP | OR | PENDLETON | BUCKAROO | OH_210603_1550004111 | 2016 | After | 2016-10-14 01:01 | 2016-10-14 14:53 | 84 | 56245.417 | 0 | 0 | 2 | Y | N | N | N | Y | OR Northeast 10-13-2016 | TREES | TREE - NON-PREVENTABLE | WEATHER | WIND | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Wanous 07408 reports phase down, #6 copper, behind 4222 SW Vista, can isolate will contact dispatch to model.1452 repairs completed, service restored. | DISTRIBUTION | DEVICE | MANUAL | 2016-10-14 08:00 | COMPLETED |  | 2016-10-14 01:05 | 2016-10-18 11:28 | 2016-10-14 19:28 | -118.8265 | 45.6411
5W202 | 1725626 | CPCC | CPCC1088945 | PP | OR | PENDLETON | BUCKAROO | BCK_CB5W202 | 2016 | After | 2016-12-12 03:02 | 2016-12-12 07:21 | 1535 | 398076.667 | 0 | 0 | 1 | Y | N | N | N | Y | OR Consolidated 12-09-2016 | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Serviceman reports they are patroling line - found possible issue with Field recloser 5W502 Found bad 3 phase cutout between 2 reclosers and substation breaker PROSPER: Please change/add an arrive time of 0345 to this outage Damage location was cutouts at FP #085802 | DISTRIBUTION | DEVICE | MANUAL | 2016-12-12 07:30 | COMPLETED |  | 2016-12-12 03:02 | 2016-12-16 08:39 | 2016-12-12 09:13 | -118.8368 | 45.6762
5W202 | 1729014 | CPCC | CPCC1092917 | PP | OR | PENDLETON | BUCKAROO | RC_072201_802520342 | 2016 | After | 2016-12-20 06:56 | 2016-12-20 08:24 | 185 | 16372.5 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | RECLOSER-NORMAL OPERATION OH (NO CAUSE FOUND) |  |  |  | SOURCE: high wind blew debris into line, svcmn tested, recloser held | DISTRIBUTION | DEVICE | AUTO | 2016-12-20 10:00 | COMPLETED |  | 2016-12-20 06:56 | 2016-12-20 19:25 | 2016-12-20 19:28 | -118.8664 | 45.6634
5W202 | 1725652 | CPCC | CPCC1088996 | PP | OR | PENDLETON | BUCKAROO | TR_179660_886280346 | 2016 | After | 2016-12-12 09:20 | 2016-12-12 10:36 | 1 | 76.05 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: fuse open on transformer , no cause found | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2016-12-12 12:30 | COMPLETED |  | 2016-12-12 09:20 | 2016-12-12 11:06 | 2016-12-12 11:08 | -118.8288 | 45.6554
5W202 | 1715179 | CPCC | CPCC1080600 | PP | OR | PENDLETON | BUCKAROO | TR_128004_842710096 | 2016 | After | 2016-10-30 20:34 | 2016-10-30 21:48 | 1 | 73.683 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: Crew repaired a bad cut out Related to Outage 108059 | DISTRIBUTION | CUSTOMER | AUTO | 2016-10-30 23:45 | COMPLETED |  | 2016-10-30 20:34 | 2016-10-31 06:46 | 2016-10-31 06:48 | -118.8753 | 45.6609
5W202 | 1729009 | CPCC | CPCC1092948 | PP | OR | PENDLETON | BUCKAROO | SB_128009_842710153 | 2016 | After | 2016-12-20 08:30 | 2016-12-20 10:31 | 123 | 14880.95 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: wire down, crew to repair, all repairs completed | DISTRIBUTION | DEVICE | AUTO | 2016-12-20 12:15 | COMPLETED |  | 2016-12-20 09:04 | 2016-12-20 19:24 | 2016-12-20 19:28 | -118.8747 | 45.6603
5W202 | 1723044 | CPCC | CPCC1086067 | PP | OR | PENDLETON | BUCKAROO | BCK_CB5W202 | 2016 | After | 2016-12-05 23:46 | 2016-12-05 23:46 | 0 | 0 | 1534 | 306.8 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: T&R | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2016-12-05 23:46 | 2016-12-06 07:40 | 2016-12-06 07:43 | -118.8368 | 45.6762
5W202 | 1750437 | CPCC | CPCC1117330 | PP | OR | PENDLETON | BUCKAROO | OH_119000_842710139 | 2017 | After | 2017-02-25 18:33 | 2017-02-26 00:59 | 42 | 16199.4 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | OTHER, KNOWN CAUSE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Wire down, cause unknown. Crew to make repairs | DISTRIBUTION | DEVICE | AUTO | 2017-02-25 21:45 | COMPLETED |  | 2017-02-25 18:42 | 2017-02-26 01:00 | 2017-02-26 01:03 | -118.893 | 45.6614
5W202 | 1736175 | CPCC | CPCC1103495 | PP | OR | PENDLETON | BUCKAROO | TR_090201_94990453 | 2017 | After | 2017-01-10 19:58 | 2017-01-10 21:17 | 1 | 78.25 | 0 | 0 | 1 | Y | N | N | N | Y | OR Consolidated 01-02-2017 | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: Serviceman replaced B/O Connectors and restored all customers | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2017-01-10 23:00 | COMPLETED |  | 2017-01-10 19:59 | 2017-01-11 05:21 | 2017-01-11 05:23 | -118.8272 | 45.663
5W202 | 1745182 | CPCC | CPCC1113074 | PP | OR | PENDLETON | BUCKAROO | TR_212400_752850171 | 2017 | After | 2017-02-07 19:12 | 2017-02-07 19:45 | 4 | 132.8 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Re-fused transformer -- no cause | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2017-02-07 21:30 | COMPLETED |  | 2017-02-07 19:12 | 2017-02-08 04:38 | 2017-02-08 04:43 | -118.8234 | 45.6369
5W202 | 1741866 | CPCC | CPCC1109079 | PP | OR | PENDLETON | BUCKAROO | TR_179660_886280346 | 2017 | After | 2017-01-25 06:41 | 2017-01-25 14:00 | 1 | 438.517 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | SOURCE: Crew replaced bad secondary underground cable | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2017-01-25 11:45 | COMPLETED |  | 2017-01-25 06:42 | 2017-01-25 15:59 | 2017-01-25 16:03 | -118.8288 | 45.6554
5W202 | 1746727 | CPCC | CPCC1114395 | PP | OR | PENDLETON | BUCKAROO | TR_164740_619850499 | 2017 | After | 2017-02-12 18:54 | 2017-02-12 19:58 | 1 | 64.067 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | SOURCE: Serviceman replaced a bad connection at the weatherhead Work completed at 1958 | DISTRIBUTION | CUSTOMER | AUTO | 2017-02-12 22:00 | COMPLETED |  | 2017-02-12 18:54 | 2017-02-13 13:23 | 2017-02-13 08:18 | -118.8189 | 45.6569
5W202 | 1740438 | CPCC | CPCC1107911 | PP | OR | PENDLETON | BUCKAROO | TR_151780_842710116 | 2017 | After | 2017-01-22 00:11 | 2017-01-22 01:17 | 1 | 65.683 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: REPLACED TRANSFORMER FUSE, CAUSE UNKNOWN | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2017-01-22 03:15 | COMPLETED |  | 2017-01-22 00:11 | 2017-01-22 08:18 | 2017-01-22 08:18 | -118.9286 | 45.6558
5W202 | 1772377 | CPCC | CPCC1138392 | PP | OR | PENDLETON | BUCKAROO | BCK_CB5W202 | 2017 | After | 2017-05-07 15:29 | 2017-05-07 15:29 | 0 | 0 | 1542 | 359.8 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: T&R Unknown | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2017-05-07 15:29 | 2017-05-07 21:35 | 2017-05-07 21:38 | -118.8368 | 45.6762
5W202 | 1778767 | CPCC | CPCC1142984 | PP | OR | PENDLETON | BUCKAROO | TR_342301_886280493 | 2017 | After | 2017-05-28 06:52 | 2017-05-28 12:45 | 1 | 352.7 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | TRANSFORMER OH |  |  |  | SOURCE: Squirrel damaged Cutout, Crew needs to change out, ARCOS Callout initiated, Crew changed cutout but found Bad bushings on transformer, Crew to Change Out | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2017-05-28 15:00 | COMPLETED |  | 2017-05-28 06:53 | 2017-05-28 13:22 | 2017-05-28 13:23 | -118.8015 | 45.6069
5W202 | 1756335 | CPCC | CPCC1121841 | PP | OR | PENDLETON | BUCKAROO | TR_164543_619850487 | 2017 | After | 2017-03-19 13:21 | 2017-03-19 13:59 | 1 | 38.883 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman changed transformer fuse blown due to suicidal squirrell, all customers restored | DISTRIBUTION | CUSTOMER | AUTO | 2017-03-19 16:30 | COMPLETED |  | 2017-03-19 13:21 | 2017-03-19 17:40 | 2017-03-19 17:43 | -118.8177 | 45.6527
5W202 | 1778952 | CPCC | CPCC1143053 | PP | OR | PENDLETON | BUCKAROO | TR_164507_619850467 | 2017 | After | 2017-05-29 08:54 | 2017-05-29 10:34 | 5 | 498.333 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Re-fused transformer -- squirrel | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2017-05-29 12:00 | COMPLETED |  | 2017-05-29 08:54 | 2017-05-29 17:53 | 2017-05-29 17:58 | -118.8188 | 45.6528
5W202 | 1755184 | CPCC | CPCC1121146 | PP | OR | PENDLETON | BUCKAROO | TR_027900_842710095 | 2017 | After | 2017-03-14 15:43 | 2017-03-14 16:20 | 1 | 36.267 | 0 | 0 | 1 | Y | N | N | N | N |  | INTERFERENCE | OTHER INTERFERING OBJECT |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Customer got their equipment tangled in line, a crew in the area assisted and all power restored. | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2017-03-14 19:00 | COMPLETED |  | 2017-03-14 15:44 | 2017-03-14 16:22 | 2017-03-14 16:23 | -118.8964 | 45.6882
5W202 | 1755385 | CPCC | CPCC1121239 | PP | OR | PENDLETON | BUCKAROO | OH_138904_842710193 | 2017 | After | 2017-03-15 12:27 | 2017-03-15 13:23 | 30 | 1679 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | SOURCE: Line fuse was blown, cause was transformer bank on FP# 136402. | DISTRIBUTION | DEVICE | AUTO | 2017-03-15 15:30 | COMPLETED |  | 2017-03-15 12:27 | 2017-03-15 13:59 | 2017-03-15 14:03 | -118.8758 | 45.6587
5W202 | 1784853 | CPCC | CPCC1146507 | PP | OR | PENDLETON | BUCKAROO | TR_162480_619850409 | 2017 | After | 2017-06-15 16:47 | 2017-06-15 17:33 | 1 | 46.667 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | OTHER UG (EXPLAIN IN COMMENTS FIELD) |  |  |  | SOURCE: Serviceman tightened a loose neutral connection at the transformer | DISTRIBUTION | CUSTOMER | AUTO | 2017-06-15 20:00 | COMPLETED |  | 2017-06-15 16:47 | 2017-06-15 17:45 | 2017-06-15 17:48 | -118.8221 | 45.6522
5W202 | 1780638 | CPCC | CPCC1144114 | PP | OR | PENDLETON | BUCKAROO | OH_163501_619850475 | 2017 | After | 2017-06-04 01:43 | 2017-06-04 03:00 | 25 | 1935 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: serviceman reports open fuse (100 amp) at FP 163501 and open transformer fuse at FP 164516 - patrolled and then refused at both locations and customers power restored | DISTRIBUTION | DEVICE | AUTO | 2017-06-04 04:45 | COMPLETED |  | 2017-06-04 01:43 | 2017-06-04 17:59 | 2017-06-04 18:03 | -118.8213 | 45.6534
5W202 | 1784535 | CPCC | CPCC1146327 | PP | OR | PENDLETON | BUCKAROO | TR_121502_836510023 | 2017 | After | 2017-06-14 17:32 | 2017-06-14 21:08 | 1 | 215.433 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Crew repaired broken primary conductor at F/P 122801 PROSPER: power out | DISTRIBUTION | CUSTOMER | MANUAL | 2017-06-14 22:02 | COMPLETED |  | 2017-06-14 17:33 | 2017-06-15 09:20 | 2017-06-14 22:13 | -119.015 | 45.6686
5W202 | 1782788 | CPCC | CPCC1145652 | PP | OR | PENDLETON | BUCKAROO | TR_121502_836510023 | 2017 | After | 2017-06-10 22:02 | 2017-06-10 23:26 | 2 | 168.467 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: replaced transformer fuse | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2017-06-10 22:02 | 2017-06-11 02:58 | 2017-06-11 03:00 | -119.015 | 45.6686
5W202 | 1788632 | CPCC | CPCC1148987 | PP | OR | PENDLETON | BUCKAROO | OH_119000_842710139 | 2017 | After | 2017-06-26 17:06 | 2017-06-27 04:18 | 23 | 15462.133 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Line Fuse open, patrolling for cause, no cause found, assume lightning, refused and restored all customers | DISTRIBUTION | DEVICE | MANUAL | 2017-06-27 06:00 | COMPLETED |  | 2017-06-26 17:06 | 2017-06-27 04:58 | 2017-06-27 05:03 | -118.893 | 45.6614
5W202 | 1788687 | CPCC | CPCC1149161 | PP | OR | PENDLETON | BUCKAROO | TR_357001_132440014 | 2017 | After | 2017-06-26 23:08 | 2017-06-27 07:27 | 3 | 1499.15 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: replaced transformer fuse | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2017-06-27 09:15 | COMPLETED |  | 2017-06-26 23:09 | 2017-06-27 07:33 | 2017-06-27 07:39 | -118.8971 | 45.6892
5W202 | 1788758 | CPCC | CPCC1149211 | PP | OR | PENDLETON | BUCKAROO | OH_081601_802520511 | 2017 | After | 2017-06-27 08:55 | 2017-06-27 08:55 | 0 | 0 | 4 | 2.8 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: found blown fuse on FP 081601 | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2017-06-27 08:55 | 2017-06-27 10:37 | 2017-06-27 10:39 | -118.8452 | 45.6697
5W202 | 1788749 | CPCC | CPCC1149182 | PP | OR | PENDLETON | BUCKAROO | OH_081600__3886717 | 2017 | After | 2017-06-27 06:49 | 2017-06-27 08:56 | 3 | 381 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: found fuse blown on FP 081600 | DISTRIBUTION | DEVICE | MANUAL | 2017-06-27 15:30 | COMPLETED |  | 2017-06-27 06:49 | 2017-06-27 10:36 | 2017-06-27 10:39 | -118.845 | 45.6697
5W202 | 1788752 | CPCC | CPCC1149172 | PP | OR | PENDLETON | BUCKAROO | TR_125000_842710159 | 2017 | After | 2017-06-26 18:49 | 2017-06-27 07:55 | 2 | 1572.467 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | SOURCE: transformer replaced | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2017-06-27 15:30 | COMPLETED |  | 2017-06-27 03:34 | 2017-06-27 10:35 | 2017-06-27 10:39 | -118.8809 | 45.6605
5W202 | 1788753 | CPCC | CPCC1149012 | PP | OR | PENDLETON | BUCKAROO | TR_127003_842710158 | 2017 | After | 2017-06-26 17:16 | 2017-06-27 07:56 | 1 | 880.117 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | SOURCE: transformer replaced | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2017-06-27 15:30 | COMPLETED |  | 2017-06-26 17:16 | 2017-06-27 10:35 | 2017-06-27 10:39 | -118.8765 | 45.6603
5W202 | 1788874 | CPCC | CPCC1149053 | PP | OR | PENDLETON | BUCKAROO | TR_027900_842710095 | 2017 | After | 2017-06-26 17:56 | 2017-06-27 12:34 | 1 | 1117.9 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT | WEATHER | LIGHTNING | TRANSFORMER OH |  |  |  | SOURCE: b/o xfmr. | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2017-06-27 15:30 | COMPLETED |  | 2017-06-26 17:56 | 2017-06-27 15:24 | 2017-06-27 15:29 | -118.8964 | 45.6882
5W202 | 1788877 | CPCC | CPCC1149176 | PP | OR | PENDLETON | BUCKAROO | Line Cut-107736 | 2017 | After | 2017-06-27 05:26 | 2017-06-27 15:23 | 3 | 1790.5 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE | WEATHER | LIGHTNING | POLE OH |  |  |  | SOURCE: pole is repaired PROSPER: power out | DISTRIBUTION | DEVICE | MANUAL | 2017-06-27 17:00 | COMPLETED |  | 2017-06-27 05:26 | 2017-06-28 08:50 | 2017-06-27 15:29 | -118.8432 | 45.6687
5W202 | 1789790 | CPCC | CPCC1149681 | PP | OR | PENDLETON | BUCKAROO | Line Cut-107777 | 2017 | After | 2017-06-29 12:24 | 2017-06-29 14:07 | 2 | 205.533 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | JUMPER WIRE/STIRRUP OH |  |  |  | SOURCE: Broken primary jumper on pole 122600 | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2017-06-29 12:24 | 2017-06-29 15:29 | 2017-06-29 15:34 | -119.0129 | 45.67
5W202 | 1794247 | CPCC | CPCC1152569 | PP | OR | PENDLETON | BUCKAROO | TR_164547_619850472 | 2017 | After | 2017-07-13 08:35 | 2017-07-13 09:20 | 4 | 181.133 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown line fuses, patrolling for cause, Squirrel Suicide, Refused and restored | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2017-07-13 11:45 | COMPLETED |  | 2017-07-13 08:35 | 2017-07-13 11:21 | 2017-07-13 11:23 | -118.8185 | 45.6534
5W202 | 1801226 | CPCC | CPCC1156540 | PP | OR | PENDLETON | BUCKAROO | TR_190600_886280338 | 2017 | After | 2017-08-02 20:52 | 2017-08-02 21:49 | 1 | 56.483 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman refused transformer fuse, no cause found, restored all customers | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2017-08-03 | COMPLETED |  | 2017-08-02 20:53 | 2017-08-03 02:21 | 2017-08-03 02:23 | -118.8706 | 45.6405
5W202 | 1802571 | CPCC | CPCC1157310 | PP | OR | PENDLETON | BUCKAROO | OH_274105_1550180141 | 2017 | After | 2017-08-07 08:59 | 2017-08-07 11:40 | 107 | 17164.583 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown line fuse, patrolled, no cause found | DISTRIBUTION | DEVICE | AUTO | 2017-08-07 12:15 | COMPLETED |  | 2017-08-07 09:05 | 2017-08-07 11:49 | 2017-08-07 11:53 | -118.797 | 45.6189
5W202 | 1816229 | CPCC | CPCC1165169 | PP | OR | PENDLETON | BUCKAROO | TR_163640_619850502 | 2017 | After | 2017-09-22 22:48 | 2017-09-23 00:29 | 1 | 101.8 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | SOURCE: bad connectors on service wire, wire burnt down. NO STRUCTURES involved. PROSPER: hazard | DISTRIBUTION | CUSTOMER | AUTO | 2017-09-23 01:30 | COMPLETED |  | 2017-09-22 22:48 | 2017-09-25 14:31 | 2017-09-23 00:44 | -118.8213 | 45.6553
5W202 | 1821881 | CPCC | CPCC1168259 | PP | OR | PENDLETON | BUCKAROO | TR_212800_752850217 | 2017 | After | 2017-10-16 14:26 | 2017-10-16 15:29 | 1 | 62.667 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | SOURCE: Replaced connectors at the weatherhead | DISTRIBUTION | CUSTOMER | AUTO | 2017-10-16 17:00 | COMPLETED |  | 2017-10-16 14:27 | 2017-10-16 15:32 | 2017-10-16 15:33 | -118.8224 | 45.6435
5W202 | 1822127 | CPCC | CPCC1168299 | PP | OR | PENDLETON | BUCKAROO | TR_273101_886280446 | 2017 | After | 2017-10-17 08:47 | 2017-10-17 10:48 | 2 | 240.533 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: squrriel | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2017-10-17 11:30 | COMPLETED |  | 2017-10-17 08:47 | 2017-10-17 13:15 | 2017-10-17 13:18 | -118.7992 | 45.6187
5W202 | 1834928 | CPCC | CPCC1177906 | PP | OR | PENDLETON | BUCKAROO | Line Cut-110074 | 2017 | After | 2017-12-08 13:08 | 2017-12-08 13:48 | 7 | 285.25 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | EMERGENCY DAMAGE REPAIR |  |  | CROSS ARM OH |  |  |  | SOURCE: pole fire, crew making repairs | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2017-12-08 13:08 | 2017-12-08 15:51 | 2017-12-08 15:54 | -118.825 | 45.6443
5W202 | 1838797 | CPCC | CPCC1180368 | PP | OR | PENDLETON | BUCKAROO | TR_159000_548520311 | 2017 | After | 2017-12-28 09:44 | 2017-12-28 10:32 | 3 | 143.4 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Re-fused transformer | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2017-12-28 12:15 | COMPLETED |  | 2017-12-28 09:44 | 2017-12-28 15:34 | 2017-12-28 15:39 | -118.7887 | 45.6461
5W202 | 1841253 | CPCC | CPCC1183075 | PP | OR | PENDLETON | BUCKAROO | RC_072201_802520342 | 2018 | After | 2018-01-09 14:09 | 2018-01-09 17:20 | 189 | 32009 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Wire Down at F/P 120001 Crew repaired a broken conductor at F/ P 120001 | DISTRIBUTION | DEVICE | AUTO | 2018-01-09 18:45 | COMPLETED |  | 2018-01-09 14:17 | 2018-01-09 20:14 | 2018-01-09 20:19 | -118.8664 | 45.6634
5W202 | 1846047 | CPCC | CPCC1187222 | PP | OR | PENDLETON | BUCKAROO | OH_152600_842710111 | 2018 | After | 2018-02-03 07:21 | 2018-02-03 11:18 | 35 | 8287.417 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Crew repaired broken primary conductor due to a anchor breaking loose | DISTRIBUTION | DEVICE | MANUAL | 2018-02-03 12:14 | COMPLETED |  | 2018-02-03 07:24 | 2018-02-03 18:52 | 2018-02-03 18:54 | -118.928 | 45.6547
5W202 | 1857221 | CPCC | CPCC1195068 | PP | OR | PENDLETON | BUCKAROO | OH_119000_842710139 | 2018 | After | 2018-03-22 10:48 | 2018-03-22 13:07 | 3 | 415.25 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: refused | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2018-03-22 10:48 | 2018-03-22 15:02 | 2018-03-22 15:06 | -118.893 | 45.6614
5W202 | 1857224 | CPCC | CPCC1195066 | PP | OR | PENDLETON | BUCKAROO | OH_152600_842710111 | 2018 | After | 2018-03-22 10:29 | 2018-03-22 13:07 | 12 | 1893.6 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: refused | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2018-03-22 10:37 | 2018-03-22 15:02 | 2018-03-22 15:06 | -118.928 | 45.6547
5W202 | 1857222 | CPCC | CPCC1195069 | PP | OR | PENDLETON | BUCKAROO | OH_176701_842710130 | 2018 | After | 2018-03-22 10:56 | 2018-03-22 13:07 | 15 | 1955.5 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | WIND |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: refused | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2018-03-22 10:56 | 2018-03-22 15:02 | 2018-03-22 15:06 | -118.9609 | 45.6567
5W202 | 1858671 | CPCC | CPCC1195996 | PP | OR | PENDLETON | BUCKAROO | OH_119000_842710139 | 2018 | After | 2018-03-27 13:14 | 2018-03-27 14:42 | 37 | 3251.067 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: conductor becoming unraveled at pole 165500 | DISTRIBUTION | DEVICE | MANUAL | 2018-03-27 16:30 | COMPLETED |  | 2018-03-27 13:23 | 2018-03-27 16:47 | 2018-03-27 16:51 | -118.893 | 45.6614
5W202 | 1862636 | CPCC | CPCC1198497 | PP | OR | PENDLETON | BUCKAROO | OH_152600_842710111 | 2018 | After | 2018-04-13 23:11 | 2018-04-14 01:30 | 29 | 4039.217 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: serviceman reports that there were two fuses blown, patrolled the line and found nothing, refused the cutouts and it held, all customers are back in service | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2018-04-13 23:11 | 2018-04-14 03:42 | 2018-04-14 03:45 | -118.928 | 45.6547
5W202 | 1865004 | CPCC | CPCC1199429 | PP | OR | PENDLETON | BUCKAROO | TR_070102_802520533 | 2018 | After | 2018-04-23 08:18 | 2018-04-23 09:40 | 1 | 81.65 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CONNECTOR OH |  |  |  | SOURCE: Bad order connectors on service. Connectors have been replaced. | DISTRIBUTION | CUSTOMER | AUTO | 2018-04-23 11:30 | COMPLETED |  | 2018-04-23 09:43 | 2018-04-23 20:45 | 2018-04-23 20:45 | -118.8699 | 45.6618
5W202 | 1865658 | CPCC | CPCC1199792 | PP | OR | PENDLETON | BUCKAROO | TR_161440_619850403 | 2018 | After | 2018-04-27 06:12 | 2018-04-27 07:48 | 4 | 384.733 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | CUT-OUT B/O OH |  |  |  | SOURCE: failed cut out, 2nd man needed(06:47 r4r) | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2018-04-27 09:15 | COMPLETED |  | 2018-04-27 06:12 | 2018-04-27 10:47 | 2018-04-27 10:50 | -118.8242 | 45.6519
5W202 | 1867976 | CPCC | CPCC1201828 | PP | OR | PENDLETON | BUCKAROO | TR_082981_802520399 | 2018 | After | 2018-05-08 23:35 | 2018-05-09 02:25 | 1 | 169.733 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CROSS ARM OH |  |  |  | SOURCE: Bad cutout arm -- every one is back in service -- work on routine work PROSPER: power out | DISTRIBUTION | CUSTOMER | MANUAL | 2018-05-09 04:15 | COMPLETED |  | 2018-05-08 23:37 | 2018-05-09 09:03 | 2018-05-09 04:25 | -118.8437 | 45.6731
5W202 | 1867974 | CPCC | CPCC1201698 | PP | OR | PENDLETON | BUCKAROO | TR_164841_619850498 | 2018 | After | 2018-05-08 19:33 | 2018-05-09 03:15 | 1 | 462.067 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Tree fell & tore off customer weatherhead -- disconnected service -- customer needs a electrician -- no one to advise | DISTRIBUTION | CUSTOMER | MANUAL | 2018-05-09 04:30 | COMPLETED |  | 2018-05-08 19:33 | 2018-05-09 04:19 | 2018-05-09 04:20 | -118.8182 | 45.6572
5W202 | 1867983 | CPCC | CPCC1201811 | PP | OR | PENDLETON | BUCKAROO | BCK_CB5W202 | 2018 | After | 2018-05-08 22:20 | 2018-05-08 22:20 | 0 | 0 | 1716 | 600.6 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Trip & Close | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2018-05-08 22:20 | 2018-05-09 04:19 | 2018-05-09 04:25 | -118.8368 | 45.6761
5W202 | 1868328 | CPCC | CPCC1201863 | PP | OR | PENDLETON | BUCKAROO | TR_175800_842710092 | 2018 | After | 2018-05-09 07:47 | 2018-05-09 11:08 | 1 | 200.483 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Line Fuse Open due to Lightning, Servicmean patrolled and refused | DISTRIBUTION | CUSTOMER | MANUAL | 2018-05-09 12:30 | COMPLETED |  | 2018-05-09 07:47 | 2018-05-10 16:15 | 2018-05-10 16:20 | -118.9625 | 45.6586
5W202 | 1868340 | CPCC | CPCC1201897 | PP | OR | PENDLETON | BUCKAROO | OH_152600_842710111 | 2018 | After | 2018-05-09 11:03 | 2018-05-09 11:09 | 22 | 114.767 | 0 | 0 | 1 | Y | N | N | N | N |  | WEATHER | LIGHTNING |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Line Fuse Open due to Lightning, Serviceman patrolled and refused | DISTRIBUTION | DEVICE | AUTO | 2018-05-09 14:30 | COMPLETED |  | 2018-05-09 11:03 | 2018-05-10 16:16 | 2018-05-10 16:20 | -118.928 | 45.6547
5W202 | 1868994 | CPCC | CPCC1202349 | PP | OR | PENDLETON | BUCKAROO | TR_087300_802520473 | 2018 | After | 2018-05-13 19:43 | 2018-05-13 20:40 | 1 | 56.85 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Serviceman replaced a blown fuse at F/P 088401 | DISTRIBUTION | CUSTOMER | AUTO | 2018-05-13 22:45 | COMPLETED |  | 2018-05-13 19:43 | 2018-05-14 07:08 | 2018-05-14 07:10 | -118.8322 | 45.665
5W202 | 1869293 | CPCC | CPCC1202440 | PP | OR | PENDLETON | BUCKAROO | TR_029100_1550541152 | 2018 | After | 2018-05-15 00:19 | 2018-05-15 01:57 | 1 | 98.25 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Fuse blown, cause unknown. Servicemnan replaced the blown fuse | DISTRIBUTION | CUSTOMER | AUTO | 2018-05-15 03:30 | COMPLETED |  | 2018-05-15 00:19 | 2018-05-15 13:52 | 2018-05-15 13:55 | -119.0169 | 45.6785
5W202 | 1870138 | CPCC | CPCC1202849 | PP | OR | PENDLETON | BUCKAROO | TR_346600_886280562 | 2018 | After | 2018-05-19 10:09 | 2018-05-19 11:27 | 4 | 311.867 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: located open fuse due to animal contact, no damage, refused and restored | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2018-05-19 13:15 | COMPLETED |  | 2018-05-19 10:09 | 2018-05-19 11:54 | 2018-05-19 11:55 | -118.7946 | 45.6114
5W202 | 1872884 | CPCC | CPCC1204381 | PP | OR | PENDLETON | BUCKAROO | RC_072201_802520342 | 2018 | After | 2018-06-01 04:19 | 2018-06-01 06:54 | 188 | 23388.712 | 0 | 0 | 2 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Phase Down, Serviceman isolated and closed Recloser, Crew to repair PROSPER: change time to first out 06/01/2018 4:18:35, was 06/01/2018 4:14:05 | DISTRIBUTION | DEVICE | MANUAL | 2018-06-01 08:45 | COMPLETED |  | 2018-06-01 04:20 | 2018-06-01 08:39 | 2018-06-01 07:00 | -118.8664 | 45.6634
5W202 | 1872922 | CPCC | CPCC1204404 | PP | OR | PENDLETON | BUCKAROO | OH_138904_842710193 | 2018 | After | 2018-06-01 07:18 | 2018-06-01 09:41 | 30 | 4305 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: patrolling line, found melted out line fuse, replaced | DISTRIBUTION | DEVICE | AUTO | 2018-06-01 10:45 | COMPLETED |  | 2018-06-01 07:18 | 2018-06-01 09:42 | 2018-06-01 09:45 | -118.8758 | 45.6587
5W202 | 1875733 | CPCC | CPCC1206229 | PP | OR | PENDLETON | BUCKAROO | TR_126900_836510016 | 2018 | After | 2018-06-12 14:20 | 2018-06-12 19:23 | 1 | 302.883 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | OTHER OH (EXPLAIN IN COMMENTS FIELD) |  |  |  | SOURCE: serviceman reports that the meter was bad, will install new meter | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2018-06-12 21:00 | COMPLETED |  | 2018-06-12 14:20 | 2018-06-13 04:38 | 2018-06-13 04:40 | -119.0036 | 45.6754
5W202 | 1876923 | CPCC | CPCC1207306 | PP | OR | PENDLETON | BUCKAROO | OH_152600_842710111 | 2018 | After | 2018-06-17 22:41 | 2018-06-18 02:41 | 35 | 8376.083 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | OTHER, KNOWN CAUSE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: 2nd man assist for patrolling requested, arcos(23:13 r4r), arcos dispatched(23:47 r4r), patroling(00:47 r4r), located open fuses due to wrapeed primary conductors, repaired, refused and restored | DISTRIBUTION | DEVICE | MANUAL | 2018-06-18 04:00 | COMPLETED |  | 2018-06-17 22:41 | 2018-06-18 03:19 | 2018-06-18 03:20 | -118.928 | 45.6547
5W202 | 1878096 | CPCC | CPCC1210798 | PP | OR | PENDLETON | BUCKAROO | OH_138904_842710193 | 2018 | After | 2018-06-20 05:24 | 2018-06-20 08:08 | 43 | 7072.067 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Tap fuse blown -- patrolled line -- no trouble found -- re-fused | DISTRIBUTION | DEVICE | MANUAL | 2018-06-20 10:15 | COMPLETED |  | 2018-06-20 07:13 | 2018-06-21 05:52 | 2018-06-21 05:55 | -118.8758 | 45.6587
5W202 | 1878397 | CPCC | CPCC1210825 | PP | OR | PENDLETON | BUCKAROO | TR_033881_762510377 | 2018 | After | 2018-06-20 10:11 | 2018-06-20 13:12 | 1 | 181.267 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | SOURCE: 1 bad leg on bad ug service -- installed service saver | DISTRIBUTION | CUSTOMER | MANUAL | 2018-06-20 15:00 | COMPLETED |  | 2018-06-20 10:11 | 2018-06-22 06:13 | 2018-06-22 06:15 | -118.8005 | 45.5998
5W202 | 1878375 | CPCC | CPCC1211121 | PP | OR | PENDLETON | BUCKAROO | TR_033881_762510377 | 2018 | After | 2018-06-21 15:56 | 2018-06-21 20:27 | 1 | 271.25 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | SOURCE: Need crew to repair ug service Crew reports repairs made, customer power restored. | DISTRIBUTION | CUSTOMER | MANUAL | 2018-06-21 22:00 | COMPLETED |  | 2018-06-21 15:56 | 2018-06-22 06:01 | 2018-06-22 06:05 | -118.8005 | 45.5998
5W202 | 1879554 | CPCC | CPCC1212085 | PP | OR | PENDLETON | BUCKAROO | TR_160181_619850376 | 2018 | After | 2018-06-26 05:42 | 2018-06-26 09:03 | 1 | 200.75 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | SOURCE: Bad order secondary UG. Installed service saver. | DISTRIBUTION | CUSTOMER | MANUAL | 2018-06-26 13:15 | COMPLETED |  | 2018-06-26 05:42 | 2018-06-27 07:43 | 2018-06-27 07:45 | -118.8263 | 45.6479
5W202 | 1884423 | CPCC | CPCC1215487 | PP | OR | PENDLETON | BUCKAROO | TR_272004_886280456 | 2018 | After | 2018-07-14 08:27 | 2018-07-14 10:26 | 1 | 118.75 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | CONNECTOR OH |  |  |  | SOURCE: connection at pole | DISTRIBUTION | CUSTOMER | MANUAL | 2018-07-14 12:30 | COMPLETED |  | 2018-07-14 08:27 | 2018-07-14 15:40 | 2018-07-14 15:45 | -118.8017 | 45.6169
5W202 | 1884716 | CPCC | CPCC1216221 | PP | OR | PENDLETON | BUCKAROO | BCK_CB5W202 | 2018 | After | 2018-07-15 21:03 | 2018-07-15 21:19 | 426 | 6631.4 | 0 | 0 | 1 | Y | N | N | N | N |  | LOSS OF SUPPLY | LOSS OF FEED FROM SUPPLIER |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Cause of outage was loss of feed from BPA at Roundup Substation. Power was restored at 2119. | DISTRIBUTION | DEVICE | AUTO | 2018-07-15 23:30 | COMPLETED |  | 2018-07-15 21:10 | 2018-07-16 15:25 | 2018-07-16 00:15 | -118.8368 | 45.6759
5W202 | 1886236 | CPCC | CPCC1216896 | PP | OR | PENDLETON | BUCKAROO | TR_033980_762510375 | 2018 | After | 2018-07-19 11:10 | 2018-07-19 15:56 | 1 | 286.117 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | SECONDARY CABLE UG |  |  |  | SOURCE: B/O secondary cable, svc man to install svc saver | DISTRIBUTION | CUSTOMER | MANUAL | 2018-07-19 17:30 | COMPLETED |  | 2018-07-19 11:10 | 2018-07-19 17:52 | 2018-07-19 17:55 | -118.8006 | 45.601
5W202 | 1886895 | CPCC | CPCC1217230 | PP | OR | PENDLETON | BUCKAROO | TR_272004_886280456 | 2018 | After | 2018-07-21 05:42 | 2018-07-21 09:31 | 1 | 228.3 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Service burned up in trees. Service cleared of trees. | DISTRIBUTION | CUSTOMER | MANUAL | 2018-07-21 11:15 | COMPLETED |  | 2018-07-21 05:43 | 2018-07-22 06:33 | 2018-07-22 06:35 | -118.8017 | 45.6169
5W202 | 1891266 | CPCC | CPCC1219612 | PP | OR | PENDLETON | BUCKAROO | TR_162807_619850512 | 2018 | After | 2018-08-07 06:08 | 2018-08-07 07:23 | 5 | 377.5 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blown XFRM Fuse. Cause is starling. | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2018-08-07 08:45 | COMPLETED |  | 2018-08-07 06:08 | 2018-08-07 14:26 | 2018-08-07 14:30 | -118.8217 | 45.6574
5W202 | 1891268 | CPCC | CPCC1219611 | PP | OR | PENDLETON | BUCKAROO | BCK_CB5W202 | 2018 | After | 2018-08-07 06:02 | 2018-08-07 06:02 | 0 | 0 | 1553 | 414.133 | 1 | Y | N | N | N | N |  | ANIMALS | BIRD MORTALITY (NON-PROTECTED SPECIES) |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: TNR due to Blown xfmr fuse caused by starling. See outage 1219612 | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2018-08-07 06:02 | 2018-08-07 14:26 | 2018-08-07 14:30 | -118.8368 | 45.6761
5W202 | 1893023 | CPCC | CPCC1220795 | PP | OR | PENDLETON | BUCKAROO | TR_342300_886280497 | 2018 | After | 2018-08-14 07:20 | 2018-08-14 08:34 | 1 | 73.633 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Serviceman replaced transformer fuse blown due to Squirrel | DISTRIBUTION | CUSTOMER | AUTO | 2018-08-14 10:00 | COMPLETED |  | 2018-08-14 07:20 | 2018-08-14 12:31 | 2018-08-14 12:35 | -118.8015 | 45.6074
5W202 | 1896178 | CPCC | CPCC1222342 | PP | OR | PENDLETON | BUCKAROO | OH_079600_802520520 | 2018 | After | 2018-08-25 19:00 | 2018-08-25 23:58 | 10 | 2978 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: serviceman reports that there was a blown tap line fuse, patrolled the line and no cause found, refused the cutout and customers are back in service | DISTRIBUTION | DEVICE | MANUAL | 2018-08-26 00:30 | COMPLETED |  | 2018-08-25 19:00 | 2018-08-26 03:49 | 2018-08-26 03:50 | -118.8514 | 45.6691
5W202 | 1897030 | CPCC | CPCC1222999 | PP | OR | PENDLETON | BUCKAROO | TR_165741_619850636 | 2018 | After | 2018-08-29 16:47 | 2018-08-29 17:17 | 1 | 30.267 | 0 | 0 | 1 | Y | N | N | N | N |  | TREES | TREE - NON-PREVENTABLE |  |  | CONNECTOR OH |  |  |  | SOURCE: REMOVED TREE BRANCH & REPAIRED CONNECTOR | DISTRIBUTION | CUSTOMER | AUTO | 2018-08-29 19:30 | COMPLETED |  | 2018-08-29 16:47 | 2018-08-29 17:24 | 2018-08-29 17:25 | -118.8172 | 45.6566
5W202 | 1902207 | CPCC | CPCC1230292 | PP | OR | PENDLETON | BUCKAROO | Line Cut-114566 | 2018 | After | 2018-09-21 00:50 | 2018-09-21 01:16 | 1554 | 40067.3 | 0 | 0 | 1 | Y | N | N | N | N |  | PLANNED | INTENTIONAL TO CLEAR TROUBLE |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: To Isolate R-542 at Pilot Rock Sub | DISTRIBUTION | DEVICE | AUTO | 2018-09-21 04:00 | COMPLETED |  | 2018-09-21 00:53 | 2018-09-21 01:40 | 2018-09-21 01:45 | -118.8369 | 45.6756
5W202 | 1905792 | CPCC | CPCC1232466 | PP | OR | PENDLETON | BUCKAROO | BCK_CB5W202 | 2018 | After | 2018-10-07 15:25 | 2018-10-07 15:25 | 0 | 0 | 1555 | 362.833 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: T&R, unknown | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2018-10-07 15:25 | 2018-10-07 16:38 | 2018-10-07 16:40 | -118.8368 | 45.6761
5W202 | 1913909 | CPCC | CPCC1238921 | PP | OR | PENDLETON | BUCKAROO | TR_164841_619850498 | 2018 | After | 2018-11-15 10:44 | 2018-11-15 11:33 | 10 | 490.5 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: Blowen cut out - squirrel | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2018-11-15 14:30 | COMPLETED |  | 2018-11-15 08:55 | 2018-11-16 14:33 | 2018-11-15 17:25 | -118.8182 | 45.6572
5W202 | 1915753 | CPCC | CPCC1242700 | PP | OR | PENDLETON | BUCKAROO | BCK_CB5W202 | 2018 | After | 2018-11-25 11:07 | 2018-11-25 11:07 | 0 | 0 | 1555 | 388.75 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: t & r | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2018-11-25 11:07 | 2018-11-25 12:10 | 2018-11-25 12:15 | -118.8368 | 45.6761
5W202 | 1915801 | CPCC | CPCC1242726 | PP | OR | PENDLETON | BUCKAROO | TR_214903_752850132 | 2018 | After | 2018-11-25 16:11 | 2018-11-25 16:53 | 1 | 41.9 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: Blown Fuse, no cause found. Re-fused, customer in service | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2018-11-25 18:45 | COMPLETED |  | 2018-11-25 16:11 | 2018-11-25 16:54 | 2018-11-25 16:55 | -118.8189 | 45.6446
5W202 | 1917575 | CPCC | CPCC1244013 | PP | OR | PENDLETON | BUCKAROO | TR_084801_802520498 | 2018 | After | 2018-12-03 14:54 | 2018-12-03 18:00 | 2 | 371.533 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | SECONDARY CONDUCTOR OH |  |  |  | SOURCE: Burnt up service, equipment replaced, customer in service | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2018-12-03 14:54 | 2018-12-03 18:01 | 2018-12-03 18:05 | -118.839 | 45.6717
5W202 | 1923732 | CPCC | CPCC1252427 | PP | OR | PENDLETON | BUCKAROO | TR_074202_802520525 | 2018 | After | 2018-12-29 13:49 | 2018-12-29 14:51 | 1 | 61.95 | 0 | 0 | 1 | Y | N | N | N | N |  | OTHER | UNKNOWN |  |  | FUSE (NO CAUSE FOUND) OH |  |  |  | SOURCE: REPLACED TRANSFORMER FUSE | DISTRIBUTION | SERVICE TRANSFORMER | AUTO | 2018-12-29 16:45 | COMPLETED |  | 2018-12-29 13:50 | 2018-12-29 16:11 | 2018-12-29 16:15 | -118.8625 | 45.6641
5W202 | 1924778 | CPCC | CPCC1252926 | PP | OR | PENDLETON | BUCKAROO | TR_078800_802520363 | 2019 | After | 2019-01-02 14:48 | 2019-01-02 18:52 | 1 | 244.183 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | TRANSFORMER OH |  |  |  | SOURCE: Bad Transformer Bushing, Crew to change transformer | DISTRIBUTION | SERVICE TRANSFORMER | MANUAL | 2019-01-02 19:45 | COMPLETED |  | 2019-01-02 14:49 | 2019-01-02 19:36 | 2019-01-02 19:40 | -118.8531 | 45.6722
5W202 | 1928883 | CPCC | CPCC1257248 | PP | OR | PENDLETON | BUCKAROO | BCK_CB5W202 | 2019 | After | 2019-01-20 10:31 | 2019-01-20 10:31 | 0 | 0 | 1557 | 441.15 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: T&R; squirrel. see outage 1257250 | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2019-01-20 10:31 | 2019-01-20 13:25 | 2019-01-20 13:30 | -118.8368 | 45.6761
5W202 | 1928882 | CPCC | CPCC1257250 | PP | OR | PENDLETON | BUCKAROO | TR_164640_619850496 | 2019 | After | 2019-01-20 10:45 | 2019-01-20 13:23 | 4 | 633.4 | 0 | 0 | 1 | Y | N | N | N | N |  | ANIMALS | ANIMALS |  |  | NO DISTRIBUTION DAMAGE |  |  |  | SOURCE: located open fuse due to squirrel, no damage, refused and restored PROSPER: power out | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2019-01-20 10:45 | 2019-01-23 10:33 | 2019-01-20 13:25 | -118.8194 | 45.6554
5W202 | 1933527 | CPCC | CPCC1259663 | PP | OR | PENDLETON | BUCKAROO | Line Cut-117132 | 2019 | After | 2019-02-06 13:25 | 2019-02-06 14:54 | 10 | 891.5 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | DETERIORATION OR ROTTING |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: wire down | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2019-02-06 14:12 | 2019-02-06 16:16 | 2019-02-06 16:20 | -118.8515 | 45.6693
5W202 | 1933528 | CPCC | CPCC1259656 | PP | OR | PENDLETON | BUCKAROO | BCK_CB5W202 | 2019 | After | 2019-02-06 13:17 | 2019-02-06 13:17 | 0 | 0 | 1557 | 389.25 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | B/O EQUIPMENT |  |  | PRIMARY CONDUCTOR OH |  |  |  | SOURCE: Trip and reclose | DISTRIBUTION | DEVICE | AUTO |  | COMPLETED |  | 2019-02-06 13:17 | 2019-02-06 16:17 | 2019-02-06 16:20 | -118.8368 | 45.6761
5W202 | 1937477 | CPCC | CPCC1263341 | PP | OR | PENDLETON | BUCKAROO | TR_211802_752850199 | 2019 | After | 2019-02-19 19:04 | 2019-02-19 19:50 | 2 | 91.333 | 0 | 0 | 1 | Y | N | N | N | N |  | EQUIPMENT FAILURE | POLE FIRE |  |  | POLE OH |  |  |  | SOURCE: | DISTRIBUTION | SERVICE TRANSFORMER | AUTO |  | COMPLETED |  | 2019-02-19 19:04 | 2019-02-19 21:18 | 2019-02-19 21:20 | -118.8253 | 45.6435