## Cover
Clearance Table for Distribution and Transmission Line Inspectors
NESC and GO 95 Grandfathering Matrix
Facility Point Inspection NESC and GO 95 Frequently Asked Questions
Condition Code Dropdowns
Asset Management Procedure 069
Author: | Joe Clifton / Greg Linden
Revised by: | Brian Pagel
Approval: | Jon Connelly, Pacific Power
Approval: | Alex Vaz, Rocky Mountain Power
Authoring Department: | Pacific Power and Rocky Mountain Power Asset Management
Approved Location: | DFS\PDXCO\SHR04\Publications\FPP\DIS\PRO
File Number-Name: | 069-Clearance Table, Grandfathering Matrix, FAQ and Dropdown Codes.xls
Revision Number: | R23
Revision Date: | 2023-03-09
The most current version of this document is posted to engineering's intranet page for distribution forms, policies and procedures.
Master file located on the Engineering drive \\J:\Publications\FPP\DIS\PRO
Modification of this document must be approved by the authoring department and processed by engineering publications,

## Clearance Table
PacifiCorp's Inspection Clearance Table ** (Do not use Table for construction, See Construction Standards)
All distances are minimums required by the NESC at worst conditions, 3300' elev. or below. For more details see Transmission standards, section TC.
|  | Upper Level | Insulated com. conductors; messengers; surge protection wires; grounded guys; ungrounded guys exposed to 0-300 V; neutral conductors meeting Rule 230E1; supply cable meeting Rule 230C1 | Supply cables of 0-750V meeting Rules 230C2 or C3 | Non insulated com. conductors; Unguarded rigid live parts 0-750V | Supply cable over 750V meeting Rules 230C2 or 230C3; open supply conductors, 0-750 V; ungrounded guys exposed to 300-750 V | Open Supply Conductors | [8 empty] | Nonmetallic, effective grounded support arms and equipment cases | Ungrounded cases that contains equip. on 750V or less | Ungraded Ridge live parts and Cases on 750-22kV
Modified Last: | 2013-09-09 09:25 | [5 empty] | Over 750V to 8.7kV to ground | Over 8.7V to 22kV to gnd (34.5 kV to phase) | Over 22 kV to 27 kV to gnd (46 kV to phase) | Over 28 kV to 42 kV to grd (69 kV to phase) | Over 42 kV to 70 kV to gnd (115 kV to phase) | Over 70 kV to 84 kV to gnd. (138 kV to phase) | Over 84 kV to 98 kV to gnd (161 kV to phase) | Over 98 kV to 140 kV to gnd. (230 kV to phase) | Over 140kV to 210kV to gd (345KV to phase)
Ground Clearance - Where wires, conductors, or cables crossover or overhang | [15 empty] | Where rigid part over hang or are along NESC 232B3 |  |  | 232
1 | Track rails of railroad (except electrified railroads using overhead trolley conductors |  | 23.5' | 24.0' | 24.0' | 24.5' | 26.5' | 26.5' | 26.7' | 27.5' | 28.5' | 28.9' | 29.3' | 30.7' | 33.0' | -- | -- | --
2 | Roads, streets, and other areas subjected to truck traffic. |  | 15.5' | 16.0' | 16.0' | 16.5' | 18.5' | 18.5' | 18.7' | 19.2' | 20.2' | 20.6' | 21.0' | 22.4' | 24.7' | 15.0' | 16.0' | 18.0'
3 | Driveways, parking lots, and alleys |  | 15.5' | 16.0' | 16.0' | 16.5' | 18.5' | 18.5' | 18.7' | 19.2' | 20.2' | 20.6' | 21.0' | 22.4' | 24.7' | 15.0' | 16.0' | 18.0'
4 | Other land traversed by vehicles, such as cultivated, grazing, forest, orchard, etc. |  | 15.5' | 16.0' | 16.0' | 16.5' | 18.5' | 18.5' | 18.7' | 19.2' | 20.2' | 20.6' | 21.0' | 22.4' | 24.7' | 15.0' | 16.0' | 18.0'
5 | Spaces and ways subject to pedestrians or restricted traffic only. |  | 9.5' | 12.0' | 12.0' | 12.5' | 14.5' | 14.5' | 14.7' | 15.2' | 16.1' | 16.6' | 17.0' | 18.4' | 20.7' | 11.0' | 12.0' | 14.0'
Vertical Clearance - Conductors & cables on different supports Upper level | [18 empty] | 233
1 | Insulated com. conductors; messengers; surge protection wires; grounded guys; ungrounded guys exposed to 0-300 V; neutral conductors meeting Rule 230E1; supply cable needing Rule 230C1 |  | 2.0' | 2.0' | 2.0' | 2.0' | 4.0' | 4.0' | 4.2' | 4.7' | 5.6' | 6.1' | 6.5' | 7.9' | 10.2'
2 | Non insulated communication conductors; supply cables of 0-750 V meeting Rules 230C2 or 230 C3 |  | 2.0' | 2.0' | 2.0' | 2.0' | 6.0' | 6.0' | 6.2' | 6.7' | 7.6' | 8.1' | 8.5' | 9.9' | 12.2'
3 | Supply cable over 750V meeting Rules 230C2 or 230C3; open supply conductors, 0-750 V; ungrounded guys exposed to 300-750 V |  | 4.0' | 2.0' | 2.0' | 2.0' | 2.0' | 2.0' | 2.2' | 2.7' | 3.6' | 4.1' | 4.5' | 5.9' | 8.2'
4 | Over 750V to 22kV to ground (34.5 kV to phase |  | -- | -- | -- | -- | 2.0' | 2.0' | 2.2' | 2.7' | 3.6' | 4.1' | 4.5' | 5.9' | 8.2'
5 | Over 22 kV to 27 kV to ground (46 kV to phase) |  | -- | -- | -- | -- | -- | -- | 2.3' | 2.8' | 3.8' | 4.2' | 4.7' | 6.1' | 8.4'
6 | Over 28 kV to 42 kV to ground (69 kV to phase) |  | -- | -- | -- | -- | -- | -- | -- | 3.3' | 4.3' | 4.7' | 5.2' | 6.6' | 8.9'
7 | Over 42 kV to 70 kV to ground (115 kV to phase) |  | -- | -- | -- | -- | -- | -- | -- | -- | 5.2' | 5.7' | 6.1' | 7.5' | 9.8'
8 | Over 70 kV to 84 kV to ground 138 kV to phase) |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | 6.1' | 6.6' | 8.0' | 10.3'
9 | Over 84 kV to 98 kV to ground (161 kV to phase) |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 7.1' | 8.5' | 10.8'
10 | Over 98 kV to 140 kV to ground (230 kV to phase) |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 9.9' | 12.2'
Vertical Clearance - Between conductors on the same supports | [18 empty] | 235
1 | Communication Conductors & Cables
| a | Located in Communication Space | 40.0" | 40.0" | 40.0" | 40.0" | 40.0" | 40.0" | 40.0" | 40.0" | 47.0" | 52.0" | 56.9" | 73.7" | 101.3"
| b | Located in Supply Space | 16.0" | 16.0" | 16.0" | 16.0" | 16.0" | 40.0" | 40.0" | 40.0" | 47.0" | 52.0" | 56.9" | 73.7" | 101.3"
2 | Open Supply Conductors & Cables
| a | Open conductors 0 to 750 V; Supply Cable meeting Rule230C1,2,or3; Neutral cond. Rule 230E1. | 16.0" | 16.0" | 16.0" | 16.0" | 16.0" | 21.6" | 23.6" | 29.6" | 40.8" | 46.4" | 52.0" | 68.8" | 96.4"
| b | 750V to 8.7 kV | -- | -- | -- | 16" | 16.0" | 24.0" | 26.8" | 32.8" | 44.0" | 49.3" | 55.2" | 72.0" | 99.6"
| c | Over 8.7 kV to 22 kV to ground | -- | -- | -- | -- | -- | 30.1" | 32.1" | 38.1" | 49.3" | 54.9" | 60.5" | 77.3" | 104.9"
| d | Over 22 kV to 27 kV to ground (46 kV to Phase) | -- | -- | -- | -- | -- | 32.1" | 34.1" | 40.1" | 51.3" | 56.9" | 62.5" | 79.3" | 106.9"
| e | Over 27 kV to 42 kV to ground (69 kV to Phase) | -- | -- | -- | -- | -- | -- | -- | 46.1" | 57.3" | 62.9" | 68.5" | 85.3" | 112.9"
| f | Over 42 kV to 70 kV to ground (115 kV to Phase) | -- | -- | -- | -- | -- | -- | -- | -- | 68.5" | 74.1" | 79.7" | 96.5" | 124.1"
| g | Over 70 kV to 84 kV to ground (138 kV to Phase) | -- | -- | -- | -- | -- | -- | -- | -- |  | 79.7" | 85.3" | 102.1" | 129.7"
| h | Over 84 kV to 98 kV to ground (161 kV to Phase) | -- | -- | -- | -- | -- | -- | -- | -- |  |  | 90.9" | 107.7" | 135.3"
| i | Over 98 kV to 140 kV to ground (230 kV to Phase) | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  | 124.5" | 152.1"
| j | Over 140kV to 210kV to ground (345kV to Phase) | [12 empty] | 179.7
Clearances of Wires, Conductors and Cables, & Unguarded Rigid Live Parts - Adjacent but Not Attached to Buildings & Other Installations Except Bridges. No Wind | [18 empty] | 234
1 | Buildings
| Horizontal to Walls, projections and guarded windows, Unguarded windows, Balconies, and areas readily acceptable to people |  | 4.5' | 5.0' | 5.0' | 5.5' | 7.5' | 7.5' | 7.7' | 8.2' | 9.1' | 9.6' | 10.0' | 11.4' | 13.7
| Vertical over or under roofs or projections not readily accessible to pedestrians |  | 3' | 3.5' | 10.0' | 10.5' | 12.5' | 12.5' | 12.7' | 13.2' | 14.1' | 14.6' | 15.0' | 16.4' | 18.7
| Vertical to decks, balconies, roofs, etc., accessible to pedestrians, and over roofs not accessible to trucks |  | 10.5' | 11.0' | 11.0' | 11.5' | 13.5' | 13.5' | 13.7' | 14.2' | 15.1' | 15.6' | 16.0' | 17.4' | 19.7
| Vertical over roofs accessible to trucks |  | 15.5' | 16.0' | 16.0' | 16.5' | 18.5' | 18.5' | 18.7' | 19.2' | 20.1' | 20.6' | 21.0' | 22.4' | 24.7
2 | Signs, chimneys, billboards, radio and television antennas, tanks, and other installations not classified as buildings or bridges
| Horizontal |  | 3.0' | 3.5' | 5.0' | 5.5' | 7.5' | 7.5' | 7.7' | 8.2' | 9.1' | 9.6' | 10.0' | 11.4' | 13.7
| Vertical over or under |  | 3.0' | 3.5' | 5.5' | 6.0' | 8.0' | 8.0' | 8.2' | 8.7' | 9.6' | 10.1' | 10.5' | 11.9' | 14.2
3 | Other supporting structures, wires, conductors, or cables of one line passing near lighting support, traffic signal support, or a supporting structure of a second line, not attached
| Horizontal |  | 5.0' | 5.0' | 5.0' | 5.0' | 5.0' | 5.0' | 5.0' | 5.0' | 5.7' | 6.1' | 6.6' | 8.0' | 10.3
| Vertical |  | 4.5' | 4.5' | 4.5' | 4.5' | 5.5' | 5.5' | 5.5' | 5.5' | 6.2' | 6.6' | 7.1' | 8.5' | 10.8
4 | Vertical clearance to service ( 0 - 750 V), not readily accessible to pedestrians, that meets or terminates at a through-the-roof support & does not cross more than 6' of roof or is 4' or less from the roof edge shall be 18 inches. * See Distribution Standard DC-151 page 5.
Clearances of Wires, Conductors and Cables From Bridges | [18 empty] | 234
1 | Clearance over bridges.
| a. | Attached | 3.0' | 3.0' | 3.0' | 3.5' | 5.5' | 5.5' | 5.7' | 6.2' | 7.1' | 7.6' | 8.0' | 9.4' | 11.7
| b. | Not attached | 10.0' | 10.0' | 10.0' | 10.5' | 12.5' | 12.5' | 12.7' | 13.2' | 14.1' | 14.6' | 15.0' | 16.4' | 18.7
2 | Clearance beside, under or within bridge structure
| a. | Readily Accessible portion of bridge
|  | Attached | 3.0' | 3.0' | 3.0' | 3.5' | 5.5' | 5.5' | 5.7' | 6.2' | 7.1' | 7.6' | 8.0' | 9.4' | 11.7
|  | Not attached | 5.0' | 5.0' | 5.0' | 5.5' | 7.5' | 7.5' | 7.7' | 8.2' | 9.1' | 9.6' | 10.0' | 11.4' | 13.7
| b. | Ordinarily inaccessible portions of bridge
|  | Attached | 3.0' | 3.0' | 3.0' | 3.5' | 5.5' | 5.5' | 5.7' | 6.2' | 7.1' | 7.6' | 8.0' | 9.4' | 11.7
|  | Not attached | 4.0' | 4.0' | 4.0' | 4.5' | 6.5' | 6.5' | 6.7' | 7.2' | 8.1' | 7.6' | 9.0' | 10.4' | 12.7
Clearances of Wires Conductors and Cables Over Or Near Swimming Pools | [18 empty] | 234
1 | Clearance in any direction from the water, edge of pool, or base of diving platform. (Figure 8, "A") |  | 22.5' | 23.0' | 22.5' | 23.0' | 25.0' | 25.0' | 25.2' | 25.7' | 26.6' | 27.1' | 27.5' | 28.9' | 31.2
2 | Clearance to diving platform, tower, etc. (Figure 8, "B") |  | 14.5' | 15.0' | 14.5' | 15.0' | 17.0' | 17.0' | 17.2' | 17.7' | 18.6' | 19.1' | 19.5' | 20.9' | 23.2
| Exception to Rules 1 and 2 above: |  | Since 1984, Rules do not apply to insulated services over 10' horizontally from edge of pool, platforms, etc.
Other Clearances or Requirements.
1 | Minimum vertical clr between communication cable of different companies is 4" NESC Rule 235H.
2 | If a drip loop of conductors entering a luminaire or traffic signal bracket from the surface of structure is above communication cable, the lowest loop shall be 12" above communication cable or through bolt. It can be reduced to 3" if covered with non-metallic covering and extends into bracket 2".
3 | Minimum vertical clearance between power supply lines & communication cable mid-span carried on same supports is 30". NESC Rule 235C2b(1)(a)
4 | Horizontal clearance from structure to side walk curb - 6" (PacifiCorp recommended 18") |  | NESC: C=4' D=6" PacifiCorp: D=18"
5 | Conductors 0 - 300 V attached to the side of a building and/or run alongside the building shall have clearances not less than 3" since 2002, and one inch clearance for 1981-2001.
6 | Horizontal clearance from structure to fire hydrant - 4'. Exception: allows 3' if 4' is not attainable. (3' pre 2002)
(Pre 2002: 3')
A. 12' (10.5' if building height does not permit) (Pre 1977: 10' and 8')
B. 3' min. around doors, fire escapes, etc. (not readily accessible to pedestrians)
3' min. below or beside unguarded openable windows. (Since 1984)
C. 12" between communication wire and service wire. (Since 1981)
D. 40" between communication wire and service wire
at service pole (12" if this is a meter pole).
E. 40" between communication wire and service wire at
support structure.
F. 16' over driveway (See Grandfather Matrix for exceptions).
G. 18” or 3' drip loop to roof, see Fig. 6 above.
See Matrix for exceptions. Pre 1977, no requirement.
H. 18.5' min. clearance above road
for primary 750V-22kV.
Fig. 1
Fig. 2
Fig. 3
Fig. 4
Fig. 5
Fig. 7
Fig. 8
Fig. 9
A
B
C
D
E
F
G
A
H
Fig. 10
Fig. 5
3’ vertical clearance
18” vertical clearance
Fig. 6
Note on Q10: Clifton, Joseph: Table 232-21D lists this as 9 feet

## Clearance Table - Elev3301-9300
PacifiCorp's Inspection Clearance Table ** (Do not use Table for construction, See Construction Standards)
All distances are minimums required by the NESC at worst conditions for Transmission between 3301' - 9300' elevation. For more details see Transmission standards, section TC.
|  |  | Elevation - 3301 to 6300 ft. | [5 empty] | Elevation - 6301 to 9300 ft.
|  | Upper Level | Open Supply Conductors | [5 empty] | Open Supply Conductors
Modified Last: | 2013-09-09 09:25 |  | 42 kV to 70kV phase-to-ground 115 kV phase-to-phase (ft.) | 70 kV to 84 kV phase-to-ground 138 kV phase-to-phase (ft.) | 84 kV to 98 kV phase-to-ground 161 kV phase-to-phase (ft.) | 98 kV to 140 kV phase-to-ground 230 kV phase-to-phase | 140 kV to 210 kV phase-to-ground 345 phase-to-phase | 210 kV to 318 kV phase-to-ground 500 kV phase-to-phase | 42 kV to 70kV phase-to-ground 115 kV phase-to-phase (ft.) | 70 kV to 84 kV phase-to-ground 138 kV phase-to-phase (ft.) | 84 kV to 98 kV phase-to-ground 161 kV phase-to-phase (ft.) | 98 kV to 140 kV phase-to-ground 230 kV phase-to-phase | 140 kV to 210 kV phase-to-ground 345 phase-to-phase | 210 kV to 318 kV phase-to-ground 500 kV phase-to-phase
Ground Clearance - Where wires, conductors, or cables crossover or overhang
1 | Track rails of railroad (except electrified railroads using overhead trolley conductors |  | 28.2' | 28.8' | 29.3' | 30.8' | 33.3' | 37.3' | 28.4' | 28.9' | 29.5' | 31.1' | 33.9' | 38.1'
2 | Roads, streets, and other areas subjected to truck traffic. |  | 20.2' | 20.8' | 21.3' | 22.8' | 25.3' | 29.3' | 20.4' | 20.9' | 21.5' | 23.1' | 25.9' | 30.1'
3 | Driveways, parking lots, and alleys |  | 20.2' | 20.8' | 21.3' | 22.8' | 25.3' | 29.3' | 20.4' | 20.9' | 21.5' | 23.1' | 25.9' | 30.1'
4 | Other land traversed by vehicles, such as cultivated, grazing, forest, orchard, etc. |  | 20.2' | 20.8' | 21.3' | 22.8' | 25.3' | 29.3' | 20.4' | 20.9' | 21.5' | 23.1' | 25.9' | 30.1'
5 | Spaces and ways subject to pedestrians or restricted traffic only. |  | 16.2' | 16.8' | 17.3' | 18.8' | 21.3' | 25.3' | 16.4' | 16.9' | 17.5' | 19.1' | 21.9' | 26.1'
Vertical Clearance - Conductors & cables on different supports Upper level
1 | Insulated com. conductors; messengers; surge protection wires; grounded guys; ungrounded guys exposed to 0-300 V; neutral conductors meeting Rule 230E1; supply cable needing Rule 230C1 |  | 3.7' | 4.3' | 4.8' | 6.3' | 8.8' | 12.8' | 3.9' | 4.4' | 5.0' | 6.6' | 9.4' | 13.6'
2 | Non insulated communication conductors; supply cables of 0-750 V meeting Rules 230C2 or 230 C3 |  | 7.7' | 8.3' | 8.8' | 10.3' | 12.8' | 16.8' | 7.9' | 8.4' | 9.0' | 10.6' | 13.4' | 17.6'
3 | Supply cable over 750V meeting Rules 230C2 or 230C3; open supply conductors, 0-750 V; ungrounded guys exposed to 300-750 V |  | 3.7' | 4.3' | 4.8' | 6.3' | 8.8' | 12.8' | 3.9' | 4.4' | 5.0' | 6.6' | 9.4' | 13.6'
4 | Over 750V to 22kV to ground (34.5 kV to phase) |  | 3.7' | 4.3' | 4.8' | 6.3' | 8.8' | 12.8' | 3.9' | 4.4' | 5.0' | 6.6' | 9.4' | 13.6'
5 | Over 22 kV to 27 kV to ground (46 kV to phase) |  | 3.9' | 4.4' | 4.9' | 6.5' | 9' | 12.9' | 4.1 | 4.6 | 5.2 | 6.8 | 9.6 | 13.8
6 | Over 28 kV to 42 kV to ground (69 kV to phase) |  | 4.4' | 4.9' | 5.4' | 7.0' | 9.5' | 13.4' | 4.6' | 5.1' | 5.7' | 7.3' | 10.1' | 14.3'
7 | Over 42 kV to 70 kV to ground (115 kV to phase) |  | 5.5' | 6.0' | 6.5' | 8.0' | 10.6' | 14.5' | 5.8' | 6.3' | 6.9' | 8.5' | 11.3' | 15.5'
8 | Over 70 kV to 84 kV to ground 138 kV to phase) |  | -- | 6.5' | 7.0' | 8.5' | 11.1' | 15.0' | -- | 6.9' | 7.4' | 9.1' | 11.8' | 16.1'
9 | Over 84 kV to 98 kV to ground (161 kV to phase) |  | -- | -- | 7.5' | 9.0' | 11.6' | 15.5' | -- | -- | 8.0' | 9.6' | 12.4' | 16.6'
10 | Over 98 kV to 140 kV to ground (230 kV to phase) |  | -- | -- | -- | 10.6' | 13.1' | 17' | -- | -- | -- | 11.3' | 14.0' | 18.3'
Vertical Clearance - Between conductors on the same supports
1 | Communication Conductors & Cables
| a | Located in Communication Space | 49" | 55" | 61" | 80" | 110" | 157" | 50" | 57" | 63" | 83" | 116" | 167"
| b | Located in Supply Space | 49" | 55" | 61" | 80" | 110" | 157" | 50" | 57" | 63" | 83" | 116" | 167"
2 | Open Supply Conductors & Cables
| a | Open conductors 0 to 750 V; Supply Cable meeting Rule230C1,2,or3; Neutral cond. Rule 230E1. | 42" | 48" | 54" | 72" | 103" | 150" | 42" | 49" | 56" | 75" | 109" | 160"
| b | 750V to 8.7 kV | 45" | 51" | 58" | 76" | 106" | 153" | 46" | 53" | 60" | 79" | 112" | 163"
| c | Over 8.7 kV to 22 kV to ground | 50" | 57" | 63" | 81" | 111" | 159" | 52" | 58" | 65" | 85" | 118" | 169"
| d | Over 22 kV to 27 kV to ground (46 kV to Phase) | 54" | 60" | 66" | 84" | 115" | 162" | 55" | 62" | 68" | 88" | 121" | 172"
| e | Over 27 kV to 42 kV to ground (69 kV to Phase) | 59" | 65" | 71" | 90" | 120" | 167" | 61" | 68" | 75" | 94" | 127" | 178"
| f | Over 42 kV to 70 kV to ground (115 kV to Phase) | 72" | 78" | 84" | 103" | 133" | 180" | 75" | 82" | 89" | 109" | 142" | 193"
| g | Over 70 kV to 84 kV to ground (138 kV to Phase) | -- | 84" | 91" | 109" | 139" | 186" | -- | 89" | 95" | 115" | 148" | 199"
| h | Over 84 kV to 98 kV to ground (161 kV to Phase) | -- | -- | 97" | 115" | 146" | 193" | -- | -- | 102" | 122" | 155" | 206"
| i | Over 98 kV to 140 kV to ground (230 kV to Phase) | -- | -- | -- | 133" | 164" | 211" | -- | -- | -- | 142" | 175" | 226"
| j | Over 140kV to 210kV to ground (345kV to Phase) | -- | -- | -- | -- | 194" | 241" | -- | -- | -- | -- | 208" | 259"
Clearances of Wires, Conductors and Cables, & Unguarded Rigid Live Parts - Adjacent but Not Attached to Buildings & Other Installations Except Bridges. No Wind
1 | Buildings
| Horizontal to Walls, projections and guarded windows, Unguarded windows, Balconies, and areas readily acceptable to people |  | 9.3' | 9.8' | 10.4' | 11.9' | 14.4' | 18.3' | 9.4' | 10.0' | 10.6' | 12.3' | 15.0' | 19.2'
| Vertical over or under roofs or projections not readily accessible to pedestrians |  | 14.3' | 14.8' | 15.4' | 16.9' | 19.4' | 23.3' | 14.4' | 15.0' | 15.6' | 17.3' | 20.0' | 24.2'
| Vertical to decks, balconies, roofs, etc., accessible to pedestrians, and over roofs not accessible to trucks |  | 15.3' | 15.8' | 16.4' | 17.9' | 20.4' | 24.3' | 15.4' | 16.0' | 16.6' | 18.3' | 21.0' | 25.2'
| Vertical over roofs accessible to trucks |  | 20.3' | 20.8' | 21.4' | 22.9' | 25.4' | 29.3' | 20.4' | 21.0' | 21.6' | 23.3' | 26.0' | 30.2'
2 | Signs, chimneys, billboards, radio and television antennas, tanks, and other installations not classified as buildings or bridges
| Horizontal |  | 9.3' | 9.8' | 10.4' | 11.9' | 14.4' | 18.3' | 9.4' | 10.0' | 10.6' | 12.3' | 15.0' | 19.2'
| Vertical over or under |  | 9.8' | 10.3' | 10.9' | 12.4' | 14.9' | 18.8' | 9.9' | 10.5' | 11.1' | 12.8' | 15.5' | 19.7'
3 | Other supporting structures, wires, conductors, or cables of one line passing near lighting support, traffic signal support, or a supporting structure of a second line, not attached
| Horizontal |  | 6.6' | 7.3' | 7.9' | 9.4' | 11.9' | 15.8' | 6.9' | 7.5' | 8.1' | 10.1' | 13.1' | 17.6'
| Vertical |  | 6.3' | 6.8' | 7.4' | 8.9' | 11.4' | 15.3' | 6.4' | 7.0' | 7.6' | 9.3' | 12.0' | 16.2'
4 | Vertical clearance to service ( 0 - 750 V), not readily accessible to pedestrians, that meets or terminates at a through-the-roof support & does not cross more than 6' of roof or is 4' or less from the roof edge shall be 18 inches. * See Distribution Standard DC-151 page 5.
Clearances of Wires, Conductors and Cables From Bridges
1 | Clearance over bridges.
| a. | Attached | 7.3' | 7.8' | 8.4' | 9.9' | 12.4' | 16.3' | 7.4' | 8.0' | 8.6' | 10.3' | 13.0' | 17.2'
| b. | Not attached | 14.3' | 14.8' | 15.4' | 16.9' | 19.4' | 23.3' | 14.4' | 15.0' | 15.6' | 17.3' | 20.0' | 24.2'
2 | Clearance beside, under or within bridge structure
| a. | Readily Accessible portion of bridge
|  | Attached | 7.3' | 7.8' | 8.4' | 9.9' | 12.4' | 16.3' | 7.4' | 8.0' | 8.6' | 10.3' | 13.0' | 17.2'
|  | Not attached | 9.3' | 9.8' | 10.4' | 11.9' | 14.4' | 18.3' | 9.4' | 10.0' | 10.6' | 12.3' | 15.0' | 19.2'
| b. | Ordinarily inaccessible portions of bridge
|  | Attached | 7.3' | 7.8' | 8.4' | 9.9' | 12.4' | 16.3' | 7.4' | 8.0' | 8.6' | 10.3' | 13.0' | 17.2'
|  | Not attached | 8.3' | 8.8' | 9.4' | 10.9' | 13.4' | 17.3' | 8.4' | 9.0' | 9.6' | 11.3' | 14.0' | 18.2'
Clearances of Wires Conductors and Cables Over Or Near Swimming Pools
1 | Clearance in any direction from the water, edge of pool, or base of diving platform. (Figure 8, "A") |  | 26.8' | 27.3' | 27.9' | 29.4' | 31.9' | 35.9' | 26.9' | 27.5' | 28.1' | 29.8' | 32.5' | 36.7'
2 | Clearance to diving platform, tower, etc. (Figure 8, "B") |  | 18.8' | 19.3' | 19.9' | 21.4' | 23.9' | 27.8' | 18.9' | 19.5' | 20.1' | 21.8' | 24.5' | 27.8'
| Exception to Rules 1 and 2 above: |  | Since 1984, Rules do not apply to insulated services over 10' horizontally from edge of pool, platforms, etc.
Other Clearances or Requirements.
1 | Minimum vertical clr between communication cable of different companies is 4" NESC Rule 235H.
2 | If a drip loop of conductors entering a luminaire or traffic signal bracket from the surface of structure is above communication cable, the lowest loop shall be 12" above communication cable or through bolt. It can be reduced to 3" if covered with non-metallic covering and extends into bracket 2".
3 | Minimum vertical clearance between power supply lines & communication cable mid-span carried on same supports is 30". NESC Rule 235C2b(1)(a)
4 | Horizontal clearance from structure to side walk curb - 6" (PacifiCorp recommended 18")
5 | Conductors 0 - 300 V attached to the side of a building and/or run alongside the building shall have clearances not less than 3" since 2002, and one inch clearance for 1981-2001.
6 | Horizontal clearance from structure to fire hydrant - 4'. Exception: allows 3' if 4' is not attainable. (3' pre 2002)
(Pre 2002: 3')
A. 12' (10.5' if building height does not permit) (Pre 1977: 10' and 8')
B. 3' min. around doors, fire escapes, etc. (not readily accessible to pedestrians)
3' min. below or beside unguarded openable windows. (Since 1984)
C. 12" between communication wire and service wire. (Since 1981)
D. 40" between communication wire and service wire
at service pole (12" if this is a meter pole).
E. 40" between communication wire and service wire at
support structure.
F. 16' over driveway (See Grandfather Matrix for exceptions).
G. 18” or 3' drip loop to roof, see Fig. 6 above.
See Matrix for exceptions. Pre 1977, no requirement.
H. 18.5' min. clearance above road
for primary 750V-22kV.
Fig. 1
Fig. 2
Fig. 3
Fig. 4
Fig. 5
Fig. 7
Fig. 8
A
B
C
D
E
F
G
A
H
Fig. 10
Fig. 5
3’ vertical clearance
18” vertical clearance
Fig. 6

## NESC Grandfather
NESC GRANDFATHERING
CITATION | NESC 2007 | NESC 2017 | NESC 2012 | NESC 2007 | NESC 2002 | NESC 1997 | NESC 1993 | NESC 1990 | NESC 1987 | NESC 1984 | NESC 1981 | NESC 1977 | NESC 1973 | 7th NBS Edition 1971 | 6th NBS Edition 1961
NESC Article 231A, Clearance between poles and fire hydrants:
1. Minimum clearance of 4 feet (exception: 3 feet if 4 feet cannot be attained) | ççç | ççç | ççç | ççç | Adopted
2. Minimum clearance of 3 feet (recommended clearance of 4 feet) | [5 empty] | ççç | ççç | ççç | ççç | ççç | ççç | ççç | ççç | ççç | Adopted
NESC Article 232, Table 232-1, Vertical Clearance limited to conductors at 0 to 150 V to ground for spaces and ways subject to pedestrians or restricted traffic only (Areas where riders on horses or other large animals, vehicle or other mobile units exceeding a height of 8 feet are prohibited by regulation or permanent terrain configurations, or are otherwise not normally encountered nor reasonably anticipated):
Minimum clearance of 12 feet for conductors 0 to 150 V to ground (including drip loops) with the following exceptions: |  | ççç | ççç | ççç | ççç | ççç | ççç | ççç | ççç | ççç | ççç | Adopted
A. Exception: 10 feet minimum clearance for conductors meeting Rule 230C1 or 230C3 or drip loops only meeting rule 230C3 |  | Adopted
B. Exception: Minimum clearance of 10 feet for conductors and drip loops 0 to 150 V to ground where building height does not allow 12 feet. |  |  | ççç | ççç | ççç | ççç | ççç | ççç | ççç | ççç | ççç | Adopted
C. Exception 1961 - 1976: Minimum clearance of 10 feet, but 8 feet where the form of the building will not permit 10 feet. | [12 empty] | ççç | ççç | Adopted
NESC Article 232, Table 232-1, Vertical Clearance of service conductors to driveway for conductors 0 to 150V to ground:
1. Minimum clearance of 16 feet, but 12 feet for conductors and 10 feet for drip loops 0 to 150 V to ground where vehicles exceeding 8 feet in height are not normally encountered or resonably expected. |  | Adopted
Minimum clearance of 16 feet, but 12 feet for conductors and 10 feet for drip loops 0 to 150 V to ground where building height does not allow. |  |  | ççç | ççç | ççç | ççç | ççç | Adopted
A. Exception: Where service conductors cross over or run along alleys, driveways or parking lots not subject to truck traffic (vehicles at least 8 feet in height), the clearance may be reduced to 15 feet. |  | ççç | ççç | ççç | ççç | ççç | ççç | Adopted
2. Minimum clearance of 10 feet for conductors and drip loops. | [8 empty] | ççç | ççç | ççç | ççç | ççç | ççç | Adopted
NESC Article 234-E, Clearance from swimming pools (Inground or Permanently Installed Above Ground)- (does not apply if enclosed by solid or screened permanent structure):
1. Service conductors 0-750V, clearance of 22.5 feet in any direction between conductors and pool, 14.5 feet to platforms, slides, etc. |  | ççç | ççç | ççç | ççç | ççç | ççç | Adopted
Exception since 1987: Does not apply to service supply conductors more than 10 feet horizontally from the edge of the pool, platforms, etc |  | ççç | ççç | ççç | ççç | ççç | ççç | ççç | Adopted
2. Open supply conductors 0-22kV, clearance of 25 feet in any direction between conductors and pool, 17 feet to platforms, slides, etc. |  | ççç | ççç | ççç | ççç | ççç | ççç | Adopted
3. Service conductors, clearance of 18 feet in any direction to pool, 14 feet to platforms, slides, etc. | [8 empty] | ççç | ççç | ççç | Adopted
4. Open supply conductors 0-15kV, clearance of 25 feet in any direction to pool, 16 feet to platforms, slides, etc. | [8 empty] | ççç | ççç | ççç | Adopted
NESC Article 234C3d, Clearance from service conductors (0-750V) to roof, deck or balcony:
1. Inaccessible deck, balcony or roof, minimum clearance of 3 feet to service conductors (1990-1992: 2 feet). (Prior to 1977, no clearance requirement for insulated conductors, however, insulation cannot be rubbing/abrading on building.) | ççç | ççç | ççç | ççç | ççç | ççç | ççç | ççç | ççç | ççç | ççç | Adopted
A. Exception, from 1977 through 1992: If a service drop terminates at a support mast located not more than 4 feet horizontally from the nearest edge of the roof, the service drop may be maintained at a minimum of 18 inches from any portion of the roof. | [7 empty] | ççç | ççç | ççç | ççç | Adopted
B. Exception, 1993 to present: If a service drop terminates at a support mast located not more than 4 feet horizontally from the nearest edge of the roof, the service drop may be maintained at a mimimum of 18 inches to the roof for 6 feet horizontally out from the mast, and then must be maintained at a minimum of 3 feet clearance above the roof thereafter. (2017 NESC page 126, Figure 234-2.) | ççç | ççç | ççç | ççç | ççç | ççç | Adopted
2. Accessible deck, balcony or roof, minimum clearance of 10 feet to service drop conductors. |  | ççç | ççç | Adopted
3. Accessible deck, balcony or roof, minimum clearance of 8 feet to service drop conductors. |  |  |  |  | ççç | ççç | ççç | ççç | ççç | ççç | ççç | Adopted
NESC Article 234C 3d2, Clearance to window for service drops (240/120V meeting rule 230C3):
1. Service drop is above any window (openable or non-openable) or is below a non-openable window - there is no clearance requirement. |  | ççç | ççç | ççç | ççç | ççç | ççç | ççç | ççç | Adopted
NESC Article 235C1 Exception 3, Clearance between service drop (0-750V) and communication drop:
1. The minimum clearance is 12 inches on service mast since 1981. No requirement prior to 1981. | ççç | ççç | ççç | ççç | ççç | ççç | ççç | ççç | ççç | ççç | Adopted
NESC Article 215-C-2, Grounding or Insulating Guys within 8 feet of the earth:
1. Guys that are attached to a pole with energized conductors of any voltage must be effectively grounded as specified in Rule 092C2 or have an insulator installed that that limits the likelihood of the anchor guy becoming energized withing 8 feet of the ground. |  | ççç | ççç | Adopted
2. Guys that are attached to a pole with conductors over 300V must have a guy insulator(s) or be effectively grounded to the neutral or pole ground. |  |  |  |  | ççç | ççç | ççç | ççç | ççç | ççç | ççç | Adopted
3. Guys that are attached to a pole with conductors of 300V to 15kV must have a guy insulator(s) or be effectively grounded to the neutral or pole ground. | [12 empty] | ççç | ççç | Adopted
HOW TO USE THIS MATRIX TO IDENTIFY GRANDFATHERED INSTALLATIONS: |  |  |  |  | HOW TO TREAT NATIONAL ELECTRIC CODE (NEC) DEFECTS:
Identify the applicable code and the adopted date on the matrix above. |  |  |  |  | PacifiCorp's facilities are required to be inspected and maintained compliant with the NESC. Customer facilities are required to be compliant with the NEC, which is administered by the local electrical inspector. If you identify a defect of the NEC that is an immediate danger to the public, notify the local electrical inspector.
Use year of pole installation, house vintage, or other hints to determine the approximate year the installation originated.
If the installation appears to have previously met a prior existing code, enter it as a Priority "G" in the handheld.
OLDEST APPLICABLE NESC EDITION FOR OVERHEAD AND UNDERGROUND LINES: |  |  |  |  | NEC defects should only be input into FPI as notes on the "IF" screen to describe the situation.
Due to verbage in prior editions of the NESC, the oldest version that can be grandfathered is the 6th Edition issued in 1961.
Any equipment installed prior to 1961 must at the minimum meet the rules detailed in the 1961 edition, prior editions cannot be grandfathered. |  |  |  |  | An example of a NEC defect is a service mast of greater than 4' that is not guyed (NEC Article 230.28).
Note on A25: Clifton, Joseph: Need to add 5 foot horizontal

## GO95 Grandfather
CALIFORNIA GO 95 - GRANDFATHERING
CITATION | GO95 2007 | GO95 2009 | GO95 2006 | GO95 2002 | GO95 1997 | GO95 1992 | GO95 1990 | GO95 1988 | GO95 1984 | GO95 1980 | GO95 1962 | GO95 1942
GO95 Rule 51.6-A: High Voltage Marking Signs on Poles where conductors are not on Crossarms:
1. Poles which support conductors of more than 750 volts shall be marked with high voltage signs. | ççç | ççç | ççç | ççç | ççç | ççç | Adopted
2. Poles supporting conductors of 750 volts to 20,000 volts shall be marked with high voltage signs. | [7 empty] | ççç | ççç | ççç | ççç | ççç | Adopted
GO95 Table 1, Case 4, Column D: For open supply conductors 0-750V, clearance above ground along thoroughfares in rural districts or across other areas capable of being traversed by vehicles and agricultural equipment:
1. Minimum clearance 19 feet. |  | ççç | ççç | ççç | ççç | Adopted
2. Minimum clearance 16 feet. | [6 empty] | ççç | ççç | ççç | ççç | ççç | ççç | Adopted
GO95 Rule 54.4-A(2)a, Table 1, Case 3, Column E: For conductors 750V to 22,500V, clearance above ground crossing or overhanging traversable portions of roads or driveways:
1. Minimum clearance 25 feet. |  | ççç | ççç | ççç | ççç | Adopted
2. Minimum clearance of 22 feet. | [6 empty] | ççç | ççç | ççç | ççç | ççç | ççç | Adopted
GO95 Rule 54.4-A(2)b, Table 1, Case 4, Column E: Clearance above ground for lines 750V to 22,500V across areas capable of being traversed by agricultural equipment and along roads where no part of the line overhangs any traversable portion of a roadway:
1. Minimum clearance 25 feet. |  | ççç | ççç | ççç | ççç | Adopted
2. Minimum clearance of 18 feet. | [6 empty] | ççç | ççç | ççç | ççç | ççç | ççç | Adopted
GO95 Rule 54.8-D1, Table 1, Case 10, Column D: For service drops 0 - 750V, clearance from non-climbable street lighting poles and traffic signal poles or standards:
1. Service drops passing unattached shall clear non-climbable street lighting and traffic signal poles, or standards, including mastarms, brackets and lighting fixtures, a radial distance of 12 inches, except when the conductors are mechanically protected from abrasion 15 inches each direction from the cable centerline. (Prior to 1980 the code was silent on this.) |  | ççç | ççç | ççç | ççç | ççç | ççç | ççç | ççç | Adopted
HOW TO USE THIS MATRIX TO IDENTIFY GRANDFATHERED INSTALLATIONS: |  |  |  | HOW TO TREAT NATIONAL ELECTRIC CODE (NEC) DEFECTS:
Identify the applicable code and the adopted date on the matrix above. |  |  |  | PacifiCorp's facilities are required to be inspected and maintained compliant with the GO95. Customer facilities are required to be compliant with the NEC, which is administered by the local electrical inspector. If you identify a defect of the NEC that is an immediate danger to the public, notify the local electrical inspector.
Use year of pole installation, house vintage, or other hints to determine the approximate year the installation originated.
If the installation appears to have previously met a prior existing code, enter it as a Priority "G" in the handheld.
NEC defects should only be input into FPI as notes on the "IF" screen to describe the situation.

## NESC FAQ
No. | Group | NESC Issue | Resolution | Ref | Co. Code
2 | CATV/TELCO/FIBER | What condition should be used for J hooks? | J hooks owned by other companies should use Incomplete Changeover/Transfer |  |  | Review
3 | Clearance | Can a pole step or stand off bracket be installed on a pole in the first 8' if there is 8' clearance from the first step to the next device? | An 8-foot space is required to prevent someone from climbing a pole. If there is a standoff bracket within the first 8 feet, then there must be a separation of 8 feet to the next step. | 217A-2 | COOTHER | A step is different than a standoff bracket. 2172b states that steps permanently installed on supporting structures shall not be less than 8' from the ground or an accessible surface
4 | Clearance | What is the clearance for services over hot tubs in yards or on decks? | 11 foot clearance to service wires. See both paragraphs in "Note" in 234-E-1. | 234-E-1 Note Table 234-1
5 | Clearance | Does the NESC require 3 feet clearance from a window that cannot be opened? | A 3ft. clearance is required from drip loops and conductors in any direction from doors, porches, fire escapes or similar locations. Windows that have a sliding and fixed pane, the 3 ft requirement applies to the sliding portion of the window. If a window is not designed to open there is no clearance requirement. | 234C3d(2)
6 | Clearance | Does the NESC require 3 feet clearance from a window for buildings built prior to 1984? | 3 ft. minimum clearance is required around unguarded windows, door, and fire escapes. There was no clearance requirement for windows prior to 1984, so installations before 1984 are grandfathered. | 234C3d2
7 | Clearance | For services less than 300 Volts over residential buildings, is the clearance over the roof grandfathered at some time? | The service mast must be located not more than 4' from the nearest edge of the roof, measured horizontally. If the mast is installed more than 4' from the nearest edge of the roof or the service crosses over more than 6' of the roof, after a horizontal distance of 6' a vertical clearance of 3' min is required over the remainder of the roof. The vertical clearance within the 6' radius of the service mast is 18". From 1977 until 1993 the clearance was 18" within 4' of the edge of the roof and no mention was made of the 6' radius. Before 1977 there were no clearance requirements over the roof for insulated services up to 750V. | Rule 234C3d exception 2
8 | Clearance | What is the required communication clearance from a span guy that has secondary attached to it and doesn't have the proper "J" ball or insulator installation? | Proper installation is as follows: NESC states that for 300V or less, if there is 1 J-ball it should be on the power end of a span guy and if there are 2 J-balls there should be one on each end of the span guy. The required clearance is 40" at the pole and 30" at midspan. | table 235-5 section 1a for clearance at the pole and 235C2b1a for the midspan
9 | Clearance | What is the required communication clearance from a span guy that has secondary attached to it and a "J" ball or insulator installed in both ends? | The required clearance is 40" at the pole and 30" midspan, the same as the clearances for an attachment. | table 235-5 section 1a for clearance at the pole and 235C2b1a for the midspan
10 | Clearance | When midspan height conditions are captured, how are these tied to a specific facility point? | The condition can be tied to the pole on either side, however the inspector should indicate on the IF screen that the condition is between FP#XX and FP#YY.
11 | Clearance | For services less than 150 volts to ground over driveways, is the clearance over the driveway grandfathered at some time? | For installations from 1990 through 2006, the clearance is still 16', but can be as low as 12' (10' for the drip loop) if the building height does not allow higher. From 1941 through 1989, the clearance is 10 feet. | Rule 232, Table 232-1
12 | Clearance | For conductors over swimming pools, is the clearance grandfathered at some time? | From 1977 through 1989, insulated service conductors 0 to 750 volts have a clearance of 18 feet in any direction from the pool, and 14 feet to platforms, water slides, etc., and open supply conductors 0-15kV have a clearance of 25 feet in any direction between conductors and the pool, and 16 feet to platforms, water slides, etc. The is no reference to swimming pools prior to 1977. | Rule 234-E
13 | Clearance | For services 0 - 750 volts to ground over decks, balconies and roofs accessible to pedestrians, is the clearance grandfathered at some time? | For installations from 1977 through 2006, the clearance is 8 feet. | Rule 234-C-3-d
14 | Climbing space | Are bolts protruding more than 4" a condition? | Thru-bolts are condition only if 4'' beyond nut and in the only available climbing space | Rule 236E | COCATV COFIBER COTELCO
15 | Climbing space | Are messenger bonds considered a condition in the climbing space if all other wires/lines are on the opposite side of pole? | Yes, all horizontal runs of wire in the climbing space are considered to be non-conforming. |  | COOTHER | Review. Look at 236G - "Longitudinal runs on rackes, or cables on messengers, are not considerted as obstucting climbing space if the location, size, and quantity of the cables permit qualified workers to climb past them".
16 | DTLTRT | Should a DTLTRT be performed on Qwest poles? | There are agreements in some areas that allow for PTT and billing the pole owner. This is area specific. If the pole is not to be treated, perform a detail inspection.
17 | Fence | Are fences attached to poles a condition? | A fence should be reported as a condition only if there is not adequate spacing to prevent being used as a step to climb the pole. | 217-2 | COOTHER, COCATV, COTELCO
18 | FPI | If a condition exists in FPI and a second inspection shows the same condition, is it necessary to add the condition a second time? | The condition only needs to be input into FPI once. If further explanation is needed note this in the IF screen, and if the condition has worsened it can be changed to higher priority. |  | IF
19 | FPI | What should be done with facility points that are unable to be inspected due to access and customer issues? | If an inspector is not able to inspect a transmission facility because it is inaccessible because there's no road or impassable, the inspector should input CANTINSP into FPI for the facility point. If it's on a distribtuion facility and because of locked gate or no access, the inspector should input CUSTRESP CANTINSP into FPI and create an IF code to record the address and note the issue. District should identify these points and make arrangements for permanent access. |  | CANTINSP or CUSTRESP
20 | Ground | Are all ground rods out of ground to be reported, even communication ground rods? | All Ground rods out of ground must be reported, including communication company ground rods. Ground rods above ground are an NESC condittion. NESC requires 8' of rod in the soil. Note on IF screen if ground rod is from a JU licensee. | 94B2-C | BOGRD
21 | Ground | Is there a stores number for ground clamps used to ground steel conduit? Is a copper band or plumbers tape an acceptable means of grounding? | There is a standard clamp for grounding these conduits. GC 851. The SI # 5310611
22 | Ground | Is there a specific position to ground the conduits? | All grounding should be installed per company standard, 2-3" below grade.
23 | Ground | When locates are performed on poles often times the straps are popped out by the locators. Can this be corrected? | If the ground "strap" is disconnected it needs to re-connected by a qualified electrical worker.
24 | Ground | Does a customer ground rod above ground level need to be reported if they are on our pole? | All ground rods above ground level are NESC conditions. Report high customer ground rod on company facilites as BOGRD and note in IF screen that it is customer owned. |  | BOGRD
25 | Ground | Is a riser that is grounded below the surface (and therefore cannot be seen to be verified) a condition? | No, company standards call for risers to be grounded below the surface
26 | Guy or Anchor | How should down guys and anchors attached to a PacifiCorp facility on a licensee-owned anchor be inspected? | Guys installed since 1977 that are within 8' of the earth and are attached to a pole with conductors above 300V (and also below 300V since 2007) must have a guy insulator or be effectively grounded to the neutral/pole ground. Input into FPI as COTELCO or COCATV if there are NESC conditions on the JU guy or anchor. | 215-C-2 |  | Review with Corey and Tori
27 | Guy or Anchor | How should cable TV and TELCO guys attached to PacifiCorp anchors using auxiliary or sister eyes be inspected? | Sister eyes are not acceptable and are a condition COTELCO or COCATV. JU Department will coordinate with licensee to correct the problem by having licensee install their own anchor. | EU101 | COTELCO COCATV
28 | Guy or Anchor | How are foreign guys to be addressed? | Foreign guys have been allowed on PacifiCorp installations in the past. In all cases the anchor must be adequate to support the load. If there are no visible problems with the anchor, it is not a condition. If down guy is slack and anchor is "pulling," report as a condition COTELCO or COCATV. |  | COTELCO COCATV
29 | Guy or Anchor | How should cable TV and TELCO Anchors attached to PacifiCorp anchors or double head anchors that are visibly bonded be inspected? | This does not meet PacifiCorp standards and is a correctable condition. Anchor must be adequate to support the load. Bonding of down guy is issue. JU department will coordinate the repair with the licensee responsible. |  | COCATV COTELCO
30 | Guy or Anchor | Is Osmose to install guy markers on PacifiCorp anchors and licensee anchors? | Yes, install guy markers on all down guys, except marker not required if guy that is not in pedestrian or traffic area is engulfed in dense vegetation or is otherwise inaccessible. |  | BOGUY
31 | Guy or Anchor | Should tails on TELCO and CATV anchors be clipped? | Clip tails on all guy wires that extend out of grip. |  | COTELCO COCATV
32 | Guy or Anchor | Are slack guys to be reported? | Slack guys are to be reported per Policy 009, Section 3.3., only if pole is not in proper vertical position. |  | BOGUY
33 | Guy or Anchor | Should guy markers be installed on all down guys attached to a single anchor? | Yes. Down guys are to have a guy marker installed per company standard. Marker not required if guy that is not in pedestrian or traffic area is engulfed in dense vegetation or is otherwise inaccessible.
34 | Guy or Anchor | Do we install guy markers on all down guys attached to multiple anchors in the same plane? | Yes. Down guys are to have a guy marker installed per company standard. Marker not required if guy that is not in pedestrian or traffic area is engulfed in dense vegetation or is otherwise inaccessible.
35 | Guy or Anchor | What is the position of a guy insulator if there is no communications attached to the pole? | If down guy breaks, insulator must be at least 8 ft above ground. On transmission with distribution underbuild the insulator is to be positioned to land so guy cannot energize distribution. | EG 051 |  | Review
36 | Guy or Anchor | Should secondary down guy insulators below communication level be captured as a condition? | This is not a condition and should not be reported in FPI
37 | Guy or Anchor | Should down guys that cross over each other be captured? | This is not an NESC condition and should not be reported in FPI.
38 | Guy or Anchor | Are anchors extending out of the ground 12" non-conforming? | This is not an NESC issue and should not be reported.
39 | Joint Use | Are TELCO Pedestals within 3' of a pole a condition? | Because these are not NESC conditions, these should not be entered as such, but verify 8 ft. separation from the top of the pedestal to prevent climbing of the pole. Note the location of the pedestal in the IF screen. | 217-2 | IF
40 | Joint Use | Can the pole be removed on JU non transfers? | Do not remove a pole on a JU non transfer by cutting the top and leaving it attached to the TELCO because this is a hazard. | 214A-5 | TELCO
41 | Joint Use | What clearances should be reported for conductors passing by a facility point horizontally? | TELCO and CATV 3' for phase conductor and 5' for neutral conductor, measured horizontally. | 234B
42 | Joint Use | TELCO conductors crossing over roadways that run pole to pole must be 15'6" over the road. Does this apply to TELCO service drops? | Yes, this does apply to TELCO service drops. |  | CLRTELCO
43 | Pole | Do idle facilities need to be removed? | Idle facilities (pole with no equipment or wire) must be removed. A pole with a de-energized transformer or a de-energized tap line, etc, is not a condition and does not have to be removed but must be maintained. | 214B-2 214B-3 | COOTHER
44 | Pole | How should woodpecker damage be reported in FPI? | Input as BIRDDMG. Exception: if damage is severe mark as BOPOLE. |  | BIRDDMG
45 | Pole | Are dead end poles with no down guys reported as a condition? | Report if pole is leaning or needs additional support.
46 | Pole | How are old pole butts to be treated? | If the pole butt is in a rural area that is publicly inaccessible it is not a condition if it is cut off at or below ground level.
47 | Pole | How should leaning poles be addressed? | If leaning into roadway and an immediate hazard to vehicular traffic, A. If leaning severely in an urban area, A. If leaning moderately in urban area, B. Anchor pulled is BOANC. Pole deteriorated is BOPOLE. Pole cracked from stress is BOPOLE.
48 | Pole | On structure with a push brace what is treated? | On structure with a push brace the pole and the push brace are both treated. The facility point is only associated with pole. Make a notation on the IF screen that the push brace has been treated.
49 | Pole | Are customer meter bases on PacifiCorp poles allowed and if so, are they grandfathered? | These are not NESC conditions and should not be reported.
50 | Pole | What condition should be used for a leaning pole? | BOPOLE is used when the pole is leaning due to decay. BOANC is used when the anchor is pulled. BOGUY is used when a good pole needs a guy. COOTHER is used when the pole is leaning due to any other reason.
51 | Riser | Do all metallic communication risers on a pole have to be grounded? | Communications risers do not have to be grounded unless exposed to contact with open conductors of greater than 300V. | 314.B
52 | Riser | On risers, how are broken conduits and split/separated joints to be addressed? | For both primary and secondary risers, with access, below 8 feet is an A condition, above 8 feet is a B condition.
53 | Satellite dish | What is the required clearance between a satellite dish on a roof top and an electrical service riser? | Although satellite dishes are not specifically mentioned, the NESC allows 12 inches at the served structure. | 235C-1 Exception 3 | CUSTRESP
54 | Service | Can communications attach to a mast below a weatherhead? | Yes. Inspectors should verify that the communications is at least 12" below power conductor for installations since 1981. If not, this is an NESC condition and should be input into FPI. No requirements prior to 1981. | 235C-1 | CLRTELCO
55 | Service | Mast over 4' must be guyed. Are these a condition if they are not guyed? | Mast guying is an NEC requirement, and was added to the code in 1975. All masts must be adequately supported or guyed to safely support the service cable. There is no height or guying requirement in the NESC. This should be reported as a condition in FPI only if the mast is being pulled or leaning. |  | BOSVCENT
56 | Service | On a customer-owned meter pole do communication facilities or joint use attachments have to have 40" clearance? | All meter pole or service poles are considered the point of attachment so clearance requirements are the same as the point of attachment. The communication must be at least 12 in. below the power conductor. | 235C-1 | CLRTELCO CLRCATV
57 | Sign | Are signs attached to poles a condition? | Traffic signs can be grandfathered. If signs are temporary such as garage sale or lost dog signs, please remove. |  | RWENRCH
58 | Street/Area Light | What are the correct street light clearances? | If a drip loop of conductors entering a luminaire or traffic signal bracket from the surface of a structure is above the communication cable, the lowest loop shall be 12" above communication cable or through bolt. It can be reduced to 3" if covered with non-metallic conduit. The mast clearance is 20" if not grounded. This may be reduced to 4" if effectively grounded. | 238C 238D | CLEAR
59 | Street/Area Light | On customer-owned lights on a meter pole what is the clearance from the light to weatherhead? | Company must follow NESC. If installed on load side of meter installation must meet NEC. Nothing specific found on this type of installation in NEC. NESC guidelines for clearances may be applied. |  | CLEAR
60 | Street/Area Light | On street lights are mounting holes with missing lag bolts a condition? | All hardware must be securely mounted to the structure, regardless of the number of bolts. If not securely mounted report as COOTHER. |  | COOTHER
61 | Trees | Are trees that deflect a service a condition? | Service wire deflected or abraded by vegetation is a condition in Oregon only. Not a condition if guarded at point of deflection |  | CLEARSVC
62 | Trees | If trees are pulling or pushing hard on communication lines in a midspan this could create pole integrity issues on either poles on each side; should these be captured if it can be determined that there is a possible integrity issue? | Report as COTELCO or COCATV. This should only be reported if condition is severe. |  | COTELCO COCATV

## GO95 FAQs
No. | Group | GO 95 Issue | Resolution | Ref | Comments and Notes
2 | ABANDONED EQUIPMENT | How should abandoned equipment be addressed? | An abandoned item of equipment such as a transformer, switchgear unit, etc, is not nonconforming. | Rule 31.6 | Input as a C condition
3 | ABANDONED LINES | How should abandoned lines be addressed? | GO95 states that lines permanently abandoned shall be removed by their owners. "Permanently abandoned" is defined as those lines that are determined by their owner to have no foreseeable future use. | Rule 31.6 | Applies to lines or sections of lines that do not go to any buildings, structures, facilities or developments that may need electrical service in the future. Enter as a C condition for further review by District.
4 | ACCESS | What should be done with facility points that cannot be inspected due to access and customer issues? | If an inspector is not able to inspect a facility because it is inaccessible because there's no road or impassable, the inspector should input CANTINSP into FPI for the facility point. If it's because of locked gate or no access, the inspector should input CUSTRESP into FPI for the facility point and record the address. District should identify these points and make arrangements for inspection. |  | Enter as CANTINSP or CUSTRESP
5 | CLEARANCE | Do secondary poles with communication attached need to have a guard arm installed for clearances? | No, 48 inches is acceptable unless it's open wire secondary in which case a guard would need to be installed or maintain 60 inches clearance. | Rule 54.8.G2C Rule 38, Table 2, Column D Rule 84.8B2b Rule 87.4C3 Paragraph 3 & Exception Rule 92.1-B | Standard EU 241
6 | CLEARANCE | Are measurements at the pole for clearances between supply and communications to be taken from the point of attachment or should they be from wire to wire / hardware to wire? | Table 1 clearances apply for the entire length of all lines involved, including hardware. Table 2 applies to conductor crossings, midspan, and supports. Anything separated more than 5 inches at the pole will be measured centerline of conductor to centerline of conductor (lowest part of supply to highest part of communications). | Rule 37, Table 1 Rule 38, Table 2
7 | CLEARANCE | What is the required clearance from the transformer case to the secondary or neutral? | 10 inch clearance to secondary, neutral or service is requred. | Rule 54.4G Rule 58.1E Table 58-2
8 | CLEARANCE | What is the required clearance for communication services above residential driveways? | 12 feet is required. If the building cannot provide this clearance and the service is insulated, the clearance shall be as great as possible, but in no case less than 10 feet. | Rule 54.8B2(b) & Exception Training Guide page 15
9 | CLEARANCE | What is the required clearance for span wires and overhead guys above ground not accessible to vehicles? | 8 feet is required. | Rule 86.4A1© Table 1 case 5A
10 | CLEARANCE | What is the required clearance for communication conductors and supply conductors of 750V or less crossing over communication not on the same supporting structure? | 48 inches minimum is required. | Rule 54.8C1(a) Rule 54.8C4 Table 2 case 9C
11 | CLEARANCE | What is the required separation between supply service drops and communication service drops to a residence? | 12 inches at attachment to building and 12 inches for first 15 feet from building. More than 15 feet from building requires 24 inch clearance. | Rule 54.8C4 Rule 84.8D4
12 | CLEARANCE | What is the required clearance between conductors not on the same support of 750V up to 7500V? | 48 inches minimum is required. | Rule 38 Table 2, Case E5
13 | CLEARANCE | At a pole housing primary conductors, what is the required clearance at the pole between supply conductors of 0-750V and communication mounted on same pole with a guard arm? | For communications attached to the surface of the pole, the clearance is 72 inches, and can be reduced to 48 inches with a guard arm. | Rule 38 Table 2, case 8D Rule 84.8B2c Rule 87.4C3 Paragraph 3 Exception Rule 92.1-B
14 | CLEARANCE | At a pole housing primary conductors, what is the required clearance at the pole between supply conductors of 0-750V and communication mounted on same pole without a guard arm? | If communications is mounted on a crossarm, and is mounted more than 15 inches from the centerline of pole, then the clearance is 48 inches. But if less than 15 inches or if attached to the surface of pole, then 72 inches must be maintained. | Rule 38 Table 2, case 8D Rule 84.8B2b Rule 87.4C3 Paragraph 3 Rule 92.1-B
15 | CLEARANCE | What is the required clearance for supply and communication service drops over a street, alley or public thoroughfare? | 18 feet clearance from centerline until at 12 feet horizontally from curb edge, then gradually reduced to 16 feet at curb edge. | Rule 84.8C(1) Exception
16 | CLEARANCE | What is the clearance from supply conductors 0-750V crossing supply conductors 0-750V on separate supports on the same pole? | 24 inches minimum is required. | Table 2 case 9D
17 | CLEARANCE | What are the clearances for 0-750V supply service drops in midspan from communication conductors? | 24 inches minimum is required, but can be 12 inches within 15 feet of the house. | Table 2 case 3D note (i) Rule 54.8C4
17b | CLEARANCE | What are the clearances for 0-750V supply conductors in pole to pole midspan from communication conductors? | 48 inches minimum is required. May be 36 inches midspan if supply is abrasion-resistant and neutral-supported. | Rule 57 and 54.10 Table 2, note pp
18 | CLEARANCE | What is the required hardware clearance on wood poles? | Shall have a clearance of not less than 1.5 inches | Rule 54.6H
19 | CLEARANCE | What is the required clearance for the lowest pole step above the ground line? | Lowest step shall not be less than 7.5 feet above ground line. | Rule 91.3B
20 | CLEARANCE | For 0 - 750 volt services, what is the minimum horizontal clearance from buildings, bridges or other structures that the service is not attached to? | 3 feet is required. | Table 1 case 7B Table 10
21 | CLEARANCE | What is the required window clearance? | 3 feet for service drops up to 750V; 6 feet for 750V to 300kV; 15 feet for 300kv to 550kV. | Rule 54.4-H-1 Table 1 case 7
22 | CLEARANCE | Can a communication service drop lay on the roof of the building being served? | Yes, communication service drops are not required to clear the roof of the building served by any specified vertical distance. | Rule 84.8-C4
23 | CLEARANCE | For a supply service drop, what is the required vertical distance from a building that the service drop is not attached to? | The vertical clearance above buildings on premises other than the one being served shall not be less than 8 feet, except that a reduction to not less than 2 feet is permitted under certain conditions outlined in Rule 84.8-C4a&b. | Rule 84.8-C4
24 | CLEARANCE | For communications, what is the required vertical distance from a building that the comm drop is not attached to? | The vertical comm clearance above buildings on premises other than the one being served shall not be less than 8 feet, except that a reduction to not less than 2 feet is permitted under certain conditions outlined in Rule 84.8-C4a&b. | Rule 84.8-C4
25 | CLEARANCE | What is the horizontal clearance for communications from buildings and other structures not attached? | Communication cables are not required to be any specified distance from the sides of buildings, bridges and other structures, but they shall be installed so that they do not interfere with the free use of fire escapes, windows, doors and other points at which entrance or exit might be reasonably expected. | Rule 84.4E Table 1 Case 7 Subnote "u"
26 | CLEARANCE | Can a communication conductor or messenger be attached to the top or side of a guard arm and still maintain 48 inches? | No. If on top, the communication conductor/cable/ messenger needs to have 72 inches of clearance. To reduce to 48 inches, communications shall be supported on or attached to bottom or side surface of any guard arm except as permitted for service drops and their vertical and lateral runs. | Rule 84.6C Rule 84.8B2c Rule 87.7-B | If communications is 2" below the top of guard arm or attached to bottom side, it may be reduced to 48" regardless of how far it is off the centerline of pole .
27 | CLEARANCE | For communication cables and supply service drops, what is the vertical clearance required above signs upon which people cannot walk? | 2 feet | Rule 39 Table 2-A (page III-32)
28 | CLEARANCE | For communication cables and supply service drops, what is the horizontal clearance from signs which are illuminated? | 3 feet, but may be reduced to 6 inches provided illuminated sign is grounded. | Rule 39 Table 2-A (page III-32)
29 | CLEARANCE | When midspan height conditions are captured, how are these tied to a specific facility point? | The conditon can be tied to the pole on either side, however the inspector should also indicate the other pole's fp number.
30 | CLIMBING SPACE | Are bolts protruding more than 4 inches a conditon? | Report all bolts protruding more than 4 inches out from the nut as a condition if they are below a transformer, in the climbing space, or 30 inches or more below the primary. |  | Enter as COOTHER (COTELCO,COCATV, COFIBER)
31 | COMM CLEARANCE | What is the required clearance for communication services above commercial driveways? | 16 feet is required. | Rule 84.8C2(a)
32 | DEFINITIONS | What is the difference between weather-resistant, covered and insulated services? | Weather resistant: Equivalent to standard double braid weatherproofing. Covered: Protected, sheltered. Insulated: Having insulating material the dielectric strength of which is sufficient to withstand the maximum difference of potential at normal operating voltages. | 49.4C7a 20.8-G
33 | EQUIP CLEARANCE | What is the required clearance for equipment cases above ground level? | Equipment cases above ground accessible to vehicles require 17 feet clearance; not accessible to vehicles there is no clearance requirement but shall be effectively grounded if less than 8 feet above ground. | Rule 58.1B(2)
34 | GROUND | Can ground wires be exposed if molding is cracked or has minor separation? | Ground molding may have minor separation, warping, or cracks, provided the ground wire is not exposed. | Rule 54.6-B
35 | GROUND RODS | Do communication ground rods need to be a minimum distance from the pole? | The driven ground rod shall be located 24 inches or more from the surface of the pole. | Rule 92.4C2(e)
36 | GROUND RODS | Are supply ground rods required to be below ground level? | The top of the ground rod can be above ground level. However, ground rods shall be driven into the ground so that one end of the ground rod is at a minimum depth of 8 feet below the surface of the ground. | Rule 59.4-A-2-c
37 | GROUND WIRE | Do ground wires attached to the bottom or face of a crossarm need to be covered? | All ground wires need to be covered in their entirety including the bottom and face of a crossarm. | 54.6B
38 | GROUND WIRE | Are ground wires attached under the crossarm required to be covered by wood or high impact ground molding? | Both are acceptable, as is red hose, but only for under the crossarm. | Rule 22.2D
39 | GROUNDING | In a cluster mount arrangement, do transformer cases and/or racks need to be grounded? | There is no requirement for any rack to be grounded. On metal poles and metal structures, transformer cases must be bonded to the structure which must be grounded. | Rule 58.2A3 (Confirmed via CPUC correspondence of May 21, 2009)
40 | GUY CLEARANCE | What is the required clearance for supply and communication guys above industrial or commercial entrances? | 16 feet is required. | Rule 86.4A1 Exception (a)
41 | GUY CLEARANCE | What is the required clearance for supply and communication guys above private residential entrances? | 14 feet is required. | Rule 86.4A1 Exception (b)
42 | GUY OR ANCHOR | Is Osmose to install guy markers on PacifiCorp anchors and licensee anchors? | Yes, per agreement Osmose will install guy markers on all guys. |  | Enter as condition and correct the condition in FPI.
43 | GUY OR ANCHOR | Should guy tails on Telco, Fiber and CATV anchors be clipped? | Clip tails on all guy wires that extend out of strandvise. |  | Enter as COTELCO OR COCATV
44 | GUY OR ANCHOR | Are slack guys to be reported? | Slack guys are to be reported as BOGUY for futher evaluation. | Rule 56.2 EG 091 | Enter as GO95 GUY
45 | GUYS | If there is no communication on pole, can there be a barrel of proximity? | Yes | Rule 56.6A Figure 56-3
46 | GUYS | Do communication down guys need to have an insulator installed or be bonded if attached to their through bolt? | They must be insulated and not grounded if they fall within Rule 56.6A barrel of proximity. | Rule 56.6A
47 | GUYS | Where should an insulator be installed in an overhead guy that is required to be sectionalized? | The insulator shall be installed not less than 6 feet and not more than 9 feet from the point of attachment to the pole, and shall be 8 feet minimum vertically above the ground. | Rule 21.3-D Figure 56-4b, 56-5, 56-6 Rule 56.7A Rule 86.7 | For ungrounded OH guys that are less than 17 feet in length, a single insulator can be installed at about midpoint between the two supports. 56-7A
48 | GUYS | Where should the insulator be installed in a primary down guy that is required to be sectionalized? | 8 feet or more above the ground, and 8 feet or more below the level of the lowest supply conductor; or 6 feet or more from the surface of the pole and 1 foot or more below the level of the lowest supply conductor. | Rule 56.7B(1)(2) Figure 56-8
51 | HIGH VOLTAGE SIGNS | What are the requirements for "High Voltage" warning signs on poles not carrying equipment? | Poles supporting line conductors more than 750 volts shall be marked with "High Voltage" signs. Signs shall be located not more than 40 inches below the lowest line conductor, or shall be located on the face and back of the crossarm. | Rule 51.6A Figure 51-1
52 | HIGH VOLTAGE SIGNS | What are the requirements for "High Voltage" warning signs on poles that are carrying equipment such as energized transformers? | Same as above, but with the option to instead install a sign that approximately encircles the pole, and that is no more than six inches below the equipment and is above all communication line conductors and supply line conductors of 0-750 volts. | Rule 51.6A(Option 2)
53 | HIGH VOLTAGE SIGNS | What are the requirements for "High Voltage" warning signs on poles that do not support line conductors of more than 750 volts, but that do support risers of more than 750 volts? | The top of the sign must be located below the top of the riser but no more than 40 inches below the top of the riser. | Rule 51.6A | For example, this may occur in agricultural areas where an UG primary feed goes up a riser to an OH transformer that feeds secondary OH to a pump house, for better visibility.
54 | MISC | Are foreign attachments allowed on poles (signs, customer signs)? | Foreign attachments are only allowed with the consent of both the utility owner and the Commission. | Rule 34 Rule 15.1
55 | MISC | Do multiconductor cables from different secondary source feeds need to have separate attachments? | Secondary of multiconductor cables being fed from different secondary sources shall have separate attachments (i.e. spools, dead ends, racks). | Rule 54.10-C(6)
56 | MISC | Do vertical communication attachments above ground level need to be securely attached? | Vertical runs shall be treated as risers where within 8 feet from the ground line. Above 8 feet all vertical communication runs not installed in conduit or covered must be supported no more than every 24 inches by bridle hooks or rings. | Rule 87.7D Rule 84.6D
57 | MISC | What is the deciding factor for determining Urban vs Rural designation? | 100% of Pacific Power's service area in California is Rural per agreement with the CPUC.
58 | NEUTRAL MARKING | Does the neutral need to be marked if located in the primary position? | Yes, a common neutral in the primary position needs to be marked as "CN". Those not in the primary position do not. | Rule 59.3E3 Rule 59.3F
60 | POLE | How should woodpecker damage be reported in FPI? | Input as "BIRDDMG". Enter as B condition per Policy 045. | PacifiCorp Woodpecker Policy 045 | Enter as BIRDDMG
61 | POLE | Are dead end poles with no down guys reported as a condition? | Report if the pole is leaning excessively or needs additional support.
62 | POLE | On structures with a push brace, what is treated? | On structures with a push brace, the pole and the push brace are both treated. The facility point is only associated with the pole. Make a notation on the IF screen that the push brace has been treated.
63 | POLE | Do communication risers including service drops running down the pole need to be covered? | Per GO 95, communication risers shall be covered to at least 8 feet above ground level. | Rule 87.7D1(a) | BORISER - A priority if below 8 ft and B if above 8 ft.
64 | POLE | Are stand-off brackets located at the bottom of a riser nonconforming? | No, this is not nonconforming.
65 | POLE | What is the required separation between staples for all covered parts of vertical run attachments including communication and ground wires? | Maximum spacing 3 feet, but locate extra staples as required to follow contour of pole. | Rule 22.2 Figure 82
66 | POLE | Are all supply service drops required to be attached to an insulator or house knob? | Yes, all service drop cables with a bare neutral conductor must be attached at the pole and the building ends by means of an insulator. | 49.4-C-7-a
67 | POLE | Does a weatherhead mast need to be guyed? | Mast guying is an NEC (customer) requirement that started in 1975. All masts must be adequately supported or guyed to safely support the service cable. This should be reported as a condition in FPI only if the mast is being pulled loose or is bent or leaning. | NEC (Not GO95 nor NESC)

## CONDITION CODE DROPDOWNS
Procedure 069 : Condition Codes | [7 empty] | Updated: 3/9/2023
Note: C-conditions are for CA supply only.
NO | CONDITION_CODE | COMPANY | STATE | DIST_TRANS | OH_UG | CONDITION_GROUP | DESCRIPTION_DETAILED | DESCRIPTION_DROP_DOWN | PRIORITY | DIFFERENTIATING | POLICY_REFERENCE | GO95 | NESC | GRANDFATHERABLE | ENERGY_RELEASE_RISK | RELIABILITY | CREW | RESPONSIBLE_PARTY
1 | AMIEQ | PP/RMP | ALL | BOTH | OH | AMI | AMI RELATED CONDITION | AMI RELATED CONDITION | B | AMI related condition which cannot be categorized in other condition codes. Physical damage to AMI equipment. RMP Only. | N/A | GO95 Rule 94.4 | NESC Rules 235I, 239G1 & 239H2 | NO | NO | NO | SINGLEMAN | POWER
2 | ANCHIDLE | PP/RMP | ALL | BOTH | OH | ANCHOR ISSUE | IDLE ANCHOR | ANCHOR - IDLE ANCHOR | A/B | For RMP, "A" if ground rod is not flush with or below the ground level in high pedestrian traffic area. "B" if not in high pedestrian traffic area. | N/A | GO95, Section I-2, Section I-3 | NESC Rule 012C, NESC Rule 214B3 | NO | NO | YES | SINGLEMAN | POWER
3 | ANCPUCO | PP/RMP | ALL | BOTH | OH | ANCHOR ISSUE | PULLED/CORRODED ANCHOR | ANCHOR - PULLED/CORRODED | A/B | "A" if anchor is pulled or > 50% corrosion. "B" is < 50% corrosion present or other damage. Buried anchor is not a condition. | Policy 009 | GO95 Rule 61.3-A3b | NESC 261B | NO | YES | YES | SINGLEMAN | POWER
4 | AVIANDMG | PP/RMP | ALL | BOTH | OH | AVIAN DAMAGE | AVIAN PROTECTION DEVICES DAMAGED | AVIAN PROTECTION DEVICE DAMAGED | A/B/D | "A" if potential to affect system reliability. "B" if not immediate hazard. Priority "D" if not threat to reliability or safety. | Policy 244 | N/A | N/A | NO | NO | YES | SINGLEMAN | POWER
5 | BIRDDMG | PP/RMP | ALL | BOTH | OH | BIRD DAMAGE | WOODPECKER HOLES | BIRDDMG - WOODPECKER HOLES | B | See policy references. Request a follow-up inspection (climbing or bucket truck) to determine extent of damage. OREGON: inspection performed no later than one year from date of discovery. CALIFORNIA: inspection performed no later than four calendar years from date of discovery. WASHINGTON, IDAHO, UTAH, and WYOMING: inspection recommended no later than four calendar years from date of discovery. | Policy 045 | N/A | NESC 012C | NO | NO | YES | SINGLEMAN | POWER
6 | BIRDNST | PP/RMP | ALL | BOTH | OH | BIRD DAMAGE | BIRD NEST, LARGE IN PRIMARY | BIRDNST - NEST IN PRIMARY | B | “B” if likely to compromise reliability - notify area manager. Otherwise not a condition. For bird mortalities, contact Environmental Services. | Policy 244; Bird Flowchart Combined Mortality and Nest | N/A | NESC 012C | NO | YES | YES | SINGLEMAN | POWER
7 | BIRDWST | PP/RMP | ALL | BOTH | OH | BIRD DAMAGE | CONTAMINATION/BIRD DROPPINGS | BIRD WASTE-CONTAMINATION/DROPPINGS | B | B if likely to compromise reliability | N/A | N/A | NESC 012C | NO | NO | YES | SINGLEMAN | POWER
8 | CANTINSP | PP/RMP | ALL | BOTH | OHUG | INSPECTION ISSUE | CANT INSPECT DUE TO CUSTOMER OBSTRUCTION | INSP ISSUE - CUSTOMER OBSTRUCTION | B | In comments note access issue. Construction obstruction, customer refusal, dog/animals, locked gate, honeybee box. See VEGCANTI and INSPISSU for vegetation and non-customer related obstructions. | Policy 361, 298, 298 & 013 | GO95 Rule 31.2 | NESC Rule 312, NESC Rule 121A | NO | NO | NO | SINGLEMAN | POWER
9 | CAPDMGLS | PP/RMP | ALL | BOTH | OH | CAPACITOR | EQUIP DAMAGED/LOOSE | CAPACITOR DAMAGED/LOOSE | B |  | Policy 009 | GO95, Section I-3 | NESC Rule 012C | NO | YES | YES | 2 MAN | POWER
10 | CFIBMID | PP/RMP | ALL | BOTH | OH | FIBER CLEARANCE CONDITION | CLEARANCE TO SUPPLY AT MID-SPAN | CLEARANCE-FIBER AT MIDSPAN | B | Less than 100% of clearance is "B". Pole to pole midspan and/or service worker safety clearances are required. | N/A | GO95 Rule 38 Table 2 | NESC Rule 235C2b(1)(a) & 235C1, Exception 3 | YES | NO | NO | COMMUNICATIONS | COMMUNICATIONS
11 | CFIBMST | PP/RMP | ALL | BOTH | OH | FIBER CLEARANCE CONDITION | CLEARANCE TO POWER SUPPLY AT MAST | CLEARANCE-FIBER AT MAST | B | Less than 12" at mast. | N/A | GO95 Rule 54.8C4 | NESC 235C1 | YES | NO | NO | COMMUNICATIONS | COMMUNICATIONS
12 | CFIBPED | PP/RMP | ALL | BOTH | OH | FIBER CLEARANCE CONDITION | COMMUNICATION PEDESTRIAN CLEARANCE | COMMUNICATION PEDESTRIAN CLEARANCE | A/B | Less than 8' clearance is "A". Between 8' feet and required clearance is "B". | N/A | GO95 Rule 84.8(3)(a), 84.8(3)b & 84.8(3)(b)(Ex) | NESC Rule 232B1 (Table 232-1), 232B3 (Table 232-2) | NO | NO | NO | COMMUNICATIONS | COMMUNICATIONS
13 | CFIBPOLE | PP/RMP | ALL | BOTH | OH | FIBER CLEARANCE CONDITION | CLEARANCE TO SUPPLY AT POLE | CLEARANCE-FIBER AT POLE | B | If less than 100% of clearance, "B". Need worker safety zone and to street light. | N/A | GO95 Rule 92.1F(3) | NESC Rule 238-2, 238D & 235C1b | YES | NO | NO | COMMUNICATIONS | COMMUNICATIONS
14 | CFIBRD | PP/RMP | ALL | BOTH | OH | FIBER CLEARANCE CONDITION | CLEARANCE OF MESSENGER TO DRIVABLE SURFACE | CLEARANCE-FIBER TO ROAD | A/B | Less than 14' clearance is "A". For pole-to-pole over residential driveways, less than 80% of the required clearance is "A". Less than 100% is a B | N/A | GO95 Rule 54.8, Table 1 | NESC Rule 232B1, Table 232-1 | YES | NO | NO | COMMUNICATIONS | COMMUNICATIONS
15 | CFIBRR | PP/RMP | ALL | BOTH | OH | FIBER CLEARANCE CONDITION | CLEARANCE OF MESSENGER TO RAILROAD | CLEARANCE OF MESSENGER TO RAILROAD | A/B | Less than 22' clearance is "A". Between 22' feet and required clearance is "B". | N/A | GO95 Rule 37 | NESC Rule 232B1 (Table 232-1) | NO | NO | NO | COMMUNICATIONS | COMMUNICATIONS
16 | CFIBSVC | PP/RMP | ALL | BOTH | OH | FIBER CLEARANCE CONDITION | CLEARANCE CROSSING SERVICE | CLEARANCE-FIBER XING SERVICE | B | If less than 100% of clearance, "B". Need 24" when off different support structure. | N/A | GO95 Rule 92.1F(3) | NESC Rule 233C1, Table 233-1 | YES | NO | NO | COMMUNICATIONS | COMMUNICATIONS
17 | CLEAR | PP/RMP | ALL | BOTH | OH | CLEARANCE CONDITION | THIS IS A CONDITION THAT WAS REASSIGNED TO CLEAR FOR POWER RESPONSIBILITY TO CORRECT COMMUNICATIONS CONDITIONS | CLEAR-POWER TO CORRECT COMM CLR | A/B |  | N/A | N/A | NESC Table 238-2, NESC Rule 238D. NESC Rule 235C1b, Table 235-5 | NO | NO | NO | SINGLEMAN | POWER
18 | CLMBHAZ | PP/RMP | ALL | BOTH | OH | CLIMBING SPACE | CLIMBING SPACE ISSUE | CLIMBING HAZARD | B | Supply issue in climbing space (long bolts, loose ground wire, vines/vegetation, etc.). In CA, climbing space hazards that are more than a supply space issue use condition code GO95CLMP. | Policy 009 | GO95 Rule 54.7 | NESC Rule 217A4b, NESC 236A, | NO | NO | NO | SINGLEMAN | POWER
19 | CLMBTRE | PP | CA, OR, WA | BOTH | OH | VEGETATION | VEGETATION IN CLIMBING SPACE | VEGETATION IN CLIMBING SPACE | B | PP Only - Climbing Hazard Due To Vegetation In Climbing Space | N/A | GO95 Rule 54.7 | NESC Rule 217A4b, NESC 236A, | NO | YES | YES | SINGLEMAN | POWER
20 | CLRBLDG | PP/RMP | ALL | BOTH | OH | CLEARANCE CONDITION | PRIMARY CONDUCTOR TO BUILDING / SIGN | CLEARANCE: PRIMARY-BUILDING/SIGN | A |  | N/A | N/A | NESC Rule 234C1a, Table 234-1 | NO | YES | NO | SINGLEMAN | POWER
21 | CLRLOW | PP/RMP | ALL | BOTH | OH | CLEARANCE CONDITION | LOW PRIMARY CONDUCTOR | CLEARANCE: PRIMARY LOW | A | Use GO95 clearances in CA; NESC clearances in all other states | N/A | GO95 54.5 | NESC Rule 232B1, Table 232-1 | NO | YES | NO | SINGLEMAN | POWER
22 | CLRTOPOL | PP/RMP | ALL | BOTH | OH | CLEARANCE CONDITION | UNATTACHED CONDUCTOR CLR TO POLE | UNATTACHED CONDUCTOR CLEARANCE TO POLE | B | less than 5 ft. to supply. Effectively grounded neutrals and service conductors of 300V or less can be 3 ft. | N/A | GO95 Rule 54.4-D3, Table 1 Case 8 | NESC Rule 234B1a, NESC Rule 234B2a | NO | YES | NO | SINGLEMAN | POWER
23 | CLRTOUCH | PP/RMP | ALL | BOTH | OH | CLEARANCE CONDITION | SERVICE/PRIMARY NEUTRAL TOUCHING GUY/TRANSFORMER/POLE | CLEARANCE TOUCHING GUY/XFMR/POLE | B |  | N/A | N/A | NESC Rule 235E, Table 235-6 | NO | YES | NO | SINGLEMAN | POWER
24 | COANT | PP/RMP | ALL | BOTH | OH | COMMUNICATION | CELL ANTENNA OR WIFI ANTENNA | ANTENNA CELL OR WIFI | B | Cell Antenna Or Wifi Antenna Related Conditions Which Cannot Be Categorized In Other Condition Codes | N/A | GO95 Rule 94.4 | NESC Rule 235I, Table 235-6 row 1c, 239G1 & 239H2 | NO | NO | NO | COMMUNICATIONS | COMMUNICATIONS
25 | COCATV | PP/RMP | ALL | BOTH | OH | CATV CONDITION | ANY CATV RELATED CONDITION THAT CAN NOT BE CATEGORIZED IN OTHER CATV CONDITION CODES | COND-CATV GENERAL | A/B/C | "C" condition only applies to California | N/A | N/A | N/A | NO | NO | NO | COMMUNICATIONS | COMMUNICATIONS
26 | COFIBBND | PP/RMP | ALL | BOTH | OH | FIBER CONDITION | COMM MESSENGER NOT BONDED/GROUNDED | COMM MESSENGER NOT BONDED/GROUNDED | B | Messengers shall be effectively grounded | N/A | GO95 Rule 92.4D & 93B | NESC Rule 215C1 & 215C5 | NO | NO | NO | COMMUNICATIONS | COMMUNICATIONS
27 | COFIBCLM | PP/RMP | ALL | BOTH | OH | FIBER CONDITION | CLIMBING SPACE CONDITION | COND-FIBER CLIMBING SPACE | B | Any condition resulting in no available climbing space. Thru-bolts are condition only if 4" beyond nut and in the only available climbing space. | N/A | N/A | NESC Rule 217A4b, NESC 236A, | NO | NO | NO | COMMUNICATIONS | COMMUNICATIONS
28 | COFIBER | PP/RMP | ALL | BOTH | OH | FIBER CONDITION | ANY FIBER RELATED CONDITION THAT CAN NOT BE CATEGORIZED IN OTHER FIBER CONDITION CODES | COND-FIBER GENERAL | A/B/C | "C" condition only applies to California | N/A | N/A | N/A | NO | NO | NO | COMMUNICATIONS | COMMUNICATIONS
29 | COFIBEYE | PP/RMP | ALL | BOTH | OH | FIBER CONDITION | SISTER OR AUXILIARY EYE | COND-FIBER AUX/SISTER EYE | B | SISTER OR AUXILIARY EYE, married guy | N/A | N/A | N/A | NO | NO | NO | COMMUNICATIONS | COMMUNICATIONS
30 | COFIBGUY | PP/RMP | ALL | BOTH | OH | FIBER CONDITION | SLACK GUY OR LONG TAIL | COND-FIBER SLACK GUY-LONG TAIL | B |  | N/A | N/A | NESC Rule 264A, 214B2 | NO | NO | NO | COMMUNICATIONS | COMMUNICATIONS
31 | COFIBINS | PP/RMP | ALL | BOTH | OH | FIBER CONDITION | NO GUY INSULATOR OR NOT EFFECTIVELY GROUNDED | COND-FIBER NO GUY INSUL/NOT GRNDED | B | No guy insulator or is not effectively grounded | N/A | N/A | NESC 215C2a & b | NO | NO | NO | COMMUNICATIONS | COMMUNICATIONS
32 | COFIBRIS | PP/RMP | ALL | BOTH | OH | FIBER CONDITION | CLIMBABLE RISER | COND-FIBER RISER CLIMBABLE | A/B | "A" if climbable into primary/neutral/open secondary. "B" if climbable into insulated secondary, or if supply riser is on same pole. Not a condition if no supply riser on pole and not climbable into supply. | N/A | N/A | NESC 217A2 | NO | NO | NO | COMMUNICATIONS | COMMUNICATIONS
33 | COFIBTRN | PP/RMP | ALL | BOTH | OH | FIBER CONDITION | INCOMPLETE CHANGEOVER/TRANSFER | COND-FIBER INCOMPLETE TRANSFER | B | Comm has not transferred to new pole. | N/A | N/A | NESC RuleS 214A5, 214B3 & 234B | NO | NO | NO | COMMUNICATIONS | COMMUNICATIONS
34 | COMKLITE | PP/RMP | ALL | BOTH | OH | OTHER CONDITION | AIRPORT OR AERIAL MARKER BALL MISSING OR LIGHT FAILED | COND-MARKER BALL MSSNG/LIGHT FAILED | A/B | FAA required markers and lights. "A" if light failed. "B" if marker missing. Transmission and distribution. | N/A | N/A | N/A | NO | NO | NO | SINGLEMAN | POWER
35 | CONDCOIL | PP/RMP | ALL | BOTH | OH | CONDUCTOR | COILED SERVICE WIRE HANGING FROM POLE | CONDUCTOR COILED AT POLE | A/B | A if energized and near comm lines/in public space. Otherwise "B" | Policy 009 | N/A | NESC Rule 214B2, NESC Rule 012C | NO | YES | YES | SINGLEMAN | POWER
36 | CONDFRAY | PP/RMP | ALL | BOTH | OH | CONDUCTOR | DAMAGED/FRAYED PRIMARY CONDUCTOR | CONDUCTOR DAMAGED/FRAYED | A/B | Dependent on degree of damage, > 50% of conductor strands cut = "A". If more than surface strands damaged, "B" | Policy 009 | GO95, Section I-2, Section I-3 | NESC 261H1 | NO | YES | YES | SINGLEMAN | POWER
37 | CONDLOOS | PP/RMP | ALL | BOTH | OH | CONDUCTOR | BROKEN LOOSE TIE WIRE OR FLOATING CONDUCTOR | CONDUCTOR FLOATING/TIE WIRE BRK/LOOSE | A | If loose enough to free conductor, "A". | Policy 009 | GO95, Section I-4 | NESC Rule 214A5a, NESC Rule 012C | NO | YES | YES | SINGLEMAN | POWER
38 | COOTHER | PP/RMP | ALL | BOTH | OHUG | OTHER CONDITION | CONDITION OTHER | CONDITION OTHER | A/B/D | Used where no other condition code description defines issue. Inspector will need to document in detail issue. Priority D is RMP only. | N/A | N/A | N/A | NO | NO | NO | SINGLEMAN | POWER
39 | COPLLEAN | PP/RMP | ALL | BOTH | OH | POLE | POLE LEANING, NEEDS EVALUATION | CONDITION POLE LEANING | A/B | If leaning into roadway and an immediate hazard to vehicular traffic, "A". If leaning severely, "A". If leaning moderately in urban area, "B". | N/A | N/A | NESC 261A2a | NO | YES | NO | SINGLEMAN | POWER
40 | CORRING | PP/RMP | ALL | BOTH | OH | CORONA RING | MISSING, DAMAGED OR LOOSE CORONA RING | CORONA RING | A |  | N/A | N/A | NESC | NO | NO | YES | 3 MAN | POWER
41 | COTELBND | PP/RMP | ALL | BOTH | OH | TELCO CONDITION | COMM MESSENGER NOT BONDED/GROUNDED | COMM MESSENGER NOT BONDED/GROUNDED | B | Messengers shall be effectively grounded | N/A | GO95 Rule 92.4D & 93B | NESC Rule 215C1 & 215C5 | NO | NO | NO | COMMUNICATIONS | COMMUNICATIONS
42 | COTELCLM | PP/RMP | ALL | BOTH | OH | TELCO CONDITION | CLIMBING SPACE CONDITION | COND-TELCO CLIMBING SPACE | B | Any condition resulting in no available climbing space. Thru-bolts are condition only if 4" beyond nut and in the only available climbing space. | N/A | N/A | NESC Rule 217A4b, NESC 236A, | NO | NO | NO | COMMUNICATIONS | COMMUNICATIONS
43 | COTELCO | PP/RMP | ALL | BOTH | OH | TELCO CONDITION | ANY TELCO RELATED CONDITION THAT CAN NOT BE CATEGORIZED IN OTHER TELCO CONDITION CODES | COND-TELCO GENERAL | A/B/C | "C" condition only applies to California | N/A | N/A | N/A | NO | NO | NO | COMMUNICATIONS | COMMUNICATIONS
44 | COTELEYE | PP/RMP | ALL | BOTH | OH | TELCO CONDITION | SISTER OR AUXILIARY EYE | COND-TELCO AUX/SISTER EYE | B | SISTER OR AUXILIARY EYE, married guy | N/A | N/A | N/A | NO | NO | NO | COMMUNICATIONS | COMMUNICATIONS
45 | COTELGUY | PP/RMP | ALL | BOTH | OH | TELCO CONDITION | SLACK GUY OR LONG TAIL | COND-TELCO SLACK GUY-LONG TAIL | B |  | N/A | N/A | NESC Rule 264A, 214B2 | NO | NO | NO | COMMUNICATIONS | COMMUNICATIONS
46 | COTELINS | PP/RMP | ALL | BOTH | OH | TELCO CONDITION | NO GUY INSULATOR OR NOT EFFECTIVELY GROUNDED | COND-TELCO NO GUY INSUL/NOT GRNDED | B | No guy insulator or is not effectively grounded | N/A | N/A | NESC 215C2a & b | NO | NO | NO | COMMUNICATIONS | COMMUNICATIONS
47 | COTELRIS | PP/RMP | ALL | BOTH | OH | TELCO CONDITION | CLIMBABLE RISER | COND-TELCO RISER CLIMBABLE | A/B | "A" if climbable into primary/neutral/open secondary. "B" if climbable into insulated secondary, or if supply riser is on same pole. Not a condition if no supply riser on pole and not climbable into supply. | N/A | N/A | NESC 217A2 | NO | NO | NO | COMMUNICATIONS | COMMUNICATIONS
48 | COTELTRN | PP/RMP | ALL | BOTH | OH | TELCO CONDITION | INCOMPLETE CHANGEOVER/TRANSFER | COND-TELCO INCOMPLETE TRANSFER | B | Comm has not transferred to new pole. | N/A | N/A | NESC RuleS 214A5, 214B3 & 234B | NO | NO | NO | COMMUNICATIONS | COMMUNICATIONS
49 | COTVBND | PP/RMP | ALL | BOTH | OH | CATV CONDITION | COMM MESSENGER NOT BONDED/GROUNDED | COMM MESSENGER NOT BONDED/GROUNDED | B | Messengers shall be effectively grounded | N/A | GO95 Rule 92.4D & 93B | NESC Rule 215C1 & 215C5 | NO | NO | NO | COMMUNICATIONS | COMMUNICATIONS
50 | COTVCLM | PP/RMP | ALL | BOTH | OH | CATV CONDITION | CLIMBING SPACE CONDITION | COND-CATV CLIMBING SPACE | B | Any condition resulting in no available climbing space. Thru-bolts are condition only if 4" beyond nut and in the only available climbing space. | N/A | N/A | NESC Rule 217A4b, NESC 236A, | NO | NO | NO | COMMUNICATIONS | COMMUNICATIONS
51 | COTVEYE | PP/RMP | ALL | BOTH | OH | CATV CONDITION | SISTER OR AUXILIARY EYE | COND-CATV AUX/SISTER EYE | B | SISTER OR AUXILIARY EYE, married guy | N/A | N/A | N/A | NO | NO | NO | COMMUNICATIONS | COMMUNICATIONS
52 | COTVGUY | PP/RMP | ALL | BOTH | OH | CATV CONDITION | SLACK GUY OR LONG TAIL | COND-CATV SLACK GUY-LONG TAIL | B |  | N/A | N/A | NESC Rule 264A, 214B2 | NO | NO | NO | COMMUNICATIONS | COMMUNICATIONS
53 | COTVINS | PP/RMP | ALL | BOTH | OH | CATV CONDITION | NO GUY INSULATOR OR NOT EFFECTIVELY GROUNDED | COND-CATV NO GUY INSUL/NOT GRNDED | B | No guy insulator or is not effectively grounded | N/A | N/A | NESC 215C2a & b | NO | NO | NO | COMMUNICATIONS | COMMUNICATIONS
54 | COTVRIS | PP/RMP | ALL | BOTH | OH | CATV CONDITION | CLIMBABLE RISER | COND-CATV RISER CLIMBABLE | A/B | "A" if climbable into primary/neutral/open secondary. "B" if climbable into insulated secondary, or if supply riser is on same pole. Not a condition if no supply riser on pole and not climbable into supply. | N/A | N/A | NESC 217A2 | NO | NO | NO | COMMUNICATIONS | COMMUNICATIONS
55 | COTVTRN | PP/RMP | ALL | BOTH | OH | CATV CONDITION | INCOMPLETE CHANGEOVER/TRANSFER | COND-CATV INCOMPLETE TRANSFER | B | Comm has not transferred to new pole. | N/A | N/A | NESC Rule 214A5, 214B3 & 234B | NO | NO | NO | COMMUNICATIONS | COMMUNICATIONS
56 | COVCFRAY | PP/RMP | ALL | BOTH | OH | COVERED CONDUCTOR | COVERED CONDUCTOR CONDITION FRAYED | COVERED CONDUCTOR CONDITION FRAYED | A/B | Dependent on degree of damage, > 50% of conductor strands cut = "A". If more than surface strands damaged, "B" | TBD | N/A | N/A | NO | YES | YES | 4 MAN | POWER
57 | COVCLOOS | PP/RMP | ALL | BOTH | OH | COVERED CONDUCTOR | COVERED CONDUCTOR CONDITION LOOSE | COVERED CONDUCTOR CONDITION LOOSE | A | If loose enough to free conductor, "A". | TBD | N/A | N/A | NO | YES | YES | 4 MAN | POWER
58 | COVCOTHR | PP/RMP | ALL | BOTH | OH | COVERED CONDUCTOR | COVERED CONDUCTOR CONDITION OTHER CONDITION | COVERED CONDUCTOR CONDITION OTHER CONDITION | A/B | Another condition related to covered conductor, include in notes details. | TBD | N/A | N/A | NO | NO | YES | 4 MAN | POWER
59 | CTELMID | PP/RMP | ALL | BOTH | OH | TELCO CLEARANCE CONDITION | CLEARANCE TO SUPPLY AT MID-SPAN | CLEARANCE-TELCO AT MIDSPAN | B | Less than 100% of clearance is "B". Pole to pole midspan and/or service worker safety clearances are required. | N/A | GO95 Rule 38 Table 2 | NESC Rule 235C2b(1)(a) & 235C1, Exception 3 | YES | NO | NO | COMMUNICATIONS | COMMUNICATIONS
60 | CTELMST | PP/RMP | ALL | BOTH | OH | TELCO CLEARANCE CONDITION | CLEARANCE TO POWER SUPPLY AT MAST | CLEARANCE-TELCO AT MAST | B | Less than 12" at mast. | N/A | GO95 Rule 54.8C4 | NESC 235C1 | YES | NO | NO | COMMUNICATIONS | COMMUNICATIONS
61 | CTELPED | PP/RMP | ALL | BOTH | OH | TELCO CLEARANCE CONDITION | COMMUNICATION PEDESTRIAN CLEARANCE | COMMUNICATION PEDESTRIAN CLEARANCE | A/B | Less than 8' clearance is "A". Between 8' feet and required clearance is "B". | N/A | GO95 Rule 84.8(3)(a), 84.8(3)b & 84.8(3)(b)(Ex) | NESC Rule 232B1 (Table 232-1), 232B3 (Table 232-2) | NO | NO | NO | COMMUNICATIONS | COMMUNICATIONS
62 | CTELPOLE | PP/RMP | ALL | BOTH | OH | TELCO CLEARANCE CONDITION | CLEARANCE TO SUPPLY AT POLE | CLEARANCE-TELCO AT POLE | B | If less than 100% of clearance, "B". Need worker safety zone and to street light. | N/A | GO95 Rule 92.1F(3) | NESC Rule 238-2, 238D & 235C1b | YES | NO | NO | COMMUNICATIONS | COMMUNICATIONS
63 | CTELRD | PP/RMP | ALL | BOTH | OH | TELCO CLEARANCE CONDITION | CLEARANCE OF MESSENGER TO DRIVABLE SURFACE | CLEARANCE-TELCO TO ROAD | A/B | Less than 14' clearance is "A". For pole-to-pole over residential driveways, less than 80% of the required clearance is "A". Less than 100% is a B | N/A | GO95 Rule 54.8, Table 1 | NESC Rule 232B1, Table 232-1 | YES | NO | NO | COMMUNICATIONS | COMMUNICATIONS
64 | CTELRR | PP/RMP | ALL | BOTH | OH | TELCO CLEARANCE CONDITION | CLEARANCE OF MESSENGER TO RAILROAD | CLEARANCE OF MESSENGER TO RAILROAD | A/B | Less than 22' clearance is "A". Between 22' feet and required clearance is "B". | N/A | GO95 Rule 37 | NESC Rule 232B1 (Table 232-1) | NO | NO | NO | COMMUNICATIONS | COMMUNICATIONS
65 | CTELSVC | PP/RMP | ALL | BOTH | OH | TELCO CLEARANCE CONDITION | CLEARANCE CROSSING SERVICE | CLEARANCE-TELCO XING SERVICE | B | If less than 100% of clearance, "B". Need 24" when off different support structure. | N/A | GO95 Rule 92.1F(3) | NESC Rule 233C1, Table 233-1 | YES | NO | NO | COMMUNICATIONS | COMMUNICATIONS
66 | CTVMID | PP/RMP | ALL | BOTH | OH | CATV CLEARANCE CONDITION | CLEARANCE TO SUPPLY AT MID-SPAN | CLEARANCE-CATV AT MIDSPAN | B | Less than 100% of clearance is "B". Pole to pole midspan and/or service worker safety clearances are required. | N/A | GO95 Rule 38 Table 2 | NESC Rule 235C2b(1)(a) & 235C1, Exception 3 | YES | NO | NO | COMMUNICATIONS | COMMUNICATIONS
67 | CTVMST | PP/RMP | ALL | BOTH | OH | CATV CLEARANCE CONDITION | CLEARANCE TO POWER SUPPLY AT MAST | CLEARANCE-CATV AT MAST | B | Less than 12" at mast. | N/A | GO95 Rule 54.8C4 | NESC 235C1 | YES | NO | NO | COMMUNICATIONS | COMMUNICATIONS
68 | CTVPED | PP/RMP | ALL | BOTH | OH | CATV CONDITION | COMMUNICATION PEDESTRIAN CLEARANCE | COMMUNICATION PEDESTRIAN CLEARANCE | A/B | Less than 8' clearance is "A". Between 8' feet and required clearance is "B". | N/A | GO95 Rule 84.8(3)(a), 84.8(3)b & 84.8(3)(b)(Ex) | NESC Rule 232B1 (Table 232-1), 232B3 (Table 232-2) | NO | NO | NO | COMMUNICATIONS | COMMUNICATIONS
69 | CTVPOLE | PP/RMP | ALL | BOTH | OH | CATV CLEARANCE CONDITION | CLEARANCE TO SUPPLY AT POLE | CLEARANCE-CATV AT POLE | B | If less than 100% of clearance, "B". Need worker safety zone and to street light. | N/A | GO95 Rule 92.1F(3) | NESC Rule 238-2, 238D & 235C1b | YES | NO | NO | COMMUNICATIONS | COMMUNICATIONS
70 | CTVRD | PP/RMP | ALL | BOTH | OH | CATV CLEARANCE CONDITION | CLEARANCE OF MESSENGER TO DRIVABLE SURFACE | CLEARANCE-CATV TO ROAD | A/B | Less than 14' clearance is "A". For pole-to-pole over residential driveways, less than 80% of the required clearance is "A". Less than 100% is a B | N/A | GO95 Rule 54.8, Table 1 | NESC Rule 232B1, Table 232-1 | YES | NO | NO | COMMUNICATIONS | COMMUNICATIONS
71 | CTVRR | PP/RMP | ALL | BOTH | OH | CATV CONDITION | CLEARANCE OF MESSENGER TO RAILROAD | CLEARANCE OF MESSENGER TO RAILROAD | A/B | Less than 22' clearance is "A". Between 22' feet and required clearance is "B". | N/A | GO95 Rule 37 | NESC Rule 232B1 (Table 232-1) | NO | NO | NO | COMMUNICATIONS | COMMUNICATIONS
72 | CTVSVC | PP/RMP | ALL | BOTH | OH | CATV CLEARANCE CONDITION | CLEARANCE CROSSING SERVICE | CLEARANCE-CATV XING SERVICE | B | If less than 100% of clearance, "B". Need 24" when off different support structure. | N/A | GO95 Rule 92.1F(3) | NESC Rule 233C1, Table 233-1 | YES | NO | NO | COMMUNICATIONS | COMMUNICATIONS
73 | CUSTACCE | RMP | UT, WY, ID | BOTH | OHUG | CUSTOMER RESPONSIBILITY | NO ACCESS/ACCESS DENIED/LOCKED GATE/CUSTOMER VEG. ISSUE | CUSTOMER ACCESS/VEG ISSUE | B | Note problem in IF and record address. RMP ONLY | N/A | N/A | NESC 213 and 214 | NO | NO | NO | CUSTOMER | CUSTOMER
74 | CUSTRESP | PP/RMP | ALL | BOTH | OHUG | CUSTOMER RESPONSIBILITY | CUSTOMER RESPONSIBILITY | CUSTOMER RESPONSIBILITY | A/B/D | Customer significant risk is "A". Customer low risk is "B". Customer meter pole is "D" | N/A | N/A | N/A | NO | NO | NO | CUSTOMER | CUSTOMER
75 | CUSTWIRE | PP/RMP | ALL | BOTH | OH | CUSTOMER RESPONSIBILITY | LIGHT, WIRE, ANTENNA, OR OTHER CUSTOMER ITEM ATTACHED TO POLE | CUSTOMER WIRE/LIGHT/OTHER ATTACH POLE | B | Antenna or other Customer items attached to pole >10' from supply space. See ENCHRW for items <10' from supply space. | N/A | GO95 Rule 34 | NESC 217A-4 | NO | NO | NO | CUSTOMER | CUSTOMER
76 | CUTOUTAR | PP/RMP | ALL | BOTH | OH | CUTOUT/ARRESTOR | CUTOUT/ARRESTOR ISSUE | CUTOUT/ARRESTOR | A/B/D | Smoking, Sparking, tracking, Cracked porcelain, or split polymer is "A". "B" If Jumpered out or parts missing. Blown Arrestor is "B". Priority D is RMP only for idle equip or porcelain cutout; note in comment field. | Policy 009 | GO95, Section I-3 | NESC Rule 012C | NO | YES | YES | SINGLEMAN | POWER
77 | DISTCLOW | RMP | UT, WY, ID | DISTRIBUTION | OH | DISTRIBUTION LOW SAG ISSUE | LOW SAG PRIMARY OR OPEN SECONDARY | LOW SAG PRIMARY OR OPEN SECONDARY | D | Information only to support record keeping or other programs. Priority D is RMP only. | N/A | N/A | N/A | NO | NO | NO | SINGLEMAN | POWER
78 | DISTHDWR | PP/RMP | ALL | DISTRIBUTION | OH | DISTRIBUTION HARDWARE | MISSING OR LOOSE HARDWARE | MISSING OR LOOSE HARDWARE | A/B | "A" if missing hardware. "B" if loose hardware. Expanded spring not a condition. Note hardware in comment field. | N/A | GO95 Rule 18 A-1 | NESC Rule012C | NO | YES | YES | SINGLEMAN | POWER
79 | EARMSPCR | PP/RMP | ALL | BOTH | OH | EQUIPMENT ARM | EQUIPMENT ARM IS SPLIT/ CRACKED/ ROTTEN/ TWISTED/ TRACKING | EQUIPMENT ARM ISSUE | A/B | Severe, "A". Moderate, "B". This code does not include: weather station equipment arms, guy arms, or crossarms. | N/A | N/A | NESC Rule 012C & 252 | NO | YES | YES | SINGLEMAN | POWER
80 | ENCHCUG | RMP | UT, WY, ID | BOTH | UG | RIGHT OF WAY ENCROACHMENT | UG CONFLICT | ENCROACHMENT R.O.W. UG CONFLICT | D | Indicate issue in comment field. Priority D is RMP only. | N/A | N/A | N/A | NO | NO | NO | SINGLEMAN | POWER
81 | ENCHCUST | RMP | UT, WY, ID | BOTH | OH | RIGHT OF WAY ENCROACHMENT | CUSTOMER ITEM WITHIN MINIMUM APPROACH DISTANCE | ENCROACHMENT R.O.W. CUST IN M.A.D. | B | RMP only: Customer item is attached at pole more than 10' from lowest power. For PP, use CUSTWIRE. | N/A | N/A | N/A | NO | NO | NO | SINGLEMAN | POWER
82 | ENCHRW | PP/RMP | ALL | BOTH | OH | RIGHT OF WAY ENCROACHMENT | LIGHT, WIRE, ANTENNA, OR OTHER CUSTOMER ITEM ATTACHED TO POLE | ENCROACHMENT R.O.W. CUST ATTCH POLE | A/B | If within 40" of primary or open secondary conductor, "A". Between 40" and 10' is a "B". Otherwise it gets classified as (ENCHCUST RMP) or (CUSTWIRE PP). Public safety signs may be grandfathered (Priority "G") per operations. | N/A | GO95 Rule 34 | NESC 217A4 | YES | NO | NO | SINGLEMAN | POWER
83 | ENCHSVCE | PP/RMP | ALL | BOTH | OH | RIGHT OF WAY ENCROACHMENT | CUSTOMER ITEM LESS THAN 3" AT SERVICE ENTRANCE | CUSTOMER ITEM <3" AT SERVICE ENTRANCE | A/B | A priority if contacting, B if customer is less than 3" at service entrance | N/A | N/A | NESC 234C3c | NO | NO | NO | SINGLEMAN | POWER
84 | EQUIPOIL | PP/RMP | ALL | BOTH | OHUG | EQUIPMENT | EQUIPMENT LEAKING OIL | EQUIPMENT LEAKING OIL | A / B | Actively leaking oil onto the ground or into the environment is "A". Weeping oil is a priority B (California Only). Note type of equipment leaking oil in comment field. | Policy 009 | GO95, Section I-2 | NESC Rule 214A5a, NESC Rule 012C | NO | YES | YES | 3 MAN | POWER
85 | EQUIPPAD | PP/RMP | ALL | BOTH | UG | UG PAD / VAULT | DAMAGED CONCRETE OR FIBERGLASS PAD / VAULT | PAD/VAULT DAMAGED | A/B | Exposed with access is "A". Badly damaged w/o access is "B". | N/A | GO128 Rule 31.3, 33.5 | NESC Rule 323 A&I, 363A | NO | NO | NO | SINGLEMAN | POWER
86 | FIREHYDR | PP/RMP | ALL | BOTH | OH | CUSTOMER RESPONSIBILITY | FIRE HYDRANT TOO CLOSE TO POLE | FIRE HYDRANT CLR TO POLE | B | Resolve with local fire dept. | N/A | N/A | NESC 231A | YES | NO | NO | CUSTOMER | CUSTOMER
87 | FOOTING | PP/RMP | ALL | BOTH | OH | CONCRETE FOOTING | NEEDS TREATMENT OR CAP, IS BELOW GRADE, SEVERELY CRACKED/CRUMBLING | FOOTING, CONCRETE | B/D | RMP only: Priority B is RMP only, for severe deterioration/damage with exposed rebar needs treatment. Minor deterioration (erosion, cracking, spalling, flaking, chipping) of concrete without exposed rebar is "D". PP only: any deterioration or damage is a "D" priority." | N/A | N/A | NESC 261a/b | NO | NO | NO | SINGLEMAN | POWER
88 | FRGNELEC | PP/RMP | ALL | BOTH | OH | FOREIGN ELECTRIC ISSUE | THIS IS FOR INTERNAL COMPANY USE AND FOR IDENTIFYING A FOREIGN ELECTRIC ATTACHMENT FACILITY DEFICIENCY | FOREIGN ELECTRIC ISSUE | A/B/D | Priority D is RMP only. | N/A | N/A | N/A | NO | YES | NO | COMMUNICATIONS | POWER
89 | GO95ABND | PP | CA | BOTH | OH | GO95 | PERMANENTLY IDLE/ ABANDONED EQUIPMENT/CONDUCTOR | GO95 ABANDONED EQUIPMENT | C | Idle and abandoned conductors and equipment are a priority C. Pacific Power Only. | N/A | GO95 Section 1-4, "Appendix I-Level 3" | N/A | NO | NO | NO | SINGLEMAN | POWER
90 | GO95BLTC | PP | CA | BOTH | OH | GO95 | MISSING BOLT COVERS | GO95 BOLT COVERS MISSING | C | Bolts supporting energized equipment are required to be covered. Pacific Power Only. California Only. | N/A | GO95 II-17 | N/A | NO | NO | NO | SINGLEMAN | POWER
91 | GO95CL10 | PP | CA | BOTH | OH | GO95 CLEARANCE | 10 INCH CLEARANCE FROM EQUIPMENT TO SEC, NEUT OR SERVICE | GO95 CLEARANCE CONDITION | B/C | "B" if wire is contacting transformer, capacitor or other similar apparatus. "C" if clearance is less than 10''. Pacific Power Only. California Only. | N/A | GO95 Rule 54.9-E(2)C | N/A | YES | NO | NO | SINGLEMAN | POWER
92 | GO95CLMF | PP | CA | BOTH | OH | GO95 COMM | FIBER CLIMBING SPACE CONDITION | GO95 CLIMBING SPACE - FIBER ISSUE | B | Pacific Power Only. California Only. | N/A | GO95, Section I-4 | N/A | NO | NO | NO | COMMUNICATIONS | COMMUNICATIONS
93 | GO95CLMP | PP | CA | BOTH | OH | GO95 | CLIMBING SPACE HAZARD | GO95 CLIMBING SPACE - POWER ISSUE | B | Record as a condition if climbing hazard cannot be easily remedied during ascent. Pacific Power Only. California Only. | N/A | GO95 I-4 | NESC 236A | NO | NO | NO | SINGLEMAN | POWER
94 | GO95CLMT | PP | CA | BOTH | OH | GO95 COMM | TELEPHONE CLIMBING SPACE CONDITION | GO95 CLIMBING SPACE - TELCO ISSUE | B | Pacific Power Only. California Only. | N/A | GO95, Section I-4 | N/A | NO | NO | NO | COMMUNICATIONS | COMMUNICATIONS
95 | GO95CLMV | PP | CA | BOTH | OH | GO95 COMM | CABLE TV CLIMBING SPACE CONDITION | GO95 CLIMBING SPACE - TV ISSUE | B | Pacific Power Only. California Only. | N/A | GO95, Section I-4 | N/A | NO | NO | NO | COMMUNICATIONS | COMMUNICATIONS
96 | GO95CLSV | PP | CA | BOTH | OH | GO95 CLEARANCE | SERVICE TOO LOW OVER GROUND | GO95 GROUND CLEARANCE CONDITION | A/B | "A" = less than 7'. "B" = from 7' to 8.49'. Pacific Power Only. California Only. | N/A | GO95 Rule 54.8-B3, Table 10 | N/A | NO | NO | NO | SINGLEMAN | POWER
97 | GO95CN | PP | CA | BOTH | OH | GO95 | COMMON NEUTRAL SIGN MISSING | GO95 COMMON NEUTRAL SIGN MISSING | C | Neutral sign may be a >1" tag or sign with text >3". | N/A | GO95 Section V-165, Section V-166, "Rule 59.3-F" | N/A | NO | NO | NO | SINGLEMAN | POWER
98 | GO95GUYB | PP | CA | BOTH | OH | GO95 | BROKEN GUY | GO95 GUY BROKEN | A/B/C | "A" if broken/damaged in barrel of proximity to HV, "B" if out of proximity. Pacific Power Only. California Only. | N/A | GO95, Section I-2, Section I-3 | N/A | NO | YES | YES | SINGLEMAN | POWER
99 | GO95GUYP | PP | CA | BOTH | OH | GO95 | GUY OR INSULATOR IN BARREL OF PROXIMITY | GO95 GUY/INSUL IN BARREL OF PROXIMITY | C | Guy and insulator must be more than one foot from primary. Insulator also must be a) more than 6' from pole and b) more than 8' below primary. Pacific Power Only. California Only. | N/A | GO95 Section V-125, "Rule 56.6-A" | N/A | NO | NO | YES | SINGLEMAN | POWER
100 | GO95HV | PP | CA | BOTH | OH | GO95 | HIGH VOLTAGE SIGN MISSING | GO95 HIGH VOLTAGE SIGN MISSING | C | HV sign missing, faded or cracked, exception for remote locations which are inaccessible by vehicle. Pacific Power Only. California Only. | N/A | GO95 Rule 51.6-A, Section V-17 | N/A | NO | NO | NO | SINGLEMAN | POWER
101 | GO95MLD | PP | CA | BOTH | OH | GO95 | MOLDING BROKEN, MISSING OR LOOSE | GO95 MOLDING BROKEN/CRACKED/MISSING | B/C | "B" if in communications or public area, otherwise "C". Pacific Power Only. California Only. | N/A | GO95 I-3, I-4, J-5 | N/A | NO | NO | NO | SINGLEMAN | POWER
102 | GO95STUB | PP | CA | BOTH | OH | GO95 | POLE STUB - UNDER 8.5 FEET IN PED AREA | GO95 POLE STUB ISSUE | A/B | "A" = hollowed out butt in pedestrian area. "B" = pedestrian area and less than 8.5' high. Pacific Power Only. California Only. | N/A | Rule 84.8-C4b - PDF Page 374 | N/A | NO | NO | NO | SINGLEMAN | POWER
103 | GO95SVC | PP | CA | BOTH | OH | GO95 CLEARANCE | SERVICE WITHIN 3' OF HOUSE UNATTACHED | GO95 SERVICE CLEARANCE ISSUE | B | 3' horizontal clearance is required. No requirement if attached, In California Only. Pacific Power Only. | N/A | GO95 Rule 54.8B, Table 10 | N/A | NO | NO | NO | SINGLEMAN | POWER
104 | GO95TCH | PP | CA | BOTH | OH | GO95 CLEARANCE | MUST MAINTAIN 3" BETWEEN SERVICE WIRE AND POLE OR CROSSARM | GO95-NEED 3" GAP SVC TO POLE/XARM | B | California supply service only. Pacific Power Only. | N/A | GO95 Table 2 case 9, Table 2 case 8 | N/A | NO | NO | NO | SINGLEMAN | POWER
105 | GOCATVNP | PP | CA | BOTH | OH | GO95 COMM | NOT PROPERLY ATTACHED TO POLE OR ABANDONED EQUIPMENT | GO95 CATV IMPROPERLY ATTCH/ABANDN | C | Pacific Power Only. California Only. | N/A | N/A | N/A | NO | NO | NO | COMMUNICATIONS | COMMUNICATIONS
106 | GOFIBNP | PP | CA | BOTH | OH | GO95 COMM | NOT PROPERLY ATTACHED TO POLE OR ABANDONED EQUIPMENT | GO95 FIBER IMPROPERLY ATTCH/ABANDN | C | Pacific Power Only. California Only. | N/A | N/A | N/A | NO | NO | NO | COMMUNICATIONS | COMMUNICATIONS
107 | GOFIBUN | PP | CA | BOTH | OH | GO95 COMM | UNATTACHED TO POLE WITHIN 15 INCHES | GO95 FIBER UNATTACHED W/IN 15" | B | See Table 1 Case B8 and Rule 84.4D. Need 15 inches to pole centerline. If supply is attached and comm pole is not within ten feet of supply pole, need 22.5 inches. Pacific Power Only. California Only. | N/A | GO95 Table 1 Case B8, Rule 84.4D, Section VIII-47 | N/A | NO | NO | NO | COMMUNICATIONS | COMMUNICATIONS
108 | GOTELCNP | PP | CA | BOTH | OH | GO95 COMM | NOT PROPERLY ATTACHED TO POLE OR ABANDONED EQUIPMENT | GO95 TELCO IMPROPERLY ATTCH/ABANDN | C | Pacific Power Only. California Only. | N/A | N/A | N/A | NO | NO | NO | COMMUNICATIONS | COMMUNICATIONS
109 | GOTELUN | PP | CA | BOTH | OH | GO95 COMM | UNATTACHED TO POLE WITHIN 15 INCHES | GO95 TELCO UNATTACHED W/IN 15" | B | See Table 1 Case B8 and Rule 84.4D. Need 15 inches to pole centerline. If supply is attached and comm pole is not within ten feet of supply pole, need 22.5 inches. Pacific Power Only. California Only. | N/A | GO95 Table 1 Case B8, Rule 84.4D, Section VIII-47 | N/A | NO | NO | NO | COMMUNICATIONS | COMMUNICATIONS
110 | GOTVUN | PP | CA | BOTH | OH | GO95 COMM | UNATTACHED TO POLE WITHIN 15 INCHES | GO95 CATV UNATTACHED W/IN 15" | B | See Table 1 Case B8 and Rule 84.4D. Need 15 inches to pole centerline. If supply is attached and comm pole is not within ten feet of supply pole, need 22.5 inches. Pacific Power Only. California Only. | N/A | GO95 Table 1 Case B8, Rule 84.4D, Section VIII-47 | N/A | NO | NO | NO | COMMUNICATIONS | COMMUNICATIONS
111 | GRD230BK | PP/RMP | ALL | TRANSMISSION | OH | GROUND | TRANSMISSION 230KV AND UP. BROKEN/MISSING GROUND OR INSUFFICIENT NUMBER OF GROUNDS. PROTRUDING NAILS. | GROUND BRK/MSNG 230KV AND HIGHER | A | If shield is present, pole must be grounded. If there's no shield and the metal parts are bonded together, no pole ground is required | N/A | N/A | NESC 092B2 | NO | YES | NO | SINGLEMAN | POWER
112 | GRDBROKE | PP/RMP | ALL | BOTH | OH | GROUND | BROKEN OR MISSING GROUND DISTRIBUTION, AND TRANSMISSION < 230KV | GROUND BRK/MSNG LESS THAN 230KV | A/B | Equipment ground on delta is an "A". Any broken ground less than 8 ft above earth is "A" or can get blown into phase conductor is an "A". Another broken ground is "B" For unigrounds see UNIGROUND. | Policy 009 | GO95 Rule 21.4 | NESC 093D3, 215B | NO | YES | NO | SINGLEMAN | POWER
113 | GRDRODHI | PP/RMP | ALL | BOTH | OH | GROUND | HIGH GROUND ROD | GROUND ROD HIGH | A/B | For PP, "B" if ground rod is not flush with or below the ground level. For RMP, "A" if ground rod is not flush with or below the ground level in high pedestrian traffic area. "B" if not in high pedestrian traffic area. | Policy 009 | GO95 Rule 59.4A(2) | NESC 094B2a(3) | NO | NO | NO | SINGLEMAN | POWER
114 | GRDSHDBK | PP/RMP | ALL | BOTH | OH | GROUND | GROUND BROKEN AT SHIELD WIRE / FIBER OPTIC GROUND | GROUND-BROKEN AT SHIELD WIRE/FIBER | A/B | If ground wire is long enough to get blown into a phase conductor, "A". Otherwise "B". | N/A | N/A | NESC | NO | NO | NO | SINGLEMAN | POWER
115 | GUYBRK | PP/RMP | OR, WA, UT, WY, ID | BOTH | OH | GUY | BROKEN/CORRODED GUY | GUY BROKEN/CORRODED | A/B | "A" if broken, "B" if corroded > 50%. (For CA see GO95GUYB.) | Policy 009 | GO95 Rule 56.2 | NESC 261C2 | NO | YES | NO | SINGLEMAN | POWER
116 | GUYHINS | PP/RMP | ALL | BOTH | OH | GUY | HIGH GUY INSULATOR | GUY INSULATOR HIGH | B | Insulator too high above power to protect public space | Policy 009 | GO95 Rule 56.7C | NESC 215C2 | NO | NO | NO | SINGLEMAN | POWER
117 | GUYLOINS | PP/RMP | ALL | BOTH | OH | GUY | LOW GUY INSULATOR | GUY INSULATOR LOW | B | Bottom of guy insulator less than 8 ft above ground when broken and no ground bond. Refer to Grandfather Matrix. | Policy 009 | GO95 Rule 56.7C | NESC 215c4a | YES | NO | NO | SINGLEMAN | POWER
118 | GUYMARK | PP/RMP | ALL | BOTH | OH | GUY | MISSING/BROKEN GUY MARKER | GUY MARKER MISSING/BROKEN | B/C | Fix at time of inspection (where contract allows). Marker not required if guy is not exposed to pedestrians or traffic and/or is engulfed in dense vegetation or is otherwise inaccessible. Priority B in all states except for CA. Use priority C for CA. | Policy 009 | GO95 56.9 | NESC 217C | NO | NO | NO | SINGLEMAN | POWER
119 | GUYNOINS | PP/RMP | ALL | BOTH | OH | GUY | NO GUY INSULATOR OR NOT EFFECTIVELY GROUNDED | GUY NOT GROUNDED/NO INSULATOR | B | No guy insulator or is not effectively grounded | Policy 009 | N/A | NESC 215C2a & b | NO | NO | NO | SINGLEMAN | POWER
120 | GUYSLACK | PP/RMP | ALL | BOTH | OH | GUY | SLACK GUY | GUY SLACK | A/B | "A" if visibly slack with potential to contact energized facilities or contacting other conductors. "B" if visibly slack in CA. For all other States, “B” if slack and pole is not in proper vertical position. | Policy 009 Section 3.3(d) | GO95 Rule 56.2 | NESC 261A5C & 264A | NO | YES | YES | SINGLEMAN | POWER
121 | GUYTAIL | PP/RMP | ALL | BOTH | OH | GUY | GUY TAIL TOO LONG | GUY TAIL TOO LONG | B | Fix this at the time of inspection (if contract allows), if you can't then use this condition code. | N/A | N/A | NESC | NO | NO | NO | SINGLEMAN | POWER
122 | INSPISSU | PP/RMP | ALL | BOTH | OHUG | INSPECTION ISSUE | CANT INSPECT DUE TO NON-CUSTOMER OBSTRUCTION | INSP ISSUE - NON-CUSTOMER OBSTRUCTION | B | In comments note access issue. No road, impassable, cliff, river, or other natural obstruction. See VEGCANTI and INSPISSU for vegetation and non-customer related obstructions. | Policy 361,298, 298 & 013 | GO95 Rule 31.2 | NESC 121A, NESC 213, NESC 312 | NO | NO | NO | SINGLEMAN | POWER
123 | INSULBRK | PP/RMP | ALL | BOTH | OH | POLE OR CROSS ARM INSULATOR | BROKEN/GUNSHOT INSULATOR | INSULATOR BROKEN/SHOT | A/B/D | If tracking, assign an "A". As per policy reference. | Policy 012 | N/A | NESC 273 | NO | YES | YES | SINGLEMAN | POWER
124 | INSULDMG | PP/RMP | ALL | BOTH | OH | POLE OR CROSS ARM INSULATOR | DAMAGED/LOOSE OR MISSING HARDWARE - DISTRIBUTION OR DISCOLORATION OR OTHER DAMAGE | INSULATOR DAMAGE/LOOSE/MSSNG EQUIP | A/B/D | If damaged, per Insulator Policy 012. | Policy 012 | N/A | NESC 261H2 | NO | YES | YES | SINGLEMAN | POWER
125 | INSULDRT | RMP | UT, WY, ID | BOTH | OH | POLE OR CROSS ARM INSULATOR | INSULATOR CONTAMINATED OR DIRTY | INSULATOR DIRTY/CONTAMINATED | D | RMP Only | Policy 012 | N/A | N/A | NO | NO | NO | SINGLEMAN | POWER
126 | INSULPLM | PP/RMP | ALL | BOTH | OH | POLE OR CROSS ARM INSULATOR | INSULATOR (NOT SUSPENSION) NEEDS REPOSITIONED | INSULATOR NEEDS REPOSITIONING | A/B | "A" is insulator out of lead/alignment (twisting force on insulator) by more than 2". "B" is out of alignment <2" and >0". Not applicable to suspension insulators. | N/A | N/A | NESC 277 | NO | YES | YES | SINGLEMAN | POWER
127 | IRSPOTOH | PP/RMP | ALL | BOTH | OH | INFRARED CONDITION | DIST OR TRANS IR CONDITION | DIST OR TRANS IR CONDITION | A/B | “A” for rise temperatures greater than or equal to 64°F. “B” for rise temperatures between 19°F and 63°F. Send images and report to Asset Management. | Policy 358 | N/A | N/A | NO | YES | NO | SINGLEMAN | POWER
128 | IRSPOTUG | PP/RMP | ALL | BOTH | UG | INFRARED CONDITION | DIST OR TRANS IR CONDITION | DIST OR TRANS IR CONDITION | D | Information only to support record keeping or other programs. Input temperature reading observations (°F or °C) in comments e.g. "target equipment is 100°F vs target reference equipment is 50°F" or "target temp is 100°F vs ambient is 40°F). Send images and report to management. | N/A | N/A | N/A | NO | NO | NO | SINGLEMAN | POWER
129 | LATANODE | PP/RMP | ALL | TRANSMISSION | OH | LATTICE STRUCTURE ISSUE | ANODE CONNECTION ISSUE | LATTICE STRC-ANODE CONNECTION | B |  | N/A | N/A | N/A | NO | NO | NO | SINGLEMAN | POWER
130 | LATBNTMB | PP/RMP | ALL | TRANSMISSION | OH | LATTICE STRUCTURE ISSUE | BENT MEMBER | LATTICE STRC-BENT MEMBER | B |  | N/A | N/A | N/A | NO | NO | NO | SINGLEMAN | POWER
131 | LATCOR | PP/RMP | ALL | TRANSMISSION | OH | LATTICE STRUCTURE ISSUE | EXCESSIVE CORROSION | LATTICE STRC-EXCESSIVE CORROSION | B |  | N/A | N/A | N/A | NO | NO | NO | SINGLEMAN | POWER
132 | LATHWARE | PP/RMP | ALL | TRANSMISSION | OH | LATTICE STRUCTURE ISSUE | MISSING / LOOSE BOLTS / HARDWARE | LATTICE STRC-MISSING BOLTS/HDWARE | A/B | If jeopardizing structural integrity, "A". | N/A | N/A | N/A | NO | NO | NO | SINGLEMAN | POWER
133 | LATMISMB | PP/RMP | ALL | TRANSMISSION | OH | LATTICE STRUCTURE ISSUE | MISSING MEMBERS | LATTICE STRC-MISSING MEMBERS | A/B | If jeopardizing structural integrity, "A". | N/A | N/A | N/A | NO | NO | NO | SINGLEMAN | POWER
134 | LIGHT | PP/RMP | ALL | BOTH | OH | LIGHT | DAMAGED/LOOSE HARDWARE | LIGHT - DAMAGED/LOOSE HARDWARE | A/B | "A" if light hanging from pole or if conduit access in public space, "B" if lens cover open | N/A | N/A | NESC Rule 012C | NO | NO | NO | SINGLEMAN | POWER
135 | LWCATV | PP/RMP | ALL | BOTH | OH | CATV CONDITION | ONE OR MORE LASHING WIRES ARE BROKEN OR LOOSE ON THE CABLE TELEVISION LINE | LASHING WIRE - CATV | A | Broken or loose lashing wire is always an "A" priority condition | N/A | N/A | NESC Rule 012C | NO | YES | NO | COMMUNICATIONS | COMMUNICATIONS
136 | LWFIBER | PP/RMP | ALL | BOTH | OH | FIBER CONDITION | ONE OR MORE LASHING WIRES ARE BROKEN OR LOOSE ON THE FIBER OPTIC LINE | LASHING WIRE - FIBER | A | Broken or loose lashing wire is always an "A" priority condition | N/A | N/A | NESC Rule 012C | NO | YES | NO | COMMUNICATIONS | COMMUNICATIONS
137 | LWPAPS | PP/RMP | ALL | DISTRIBUTION | OH | CONDUCTOR | ONE OR MORE LASHING WIRES ARE BROKEN OR LOOSE ON THE SECONDARY PAPS (PARLEY) CABLE. | BROKEN LASHING WIRE ON SECONDARY PARLEY CABLE | A | Broken lashing wire is an "A" priority | N/A | N/A | N/A | NO | YES | NO | 3 MAN | POWER
138 | LWTELCO | PP/RMP | ALL | BOTH | OH | TELCO CONDITION | ONE OR MORE LASHING WIRES ARE BROKEN OR LOOSE ON THE TELEPHONE LINE | LASHING WIRE - TELCO | A | Broken or loose lashing wire is always an "A" priority condition | N/A | N/A | NESC Rule 012C | NO | YES | NO | COMMUNICATIONS | COMMUNICATIONS
139 | PADCRETE | PP/RMP | ALL | BOTH | UG | UG PAD / VAULT | DAMAGED FIBERCRETE PAD / SPALLING OR CRACKING | PAD-DAMAGED/SPALLING/CRACKING | A/B | Cracked/spalling Fibercrete around padmount equip or hole with exposed access is "A". Localized cracks/spalling or hole without access is "B". | N/A | GO128 Rule 32.3 | NESC Rule 380C | NO | NO | NO | SINGLEMAN | POWER
140 | PADINSUL | PP/RMP | ALL | BOTH | UG | UG PAD / VAULT | CRACKED OR BROKEN INSULATOR IN SWITCHGEAR | PAD-INSULATOR IN SWITCHGEAR BROKEN | A | "A" is broken or cracked | N/A | N/A | NESC Rule 012C, 312, 313A | NO | NO | NO | SINGLEMAN | POWER
141 | PADREPOS | PP/RMP | ALL | BOTH | UG | UG PAD / VAULT | REPOSITION EQUIPMENT ON PAD AND/OR REPLACE EQUIPMENT OR NEEDS FILL | PAD-REPOSITION/REPLACE EQUIPMENT | A/B | Exposed with access to wires/live equipment is "A", otherwise not a condition. If slid on pad but no access B | N/A | GO128 34.3 | NESC Rule 321B, 381G | NO | NO | NO | SINGLEMAN | POWER
142 | POLABR | PP/RMP | ALL | BOTH | OH | POLE | POLE THAT HAS BEEN MECHANICALLY DAMAGED (NOT SUFFICIENTLY TO BE REPLACED), GENERALLY SCRAPED BY A TRUCK OR OTHER VEHICLE. | POLE-ABRADED BY VEHICLE | D | This is to be able to pull reports for information | N/A | N/A | N/A | NO | NO | NO | SINGLEMAN | POWER
143 | POLANCRD | PP/RMP | ALL | BOTH | OH | OTHER CONDITION | POLE/ANCHOR SET IN CURB / ROADWAY | POLE-ANCHOR SET IN CURB/ROADWAY | B |  | N/A | N/A | NESC 231B | NO | NO | NO | SINGLEMAN | POWER
144 | POLEDERP | PP/RMP | ALL | BOTH | OH | POLE | DECAY REJECT REPLACE | POLE-DECAY/REJECT/REPLACE | A/B | As per relative policy reference. | Per Policy 013, or 298 (CA), or 299 (OR) | N/A | NESC 261A2a | NO | YES | YES | ESTIMATOR | POWER
145 | POLEDMRS | PP/RMP | ALL | BOTH | OH | POLE | DAMAGE REJECT RESTORE | POLE-DAMAGE/REJECT/RESTORE | A/B | As per relative policy reference. | Per Policy 013, or 298 (CA), or 299 (OR) | N/A | NESC 261A2a | NO | YES | YES | ESTIMATOR | POWER
146 | POLEREPL | PP/RMP | ALL | BOTH | OH | POLE | DAMAGE REJECT REPLACE | POLE-DAMAGE/REJECT/REPLACE | A/B | As per relative policy reference. | Per Policy 013, or 298 (CA), or 299 (OR) | N/A | NESC 261A2a | NO | YES | YES | ESTIMATOR | POWER
147 | POLEREST | PP/RMP | ALL | BOTH | OH | POLE | DECAY REJECT RESTORE | POLE-DECAY/REJECT/RESTORE | A/B | As per relative policy reference. | Per Policy 013, or 298 (CA), or 299 (OR) | N/A | NESC Rule 012C | NO | YES | YES | ESTIMATOR | POWER
148 | POLESTEP | PP/RMP | ALL | BOTH | OH | POLE | POLE STEP LESS THAN 8 FT ABOVE GROUND | POLE-STEP <8 FEET ABOVE GROUND | B | Does not apply to isolated or otherwise inaccessible structures. Inspector corrects on the spot when possible. | N/A | 91.3-C | NESC 217A2b | NO | NO | NO | SINGLEMAN | POWER
149 | POLETOP | PP/RMP | ALL | BOTH | OH | POLE | ROTTED/SPLIT/FEATHERED POLE TOP | POLE-TOP FEATHERED/ROTTED/SPLIT | A/B/D | If feathered top impacts ridge pin, cross arm or other supply issue then "A". "B" if severe but not creating issues as noted in "A" condition. "D" if condition is not severe but needs monitored. Priority D is RMP only. | Per Policy 013, or 298 (CA), or 299 (OR) | N/A | NESC 261A2 | NO | YES | YES | SINGLEMAN | POWER
150 | POLISSUE | PP/RMP | ALL | BOTH | OH | POLE | TRACKING ON POLE | TRACKING ON POLE | A/B | "A" If severe. "B" If moderate. | N/A | N/A | NESC 261A | NO | NO | NO | SINGLEMAN | POWER
151 | POLTOPSW | PP/RMP | ALL | BOTH | OH | POLE TOP SWITCH | DAMAGED OR SEVERELY CORRODED CONNECTION | DAMAGED OR SEVERELY CORRODED CONNECTION | A/B | If actively tracking "A". Non-operable or other issues "B". | N/A | N/A | NESC Rule 012C | NO | YES | YES | SINGLEMAN | POWER
152 | POLVIS | PP/RMP | ALL | BOTH | OH | POLE | THIS IS A STRUCTURE THAT IS LESS THAN 4 FEET OF THE CURB OR ROAD EDGE AND DOES NOT HAVE ANY VISIBILITY STRIPING OR OTHER PROTECTIVE-TYPE BARRIER | POLE-VIS. STRIPE/BARRIER MISSING | D | This is to be able to pull reports for information | N/A | N/A | N/A | NO | NO | NO | SINGLEMAN | POWER
153 | PRITERM | RMP | UT, WY, ID | DISTRIBUTION | OH | TERMINATION | DAMAGED TERMINATION ON UNDERGROUND RISER OR DIP POLES | TERMINATION CONNECTION ISSUE | A | "A" if termination is damaged. | N/A | N/A | N/A | NO | NO | YES | 3 MAN | POWER
154 | RECLDMGL | PP/RMP | ALL | BOTH | OH | RECLOSER | EQUIP DAMAGED/LOOSE | RECLOSER EQUIPMENT DAMAGED/LOOSE | B |  | Policy 009 | N/A | NESC Rule 012C | NO | YES | YES | SINGLEMAN | POWER
155 | REGDMGL | PP/RMP | ALL | BOTH | OH | REGULATOR | EQUIP DAMAGED/LOOSE | REGULATOR EQUIPMENT DAMAGED LOOSE | B |  | Policy 009 | N/A | NESC Rule 012C | NO | YES | YES | SINGLEMAN | POWER
156 | RISEBKSP | PP/RMP | ALL | BOTH | OH | RISER | BROKEN CONDUIT/JOINT SEPARATED OR IDLE RISER | RISER BRKN/SEPARATED CONDUIT/JOINT | A/B | "A" if below 8 ft. "B" if above 8 ft. Idle riser only "A" condition if conductor is accessible to the public. | N/A | GO96 54.6-D2-5, 54.6-E | NESC RULE 362A | NO | NO | NO | SINGLEMAN | POWER
157 | RISECLMB | PP/RMP | ALL | BOTH | OH | RISER | CLIMBABLE | RISER CLIMBABLE | A/B | "A" if climbable into primary/neutral/open secondary. | N/A | N/A | NESC 217A2 | NO | NO | NO | SINGLEMAN | POWER
158 | RISEGRD | PP/RMP | ALL | BOTH | OH | RISER | MISSING GROUNDING STRAP | RISER GROUND STRAP MISSING (STEEL) | B | Newer installs have grounding sticker. | N/A | GO95 Rule 54.6E(1) | NESC Rule 314B | NO | NO | NO | SINGLEMAN | POWER
159 | RISESTRP | PP/RMP | ALL | BOTH | OH | RISER | MISSING/BROKEN CONDUIT STRAPS | RISER MISSING/BRK CONDUIT STRAPS | A/B | Primary conduit not secured to pole = "A". Secondary conduit not secured to pole = "B". | N/A | N/A | NESC Rule 361B | NO | NO | NO | SINGLEMAN | POWER
160 | SECENC | PP/RMP | ALL | DISTRIBUTION | UG | SECONDARY ENCLOSURE | BROKEN BOX/PEDESTAL | SECONDARY ENCL BROKEN BOX/PEDESTAL | A | Possible access to interior, exposed wire or unable to secure. | N/A | GO128 Rule 34.3-C | NESC Rule 323D, 381G1 | NO | NO | NO | SINGLEMAN | POWER
161 | SECFRAY | PP/RMP | ALL | DISTRIBUTION | OH | CONDUCTOR | DAMAGED/FRAYED SECONDARY CONDUCTOR | SECONDARY ISSUE | A/B | Dependent on degree of damage, > 50% of conductor strands cut = "A". If more than surface strands damaged, "B" | N/A | N/A | NESC Rule 261H1 & 012C | NO | YES | NO | SINGLEMAN | POWER
162 | SECPAPS | RMP | UT, WY, ID | BOTH | OH | CONDUCTOR | WHITE-GRAY PAPS SECONDARY CABLE | SECONDARY CABLE WHITE-GRAY PAPS | D | For information only. RMP Only. | N/A | N/A | N/A | NO | NO | NO | ESTIMATOR | POWER
163 | SPLICE | RMP | UT, WY, ID | BOTH | OH | DOCUMENTATION | SPLICE ON OH CONDUCTOR | SPLICE ON OH CONDUCTOR | D | Information only to support record keeping or other programs. RMP Only | N/A | N/A | N/A | NO | NO | NO | SINGLEMAN | POWER
164 | STUBCUST | PP | OR | BOTH | OH | POLE STUB ISSUE | BARE POLE - CUSTOMER USE - BILL OF SALE | STUB-CUST USE-BILL OF SALE | B | For Oregon only. PP Only. | N/A | N/A | NESC Rule 214B3 | NO | NO | NO | SINGLEMAN | POWER
165 | STUBO2 | PP/RMP | OR, WA, UT, WY, ID | BOTH | OH | POLE STUB ISSUE | BARE POLE REMOVE STUB, OVER 2 FT TALL | STUB-REMOVE-OVER 2 FEET TALL | B | For CA see GO95STUB | N/A | N/A | NESC 214B3 | NO | NO | NO | SINGLEMAN | POWER
166 | STUBU2 | PP/RMP | OR, WA, UT, WY, ID | BOTH | OH | POLE STUB ISSUE | BARE POLE REMOVE STUB, UNDER 2 FT TALL | STUB-REMOVE-UNDER 2 FEET TALL | A/B | "A" = publicly accessible, cut off AND hollowed out. "B" = cut off at or below ground level. For CA see GO95STUB | N/A | N/A | NESC Rule 214B3 | NO | NO | NO | SINGLEMAN | POWER
167 | SUPPLYCO | PP/RMP | ALL | BOTH | OH | POWER COMPANY CONDITION | THIS IS A CONDITION THAT IS REASSIGNED TO POWER RESPONSIBILITY THAT IS NOT RELATED TO A COMMUNICATIONS CONDITION | SUPPLYCO-POWER CONDITION NOT COMM | A/B |  | N/A | N/A | N/A | NO | NO | NO | SINGLEMAN | POWER
168 | SVCCOMMD | PP/RMP | ALL | BOTH | OH | CLEARANCE CONDITION | CLEARANCE OF SERVICE POLE-TO-WEATHERHEAD OVER COMMERCIAL DRIVEWAY | SVC CLR TO WHD OVER CMRCL DVWY | A/B | See Clearance Table Less than 80% is "A". From 80% to 99.9% is "B". | N/A | GO95 Rule 54.8B(2)(a) | NESC Table 232-2 | YES | NO | NO | SINGLEMAN | POWER
169 | SVCCUSTW | PP | OR | DISTRIBUTION | OH | CLEARANCE CONDITION | CLEARANCE OF SERVICE OVER YARD CUSTOMER WIRE | SVC CLEARANCE OVER YARD-CUST WIRE | A/B | Can be guarded with customer involvement. Less than 8 feet of clearance is "A". Between 8 feet and required clearance is "B". | Policy No. 336 | N/A | N/A | YES | NO | NO | SINGLEMAN | POWER
170 | SVCDECK | PP/RMP | ALL | BOTH | OH | CLEARANCE CONDITION | CLEARANCE OF SERVICE TO DECK | SVC CLEARANCE OVER DECK | A/B | If service or weatherhead is reachable horizontally less than 2 feet is "A", between 2 to 5 feet is "B". Vertical clearance: less than 8 feet from surface of deck is "A", from 8 feet to required clearance is "B". | N/A | N/A | NESC Rule 234C3d(3), NESC Rule 234C3d(1) | YES | NO | NO | SINGLEMAN | POWER
171 | SVCDEFLC | PP | OR, CA | BOTH | OH | VEGETATION | SERVICE WIRE DEFLECTED BY VEGETATION | SVC DEFLECTED BY VEGETATION | B | Only Oregon or California when deflecting. This is not a condition if already guarded at the point of deflection. | OAR 860-024-016(6) | GO95 Rule 35 | N/A | NO | NO | NO | SINGLEMAN | POWER
172 | SVCDRIVE | PP/RMP | ALL | BOTH | OH | CLEARANCE CONDITION | CLEARANCE OF SERVICE OVER DRIVEWAY | SVC DRIVEWAY CLEARANCE CONDITION | A/B | Less than 8 feet of clearance is "A". From 8 feet to required clearance is "B". | See "CLEARANCE" and "GRANDFATHERING MATRIX" tabs in this procedure for details. Policy 305 | GO95 Rule 54.8B(2)(b) | NESC Rule 232B1, Table 232-1 | YES | NO | NO | SINGLEMAN | POWER
173 | SVCENTBK | PP/RMP | ALL | BOTH | OH | SERVICE ENTRANCE | HOUSE KNOB PULLED OUT, OR BROKEN SERVICE GRIP OR ATTACHMENT | SVC ENTRANCE-BRKN GRIP/ATTACHMENT | A/B | "A" if conductor connectors are under tension. Otherwise "B". | N/A | N/A | NESC Rule 234C3c | NO | NO | NO | SINGLEMAN | POWER
174 | SVCENTCO | PP/RMP | ALL | BOTH | OH | SERVICE ENTRANCE | BARE CONNECTORS AT WEATHER HEAD | SVC ENT BARE CONNECTOR AT WHD | A/B | If readily accessible, "A". If accessible from roof, window, etc, "B". | Standards ET312 and DE531 | N/A | NESC Rule 234C3a | NO | NO | NO | SINGLEMAN | POWER
175 | SVCGUARD | PP | OR | DISTRIBUTION | OH | CLEARANCE CONDITION | CLEARANCE OF SVC OVER YARD GUARD | CLEARANCE OF SVC OVER YARD GUARD | A/B | OREGON ONLY: Guarding PacifiCorp wire will correct condition. Less than 8 feet of clearance is "A". Between 8 feet and required clearance is "B". | Policy 336 | N/A | NESC Rule 232B1, Table 232-1 | YES | NO | NO | SINGLEMAN | POWER
176 | SVCNEUT | PP/RMP | ALL | BOTH | OH | CLEARANCE CONDITION | SERVICE TOUCHING NEUTRAL | SVC TOUCHING NEUTRAL | B |  | N/A | N/A | N/A | NO | NO | NO | SINGLEMAN | POWER
177 | SVCPOA | PP | OR | DISTRIBUTION | OH | CLEARANCE CONDITION | CLEARANCE OF SERVICE OVER YARD POINT OF ATTACHMENT | SVC CLR YARD POA | A/B | Can be raised to 10 feet without customer involvement. Less than 8 feet of clearance is "A". Between 8 feet and required clearance is "B". | Policy 336 | N/A | NESC Rule 232B1, Table 232-1 | YES | NO | NO | SINGLEMAN | POWER
178 | SVCPOACU | PP | OR | DISTRIBUTION | OH | CLEARANCE CONDITION | CLEARANCE OF SERVICE OVER YARD CUSTOMER POINT OF ATTACHMENT | SVC CLR YARD CUSTOMER POA | A/B | Can be raised to 10 feet with customer involvement. Less than 8 feet of clearance is "A". Between 8 feet and required clearance is "B". | Policy 336 | N/A | NESC Rule 232B1, Table 232-1 | YES | NO | NO | SINGLEMAN | POWER
179 | SVCPOAGU | PP | OR | DISTRIBUTION | OH | CLEARANCE CONDITION | CLEARANCE OF SVC OVER YARD | CLEARANCE OF SVC OVER YARD | A/B | OREGON ONLY: Can be corrected by both raising to 10 feet without customer involvement and guarding. Less than 8 feet of clearance is "A". Between 8 feet and required clearance is "B". | Policy 336 | N/A | NESC Rule 232B1, Table 232-1 | YES | NO | NO | SINGLEMAN | POWER
180 | SVCPOOL | PP/RMP | ALL | BOTH | OH | CLEARANCE CONDITION | SERVICE CLEARANCE OVER POOL, HOT TUB | SVC POOL/HOT TUB CLEARANCE | A | GO95 clearances in California. NESC in other states. This is for permanently installed above or in ground pool or hot tub | N/A | GO95 Rule 54.4-A3 | NESC Rule 234E, Table 234-3 | YES | NO | NO | SINGLEMAN | POWER
181 | SVCROAD | PP/RMP | ALL | BOTH | OH | CLEARANCE CONDITION | CLEARANCE OF SERVICE OVER ROADWAY OR POLE-TO-POLE OVER COMMERCIAL DRIVEWAY | SVC ROAD/POLE2POLE OVER CMRCL.DVWY | A/B/D | See Clearance Table. Less than 80% is "A". From 80% to 99.9% is "B". Road xing direct to point of service November thru February, 16'-17' is "D". | N/A | GO95 Rule 54.8B(1) | NESC Rule 232B1, Table 232-1 | YES | NO | NO | SINGLEMAN | POWER
182 | SVCROOF | PP/RMP | ALL | BOTH | OH | CLEARANCE CONDITION | SERVICE TOO LOW OVER ROOF | SVC ROOF CLEARANCE | B | See grandfathering matrix, if it does not meet the requirements it's a B | N/A | GO95 Rule 54.8-B4a | NESC Rule 234C3d(1)b | NO | NO | NO | SINGLEMAN | POWER
183 | SVCRR | PP/RMP | ALL | BOTH | OH | CLEARANCE CONDITION | CLEARANCE TO RAILROAD (HORIZONTAL/VERTICAL) | CLEARANCE TO RAILROAD (HORIZ/VERTICAL) | A/B | Refer to PacifiCorp's Inspection Clearance Table | N/A | GO95 Rule 54.8, Table 1 | NESC Rule 232B1, Table 232-1 | YES | NO | NO | SINGLEMAN | POWER
184 | SVCRUBCM | PP/RMP | ALL | BOTH | OH | CLEARANCE CONDITION | SERVICE RUBBING COMM | SVC RUBBING COMMUNICATION WIRE | A |  | N/A | N/A | NESC Rule 235C1, Exception 3 | NO | NO | NO | SINGLEMAN | POWER
185 | SVCRUBLG | PP/RMP | ALL | BOTH | OH | CLEARANCE CONDITION | SERVICE RUBBING HOUSE/ BUILDING | SVC RUBBING HOUSE/BUILDING | B |  | N/A | N/A | NESC Rule 234C3c | NO | NO | NO | SINGLEMAN | POWER
186 | SVCSVC | PP/RMP | ALL | BOTH | OH | CLEARANCE CONDITION | CLEARANCE TO ADJOINING SERVICE | CLEARANCE TO ADJOINING SERVICE | B | Service rubbing on another service. | N/A | GO95 Rule 54.10C(6) | NESC Rule 233C1, Table 233-1 | NO | NO | NO | SINGLEMAN | POWER
187 | SVCTREE | PP/RMP | ALL | BOTH | OH | DOCUMENTATION | SERVICE WIRE SUPPORTED BY A TREE (TREE POLE) | SERVICE WIRE SUPPORTED BY A TREE | D | No differentiator as only a 'D' condition is allowed | N/A | N/A | NESC 217B | NO | NO | NO | SINGLEMAN | POWER
188 | SVCWH | PP | OR | BOTH | OH | SERVICE CLEARANCE-POWER | LOW WEATHERHEAD CLEARANCE | LOW WEATHERHEAD CLEARANCE | A/B | OREGON ONLY-A priority if weatherhead below 8', B priority if weatherhead between 8' and 10' | Policy 336 | N/A | NESC Rule 232B1, Table 232-1 | NO | NO | NO | SINGLEMAN | POWER
189 | SVCWIND | PP/RMP | ALL | BOTH | OH | CLEARANCE CONDITION | SERVICE TOO CLOSE TO WINDOW / SIGN | SVC WINDOW CLEARANCE | B |  | N/A | GO95 54.8B4 | NESC Rule 234C2, Table 234-1 | NO | NO | NO | SINGLEMAN | POWER
190 | SVCYARD | PP/RMP | ALL | DISTRIBUTION | OH | CLEARANCE CONDITION | CLR OF SVC OVER YARD | CLR OF SVC OVER YARD | A/B | Less than 8 feet of clearance is "A". Between 8 feet and required clearance is "B". | Policy 336 | N/A | NESC Rule 232B1, Table 232-1 | YES | NO | NO | SINGLEMAN | POWER
191 | TRECATV | PP/RMP | ALL | BOTH | OH | CATV TREE ISSUE | TREE LIMB DEFLECTING CATV LINE CAUSE STRAIN ON POLE OR SUPPLY LINE(S) | TREE DEFLECT TV LINE | B |  | N/A | N/A | N/A | NO | NO | NO | COMMUNICATIONS | COMMUNICATIONS
192 | TREDIST | PP/RMP | ALL | DISTRIBUTION | OH | VEGETATION | DISTRIBUTION - TREE CONTACTING PRIMARY | DISTRIBUTION - TREE CONTACTING PRIMARY | A / D | Priority D is RMP only. | N/A | N/A | NESC Rule 218A1 | NO | YES | YES | SINGLEMAN | POWER
193 | TREECLMB | PP/RMP | ALL | BOTH | OH | VEGETATION | CLIMBABLE TREE TO PRIMARY | TREE CLIMBABLE | A |  | 860-024-0016 | N/A | NESC Rule 217A2a & 214A5 | NO | NO | NO | SINGLEMAN | POWER
194 | TREFIBER | PP/RMP | ALL | BOTH | OH | FIBER TREE ISSUE | TREE LIMB DEFLECTING FIBER LINE CAUSE STRAIN ON POLE OR SUPPLY LINE(S) | TREE DEFLECT FIBER LINE | B |  | N/A | N/A | N/A | NO | NO | NO | COMMUNICATIONS | COMMUNICATIONS
195 | TRESCBRN | PP/RMP | ALL | BOTH | OH | VEGETATION | TREE CONTACTING OPEN (BARE CONDUCTOR) SECONDARY | TREE CONTACTING OPEN SECONDARY | A / D | Priority D is RMP only. | 860-024-0016 | N/A | NESC Rule 218A1 & 218A2 | NO | YES | NO | SINGLEMAN | POWER
196 | TRESEC | PP/RMP | ALL | BOTH | OH | VEGETATION | TREE LIMB SEVERELY DEFLECTING SECONDARY SUPPLY (NON-BARE) LINE CAUSE STRAIN ON POLE OR ABRASION OF SECONDARY/SERVICE SUPPLY LINE(S) | SVC SEVERELY DEFLECTED/ABRADED BY VEGETATION | A | Tree Limb Severely Deflecting Secondary Supply (Non-Bare) Line Cause Strain On Pole Or Abrasion Of Secondary/Service Supply Line(S). PP Only If Severe Or Abraded. | N/A | N/A | N/A | NO | YES | NO | SINGLEMAN | POWER
197 | TRETELCO | PP/RMP | ALL | BOTH | OH | TELCO TREE ISSUE | TREE LIMB DEFLECTING TELCO LINE CAUSE STRAIN ON POLE OR SUPPLY LINE(S) | TREE DEFLECT TELCO LINE | B |  | N/A | N/A | N/A | NO | NO | NO | COMMUNICATIONS | COMMUNICATIONS
198 | TRETRBRN | PP/RMP | ALL | TRANSMISSION | OH | VEGETATION | TRANSMISSION - TREE CONTACTING LINE | TRANSMISSION - TREE CONTACTING LINE | A / D | Priority D is RMP only. | N/A | N/A | N/A | NO | YES | YES | SINGLEMAN | POWER
199 | TRETRCLR | PP/RMP | ALL | TRANSMISSION | OH | VEGETATION | TRANSMISSION - TREE CLEARANCE | TREE TO TRANSMISSION CLEARANCE | A / D | Priority D is RMP only. | N/A | N/A | N/A | NO | YES | NO | SINGLEMAN | POWER
200 | TRNCGRND | PP/RMP | ALL | TRANSMISSION | OH | TRANSMISSION GROUND CLEARANCE ISSUE | CLEARANCE TO GROUND | TRANSM GROUND CLEARANCE ISSUE | A/B | "A"-priority. Engineering to evaluate. "B"-priority if so determined by engineering evaluation. | N/A | N/A | N/A | NO | YES | NO | SINGLEMAN | POWER
201 | TRNCHOOK | PP/RMP | ALL | TRANSMISSION | OH | TRANSMISSION HARDWARE | DAMAGED/LOOSE C-HOOK OR PHASE FITTING | TRANSMISSION DAMAGED C-HOOK OR PHASE FITTING | A | "A" if visible wear on c-hook or phase fitting. | N/A | N/A | N/A | NO | YES | YES | ESTIMATOR | POWER
202 | TRNCLOW | PP/RMP | ALL | TRANSMISSION | OH | TRANSMISSION SAG | LOW SAG | TRANSMISSION LOW SAG ISSUE | A/B | "A"-priority. Engineering to evaluate. "B"-priority if so determined by engineering evaluation. | N/A | N/A | N/A | NO | NO | NO | SINGLEMAN | POWER
203 | TRNCON | PP/RMP | ALL | TRANSMISSION | OH | TRANSMISSION ENCROACHMENT | CONSTRUCTION/BUILDING/LANDSCAPING/ BACKFILL | TRANSMISSION ENCROACHMENT | A/B | "A"-priority if nonconforming to NESC/GO95. "B"-priority if blocking access or infringes on right of way. | N/A | N/A | N/A | NO | NO | NO | SINGLEMAN | POWER
204 | TRNCSAG | PP/RMP | ALL | TRANSMISSION | OH | TRANSMISSION SAG | UNEVEN SAG | TRANSMISSION UNEVEN SAG ISSUE | A/B | "A"-priority. Engineering to evaluate. "B"-priority if so determined by engineering evaluation. | N/A | N/A | N/A | NO | NO | NO | SINGLEMAN | POWER
205 | TRNSATT | PP/RMP | ALL | TRANSMISSION | OH | TRANSMISSION HARDWARE | LOOSE INSULATOR ATTACHMENT HARDWARE | TRANS LOOSE INSULATOR ATTACHMENT | A | Severe is "A". | N/A | N/A | N/A | NO | YES | NO | SINGLEMAN | POWER
206 | TRNSBOND | PP/RMP | ALL | TRANSMISSION | OH | TRANSMISSION HARDWARE | HARDWARE NOT BONDED | TRANS HARDWARE NOT BONDED | B | Hardware to hardware or hardware to ground per Construction Standards. | N/A | N/A | N/A | NO | YES | NO | SINGLEMAN | POWER
207 | TRNSBRAC | PP/RMP | ALL | TRANSMISSION | OH | TRANSMISSION HARDWARE | LOOSE X-BRACE ATTACHMENT HARDWARE | TRANS-LOOSE XBRACE ATTACHMENT | A | Severe is "A". | N/A | N/A | N/A | NO | YES | NO | SINGLEMAN | POWER
208 | TRNSCENT | PP/RMP | ALL | TRANSMISSION | OH | TRANSMISSION HARDWARE | LOOSE/MISSING X-BRACE CENTER CLAMP/NUT | TRANS-LOOSE/MISSING XBRACE CTR NUT | A | Missing is "A". Loose is "B". | N/A | N/A | N/A | NO | YES | NO | SINGLEMAN | POWER
209 | TRNSDAMP | PP/RMP | ALL | TRANSMISSION | OH | TRANSMISSION HARDWARE | DAMPER MISSING/DAMAGED/SLIPPED | TRANS-DAMPER MISSING/DMG/SLIPPED | A/B | Missing, damaged, or slipped damper. 10' or greater from the shoe or hanging over public area is an "A", otherwise it's a "B". | N/A | N/A | N/A | NO | YES | NO | SINGLEMAN | POWER
210 | TRNSGVLT | PP/RMP | OR, WA, UT, WY, ID | TRANSMISSION | OH | MARKING / SIGN | TRANSMISSION TOWER HIGH VOLTAGE SIGN FADED/MISSING | TRANS-HIGH VOLTAGE SIGN FADED/MISSING | B | For California see GO95HV | N/A | N/A | N/A | NO | NO | NO | SINGLEMAN | POWER
211 | TRNSKEY | PP/RMP | ALL | TRANSMISSION | OH | TRANSMISSION HARDWARE | MISSING/WEAK COTTER KEY | TRANS-COTTER KEY MISSING/WEAK | A/B | Missing is "A". Weak/deteriorated is "B". | N/A | N/A | N/A | NO | YES | NO | SINGLEMAN | POWER
212 | TRNSLOOS | PP/RMP | ALL | TRANSMISSION | OH | TRANSMISSION HARDWARE | HARDWARE LOOSE | TRANS-HARDWARE LOOSE | A/B | "A" if missing nuts. "B" if loose nuts. Expanded coil washer and vertical clothes pin washer are not a condition. Phase raiser covers loose or with long bolts are "B". | N/A | N/A | N/A | NO | YES | NO | SINGLEMAN | POWER
213 | TRNSNUTS | PP/RMP | ALL | TRANSMISSION | OH | TRANSMISSION HARDWARE | MISSING NUTS | TRANS-MISSING NUTS | A/B | If jeopardizing structural integrity, "A". Otherwise "B". Missing lock nut alone not a condition. | N/A | N/A | N/A | NO | YES | NO | SINGLEMAN | POWER
214 | TRNSOIL | PP/RMP | ALL | TRANSMISSION | OH | TRANSMISSION ENCROACHMENT | SOIL MOVEMENT | TRANS-SOIL ENCROACHMENT | A/D | "A"-priority if jeopardizing structural integrity. Otherwise "D" priority RMP only. | N/A | N/A | N/A | NO | YES | NO | SINGLEMAN | POWER
215 | TRNSPIN | PP/RMP | ALL | TRANSMISSION | OH | TRANSMISSION HARDWARE | PIN FALLING OUT | TRANS-PIN FALLING OUT | A/B | Severe is "A". Loose is "B". | N/A | N/A | N/A | NO | YES | NO | SINGLEMAN | POWER
216 | TRNSSIGN | PP/RMP | ALL | TRANSMISSION | OH | MARKING / SIGN | MISSING TRANSMISSION LINE INTERSECTION AERIAL IDENTIFICATION SIGN | TRANS-LINE INTERSECTN SIGN MISSING | A/B | "A" in RMP. "B" in PP. (Not an NESC condition.) | N/A | N/A | N/A | NO | NO | NO | SINGLEMAN | POWER
217 | UBBRACE | PP/RMP | ALL | DISTRIBUTION | OH | UNDERBUILD PROBLEM | DISTRIBUTION CROSS ARM | UNDERBUILD-CROSS ARM | A/B | "B" if cross brace broken, missing or hanging loose on distribution. "A" on transmission cross arm. | N/A | N/A | NESC Rule 252 & 012C | NO | YES | YES | SINGLEMAN | POWER
218 | UBPBANC | PP/RMP | ALL | DISTRIBUTION | OH | UNDERBUILD PROBLEM | DISTRIBUTION ANCHOR ISSUE | UNDERBUILD-DISTRIBUTION ANCHOR | A/B | Pulled or corrosive distribution anchor | N/A | N/A | NESC Rule 012C | NO | YES | NO | SINGLEMAN | POWER
219 | UBPBCOND | PP/RMP | ALL | DISTRIBUTION | OH | UNDERBUILD PROBLEM | DISTRIBUTION CONDUCTOR ISSUE | UNDERBUILD-DISTRIBUTION CONDUCTOR | A/B | Distribution conductor issue | N/A | N/A | N/A | NO | YES | YES | SINGLEMAN | POWER
220 | UBPBCTGD | PP/RMP | ALL | DISTRIBUTION | OH | UNDERBUILD PROBLEM | BROKEN/CUT GROUND | UNDERBUILD-GROUND BROKEN/CUT | A/B | Equipment ground on delta is an "A". Any broken ground less than 8 ft above earth is "A" or can get blown into phase conductor is an "A". Another other broken ground is "B" For unigrounds see UNIGROUND. | N/A | N/A | NESC Rule 214A5 & 095A | NO | YES | NO | SINGLEMAN | POWER
221 | UBPBCUAR | PP/RMP | ALL | DISTRIBUTION | OH | UNDERBUILD PROBLEM | ARRESTOR/CUTOUT ISSUE | UNDERBUILD-ARRESTOR/CUTOUT | A/B/D | Signs of tracking or cracked porcelain is A. If jumpered out or parts missing, B. Priority D is RMP only for idle equip or porcelain cutout; note in comment field. | N/A | N/A | NESC Rule 012C | NO | YES | YES | SINGLEMAN | POWER
222 | UBPBGYBK | PP/RMP | ALL | DISTRIBUTION | OH | UNDERBUILD PROBLEM | BROKEN DISTRIBUTION GUY | UNDERBUILD-DISTRIBUTION GUY BROKEN | A/B | Broken distribution guy wire | N/A | N/A | NESC 261C2 | NO | YES | NO | SINGLEMAN | POWER
223 | UBPBGYSL | PP/RMP | ALL | DISTRIBUTION | OH | UNDERBUILD PROBLEM | SLACK DISTRIBUTION GUY | UNDERBUILD-DISTRIBUTION GUY SLACK | A/B | Slack distribution guy wire | Policy 009 Section 3.3(d) | GO95 Rule 56.2 | NESC 261A5C & 264A | NO | YES | NO | SINGLEMAN | POWER
224 | UBPBTWFC | PP/RMP | ALL | DISTRIBUTION | OH | UNDERBUILD PROBLEM | BROKEN TIE WIRE | UNDERBUILD-TIE WIRE BROKEN | A | If loose enough to free conductor, "A". | N/A | N/A | NESC Rule 214A5a & 012C | NO | YES | YES | SINGLEMAN | POWER
225 | UBPBXARM | PP/RMP | ALL | DISTRIBUTION | OH | UNDERBUILD PROBLEM | CROSS ARM ON DISTRIBUTION ISSUE | UNDERBUILD-DISTRIB. CROSSARM | A/B | Severe, "A". Moderate, "B". | N/A | N/A | N/A | NO | YES | YES | SINGLEMAN | POWER
226 | UBPRMSHD | PP/RMP | ALL | DISTRIBUTION | OH | UNDERBUILD PROBLEM | MISSING HARDWARE | UNDERBUILD-MISSING HARDWARE | A/B | "A" if missing nuts. "B" if loose nuts. Expanded spring not a condition. | N/A | N/A | NESC Rule 012C | NO | YES | NO | SINGLEMAN | POWER
227 | UBXARMIN | PP/RMP | ALL | BOTH | OH | UNDERBUILD PROBLEM | BROKEN INSULATOR | UNDERBUILD-INSULATOR BROKEN | A/B | See Insulator Policy 012. If tracking or actively smoking it's an A priority. | Policy No. 012 | N/A | NESC Rule 012C & 447 | NO | YES | YES | SINGLEMAN | POWER
228 | UGPRIELB | PP/RMP | ALL | BOTH | UG | UG PAD / VAULT | PRIMARY UG ELBOW ISSUE | UG-PRIMARY ELBOW | A | If signs of tracking, swelling or deformation A. | N/A | N/A | NESC 447 | NO | NO | NO | SINGLEMAN | POWER
229 | UNIGRDBM | PP/RMP | OR, WA, UT, WY, ID | BOTH | OH | UNIGROUND | BROKEN / MISSING MOLDING ON DELTA OR UNIGROUND SYSTEM | UNIGROUND-BROKEN/MISSING MOLDING | B | (For CA see GO95MLD.) | N/A | N/A | NESC Rule 093D1 & 093D3 | NO | NO | NO | SINGLEMAN | POWER
230 | UNIGRDGR | PP/RMP | ALL | BOTH | OH | UNIGROUND | SEPARATION B/T GRD RODS LESS THAN 20 FT | UNIGROUND-GRD ROD SEPARATION <20FT | B | California Requirement Is 6' Between Ground Rods. All Nesc States: 20FT From Buried Comm Cables. | N/A | GO95 34C3(a) | NESC 097F | NO | NO | NO | SINGLEMAN | POWER
231 | UNIGRDSG | PP/RMP | ALL | BOTH | OH | UNIGROUND | SINGLE GROUND | UNIGROUND-SINGLE GROUND | B |  | N/A | GO95 Rule 33.3B | NESC Rule 097A, 097B & 097C | NO | NO | NO | SINGLEMAN | POWER
232 | VEGCANTI | PP/RMP | ALL | BOTH | OHUG | INSPECTION ISSUE | CANT INSPECT DUE TO VEGETATION | INSP ISSUE - VEGETATION | B | Inspection obstructed by vegetation | Policy 361, 298, 298 & 013 | GO95 Rule 31.2 | NESC 121A, NESC 213, NESC 312 | NO | NO | NO | SINGLEMAN | POWER
233 | WASHOUT | PP/RMP | ALL | BOTH | OHUG | POLE | POLE WASHOUT - NEEDS BACKFILL | WASHOUT | A/B | Pole needs rocks or other appropriate backfill. "A" if severe. | N/A | N/A | NESC Rule 012C | NO | YES | NO | SINGLEMAN | POWER
234 | WMPREPL | PP | CA, OR, WA | BOTH | OH | STRUCTURE INFORMATION | PROACTIVE REPLACEMENT OF WOODEN POLES WITH NON-WOODEN SOLUTIONS PER WMP | WMP CA POLE REPL | D | Pacific Power Only - Condition assigned to identify pole for proactive wrapping per WMP proactive programs | N/A | N/A | N/A | NO | NO | NO | SINGLEMAN | POWER
235 | WMPWRAP | PP | CA, OR, WA | BOTH | OH | STRUCTURE INFORMATION | PROACTIVE FIRE WRAPPING OF POLES PER WMP | WMP CA POLE WRAP | D | Pacific Power Only - Condition assigned to identify pole for proactive replacement per WMP proactive programs | N/A | N/A | N/A | NO | NO | NO | SINGLEMAN | POWER
236 | WRAPMESH | PP/RMP | ALL | BOTH | OH | STRUCTURE INFORMATION | MESH TYPE FIRE WRAPPED POLES | WRAPPED POLE - MESH TYPE FIRE | D | For information only | N/A | N/A | N/A | NO | NO | NO | SINGLEMAN | POWER
237 | WRAPNMSH | PP/RMP | ALL | BOTH | OH | STRUCTURE INFORMATION | NON-MESH FIRE WRAPPED POLES | WRAPPED POLE - NON-MESH FIRE | D | For information only | N/A | N/A | N/A | NO | NO | NO | SINGLEMAN | POWER
238 | XARMBRAC | PP/RMP | ALL | BOTH | OH | CROSS ARM | CROSS BRACE BROKEN/MISSING/LOOSE | XARM-CROSS BRACE BROKEN/MISSING/LOOSE | A/B | "B" if cross arm brace broken, missing or hanging loose on distribution. "A" if transmission cross arm broken or missing. If loose transmission hardware, use TRNSBRAC. | N/A | N/A | NESC 261D | NO | YES | YES | SINGLEMAN | POWER
239 | XARMSPCR | PP/RMP | ALL | BOTH | OH | CROSS ARM | ARM SPLIT/CRACKED/ROTTEN/TWISTED/TRACKING | ARM SPLIT/CRACKED/ROTTEN/TWISTED/TRACKING | A/B | "A" if severe. "B" if moderate. | N/A | N/A | NESC 261D | NO | YES | YES | SINGLEMAN | POWER
240 | XARMSQPN | PP/RMP | ALL | BOTH | OH | CROSS ARM | SQUATTER PIN | XARM-SQUATTER PIN | B | "B" if insulator is sitting on cross arm. | N/A | N/A | NESC Rule 012C & 252 | NO | YES | YES | SINGLEMAN | POWER
241 | XFRBARIR | PP/RMP | ALL | DISTRIBUTION | UG | UG PAD / VAULT | MISSING LIVEFRONT BARRIERS | MISSING LIVEFRONT BARRIERS | B/D | Information only to support record keeping or other programs. D-Priority RMP ONLY | Policy 008 | GO128 Rule 32.7 | NESC Rule 381G2 | NO | NO | NO | SINGLEMAN | POWER
242 | XFRFMNR | PP/RMP | ALL | DISTRIBUTION | UG | UG PAD / VAULT | EXCESSIVE FOREIGN MATERIAL IN XFMR | EXCESSIVE FOREIGN MATERIAL IN XFMR | B/D | Information only to support record keeping or other programs. D-Priority RMP ONLY | Policy 008 | GO128 Rule 34.3 | NESC Rule 381G2 | NO | NO | NO | SINGLEMAN | POWER
243 | XFRGRNDG | PP/RMP | ALL | BOTH | OHUG | UG PAD / VAULT | BROKEN/MISSING GROUND OR INSUFFICIENT NUMBER OF GROUNDS. | GROUND BROKEN/MISSING/INSUFFICIENT # | B | No differentiator as only a 'B' condition is allowed | Policy 008 | GO95 Rule 58.2A(3) | NESC Rule 314, 374, 384 | NO | NO | NO | SINGLEMAN | POWER
244 | XFRLBOLT | PP/RMP | ALL | DISTRIBUTION | UG | TRANSFORMER | LIFTING BOLTS NOT REMOVED OR TURNED | LIFTING BOLTS NOT REMOVED OR TURNED | B/D | Remove or turn lifting bolts at time of inspection if possible. Otherwise, information only to support record keeping or other programs. D-Priority RMP ONLY | N/A | GO128 Rule 17.3 | NESC Rule 012C | NO | NO | NO | SINGLEMAN | POWER
245 | XFRMBKH | PP/RMP | ALL | BOTH | UG | TRANSFORMER | BROKEN LATCH/HINGES OR MISSING LOCK ON UG | XFRM-BROKEN LATCH/HINGE/LOCK MISSING | A | Broken latch/hinge or missing lock on UG allowing access. | N/A | GO128 34.3-C | NESC Rule 381G1 & 2 | NO | NO | NO | SINGLEMAN | POWER
246 | XFRMBOBR | PP/RMP | ALL | BOTH | OH | TRANSFORMER | LOOSE BOLTS/ BRACKET OR MISSING BOLTS | XFRM-LOOSE/MISSING BOLTS/BRACKET | A/B | "A" if hardware is missing. "B" if hardware is loose. | N/A | GO95 Rule 18 A-1 | NESC Rule 012C | NO | YES | YES | SINGLEMAN | POWER
247 | XFRMUGRU | PP/RMP | ALL | BOTH | OHUG | TRANSFORMER | OH OR UG TRANSFORMER SEVERELY RUSTED, DOOR OR TANK RUSTED ALLOWING ACCESS ON UG | XFRM-SEVERELY RUSTED/ALLOW ACCESS | A/B | If deteriorated such that it allows access A. If no access but rust is significant B. | Policy 009 | GO128 34-3B, 35.A | NESC Rule 012C, NESC Rule 214A5 | NO | NO | YES FOR OH - NO FOR UG | SINGLEMAN | POWER
248 | XFRTRNCH | PP/RMP | ALL | BOTH | UG | UG PAD / VAULT | TRENCHING FROM PAD WAS NOT PROPERLY BACKFILLED. | TRENCHING FROM PAD NOT PROPERLY BACKFILL | B | No differentiator as only a 'B' condition is allowed | N/A | GO128 Rule 34.3 | NESC Rule 321B | NO | NO | NO | SINGLEMAN | POWER
249 | XRFMBUIN | PP/RMP | ALL | BOTH | OH | TRANSFORMER | BROKEN BUSHING/INSULATOR | XFRM-BUSHING/INSULATOR BROKEN | A/B | "A" if severe. "B" if moderate. | Policy 009 | GO95 Rule 18 A-1 | NESC Rule 012C | NO | NO | NO | SINGLEMAN | POWER
250 | COFIBBRG | PP/RMP | ALL | BOTH | OH | FIBER CONDITION | BROKEN GUY OR PULLED ANCHOR | COND-FIBER BROKEN GUY/PULLED ANCHOR | A |  | N/A | N/A | NESC Rule 264A, 214B2 | NO | YES | NO | COMMUNICATIONS | COMMUNICATIONS
251 | COTELBRG | PP/RMP | ALL | BOTH | OH | TELCO CONDITION | BROKEN GUY OR PULLED ANCHOR | COND-TELCO BROKEN GUY/PULLED ANCHOR | A |  | N/A | N/A | NESC Rule 264A, 214B2 | NO | YES | NO | COMMUNICATIONS | COMMUNICATIONS
252 | COTVBRG | PP/RMP | ALL | BOTH | OH | CATV CONDITION | BROKEN GUY OR PULLED ANCHOR | COND-CATV BROKEN GUY/PULLED ANCHOR | A |  | N/A | N/A | NESC Rule 264A, 214B2 | NO | YES | NO | COMMUNICATIONS | COMMUNICATIONS
Note on J4: BRIAN PAGEL: AS PER FP16 MAINFRAME SCREEN. THIS VERSION OF THE DESCRIPTION GOES INTO GISMO AND COMPANY GIS APPS AS MAINFRAME SCREEN IS LIMITED TO 53 CHARACTERS, TRY TO KEEP DESC TO NO MORE THAN 40 CHARACTERS SO FIELD EMPLOYEES CAN ADD TEXT
Note on S4: BRIAN PAGEL: USED IN GISMO TO ASSIGN CREW TO CORRECTION TASK GISMO ALLOWS EACH DISTRICT TO ALTER THE CREW DROP DOWN. HOWEVER, GISMO NEEDS TO HAVE A GENERIC DEFAULT AS A STARTING POINT. THAT IS WHAT THIS FIELD IS.

## Rev. Changes
December 19, 2022 Updates
The following changes were made to make Revision 22
March 9, 2023 Updates
The following changes were made to make Revision 23a