{"text_format":"1","workbook":"xlsx","n_sheets":1,"sheets":["PacifiCorp smart inverter setti"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"PacifiCorp smart inverter setti","index":0,"n_rows":88,"n_cols":2,"rows_kept":88,"cut":false,"hidden":false,"merged":[]}
["PARAMETER","VALUE"]
["MT_FILE_INFO_TYPE","SS"]
["MT_UTILITY_NAME","PacifiCorp"]
["MT_COUNTRY","United States of America"]
["MT_DATE_OF_APPLICABILITY","2024-06-01"]
["MT_NP_NORMAL_OP_CAT-APP","CAT_B"]
["MT_NP_ABNORMAL_OP_CAT-APP","CAT_III"]
["NP_P_MAX-SS"]
["NP_P_MAX_OVER_PF-SS"]
["NP_OVER_PF-SS"]
["NP_P_MAX_UNDER_PF-SS"]
["NP_UNDER_PF-SS"]
["NP_VA_MAX-SS"]
["NP_Q_MAX_INJ-SS"]
["NP_Q_MAX_ABS-SS"]
["NP_P_MAX_CHARGE-SS"]
["NP_APPARENT_POWER_CHARGE_MAX-SS"]
["NP_AC_V_NOM-SS"]
["AP_LIMIT_ENABLE-SS","DISABLED"]
["AP_LIMIT-SS",1]
["ES_PERMIT_SERVICE-SS","ENABLED"]
["ES_V_LOW-SS",0.91700000000000004]
["ES_V_HIGH-SS",1.05]
["ES_F_LOW-SS",59.5]
["ES_F_HIGH-SS",60.1]
["ES_DELAY-SS",300]
["ES_RANDOMIZED_DELAY-SS",0]
["ES_RAMP_RATE-SS",300]
["CONST_PF_MODE_ENABLE-SS","DISABLED"]
["CONST_PF_EXCITATION-SS","ABS"]
["CONST_PF-SS",1]
["CONST_Q_MODE_ENABLE-SS","DISABLED"]
["CONST_Q-SS",0]
["QV_MODE_ENABLE-SS","ENABLED"]
["QV_VREF-SS",1]
["QV_VREF_AUTO_MODE-SS","DISABLED"]
["QV_VREF_TIME-SS",300]
["QV_CURVE_V2-SS",0.98]
["QV_CURVE_Q2-SS",0]
["QV_CURVE_V3-SS",1.0249999999999999]
["QV_CURVE_Q3-SS",0]
["QV_CURVE_V1-SS",0.92]
["QV_CURVE_Q1-SS",0.44]
["QV_CURVE_V4-SS",1.0549999999999999]
["QV_CURVE_Q4-SS",-0.44]
["QV_OLRT-SS",5]
["QP_MODE_ENABLE-SS","DISABLED"]
["QP_CURVE_P3_GEN-SS",1]
["QP_CURVE_P2_GEN-SS",0.5]
["QP_CURVE_P1_GEN-SS",0.2]
["QP_CURVE_P1_LOAD-SS",-0.2]
["QP_CURVE_P2_LOAD-SS",-0.5]
["QP_CURVE_P3_LOAD-SS",-1]
["QP_CURVE_Q3_GEN-SS",-0.44]
["QP_CURVE_Q2_GEN-SS",0]
["QP_CURVE_Q1_GEN-SS",0]
["QP_CURVE_Q1_LOAD-SS",0]
["QP_CURVE_Q2_LOAD-SS",0]
["QP_CURVE_Q3_LOAD-SS",0.44]
["PV_MODE_ENABLE-SS","ENABLED"]
["PV_CURVE_V1-SS",1.06]
["PV_CURVE_P1-SS",1]
["PV_CURVE_V2-SS",1.1000000000000001]
["PV_CURVE_P2-SS",0]
["PV_OLRT-SS",10]
["OV2_TRIP_V-SS",1.2]
["OV2_TRIP_T-SS",0.16]
["OV1_TRIP_V-SS",1.1000000000000001]
["OV1_TRIP_T-SS",13]
["UV1_TRIP_V-SS",0.88]
["UV1_TRIP_T-SS",21]
["UV2_TRIP_V-SS",0.5]
["UV2_TRIP_T-SS",2]
["OF2_TRIP_F-SS",62]
["OF2_TRIP_T-SS",0.16]
["OF1_TRIP_F-SS",61.2]
["OF1_TRIP_T-SS",300]
["UF1_TRIP_F-SS",58.5]
["UF1_TRIP_T-SS",300]
["UF2_TRIP_F-SS",56.5]
["UF2_TRIP_T-SS",0.16]
["PF_DBOF-SS",3.5999999999999997E-2]
["PF_DBUF-SS",3.5999999999999997E-2]
["PF_KOF-SS",0.05]
["PF_KUF-SS",0.05]
["PF_OLRT-SS",5]
["MC_HVRT_V1-SS",1.1000000000000001]
["MC_LVRT_V1-SS",0.5]